## Sheet1
Endeavour - Rosetta Data Portal
DAPR Template Information | Year | NPR-000070 Augmentation of Box Hill ZS | NPR-000069 Establishment of West Appin ZS | NPR-000049 Establishment of Mt Gilead ZS | NPR-000533 132kV Cable Constraints in the Parramatta area | NPR-000053 Austral ZS | NPR-000052 Cambewarra Capacity Increase | NPR-000054 Capacity Increase for the Catherine Fields Growth Areas | Replacement of end of life 132kV oil filled cables in the Parramatta area
Constraint primary driver |  | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Capacity | Reliability & Safety & Environment
Location of constraint (start) |  | -33.637224, 150.898978 | ?34.20356, 150.77143 | -34.139089, 150.769423 | -33.824824, 151.030938 | -33.931801, 150.817902 | -34.857960, 150.597903 | ?34.00857, 150.75702 | -33.824824, 151.030938
Location of constraint (end) |  | -33.637224, 150.898978 | ?34.20356, 150.77143 | -34.139089, 150.769423 | -33.824824, 151.030938 | -33.931801, 150.817902 | -34.857960, 150.597903 | ?34.00857, 150.75702 | -33.824824, 151.030938
Asset ID |  | NPR-000070 Augmentation of Box Hill ZS | NPR-000069 Establishment of West Appin ZS | NPR-000049 Establishment of Mt Gilead ZS | NPR-000533 132kV Cable Constraints in the Parramatta area | NPR-000053 Austral ZS | NPR-000052 Cambewarra Capacity Increase | NPR-000054 Capacity Increase for the Catherine Fields Growth Areas | Replacement of end of life 132kV oil filled cables in the Parramatta area
Network Element |  | Zone Substation | Zone Substation | Zone Substation | Sub-transmission Line | Zone Substation | Zone Substation | Zone Substation | Sub-transmission Line
Total number of residential customers affected |  | >1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000 | >1000
Percentage of total residential customers affected |  | NA | NA | NA | NA | NA | NA | NA | NA
Voltage level (kV) |  | 132 | 66 | 66 | 132 | 132 | 11 | 132 | 132
Preferred network investment |  | Augment existing ZS | New ZS within the West Appin area | New ZS within the Gilead Precinct | Augmenting 132kV supply to Parramatta | Establish new ZS | Establish new 11kV Feeder | Establish new ZS | Replace cables at end of life with modern equivalent of increased capacity
Preferred network investment capital cost |  | 51356893 | 33509595 | 35000000 | 4319281 | 23400000 | 9713000 | 36600000 | 41800000
Preferred annual network investment operating cost |  | 205427.57 | 134038.38 | 140000 | 17277.12 | 93600 | 38852 | 146400 | 167200
Preferred network investment cost accuracy (+%) |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Preferred network investment cost accuracy (-%) |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Proposed timing FNY |  | FY28 | FY29 | FY31 | FY29 | FY30 | FY31 | FY29 | FY29
Demand reduction required to defer investment by 1 year (MVA) |  | 6.89 | 80.8421 | 15.7895 | 2.85 | 49.1579 | 17.4716 | 4.4 | N/A
Demand reduction required to defer investment by 1 year (MW) |  | 6.5469 | 76.8 | 15 | 2.7075 | 46.7 | 16.6 | 4.18 | N/A
Annual Deferral Value |  | 1679370.4 | 971480 | 1386807 | 141240.49 | 765180 | 317615.1 | 1196820 | 1366860
Load transfer capability (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load transfer capability (MW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation (MVA) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emergency generation (MW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Historic use of existing emergency response (MVA) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic use of existing emergency response (MW) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating (MVA) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Historic asset rating (MW) |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Asset Rating (MVA)
2026 |  | 22.2 | 5.17 | 3.27 | 93 | 50 | 2.39 | 15.9 | 0
2027 |  | 18.2 | 5.17 | 4.57 | 93 | 50 | 2.38 | 15.9 | 0
2028 |  | 18.2 | 5.17 | 6.51 | 93 | 50 | 2.37 | 15.9 | 0
2029 |  | 18.2 | 5.17 | 8.46 | 93 | 50 | 2.35 | 15.9 | 0
2030 |  | 18.2 | 5.17 | 11.04 | 93 | 50 | 2.34 | 15.9 | 0
Asset Rating (MW)
2026 |  | 21.09 | 4.91 | 7.94 | 88.35 | 47.5 | 2.27 | 15.11 | 0
2027 |  | 17.29 | 4.91 | 7.94 | 88.35 | 47.5 | 2.26 | 15.11 | 0
2028 |  | 17.29 | 4.91 | 7.94 | 88.35 | 47.5 | 2.25 | 15.11 | 0
2029 |  | 17.29 | 4.91 | 7.94 | 88.35 | 47.5 | 2.23 | 15.11 | 0
2030 |  | 17.29 | 4.91 | 7.94 | 88.35 | 47.5 | 2.22 | 15.11 | 0
Forecast Demand 50% POE (MVA)
2026 |  | 30.5 | 5.7 | 3.27 | 121 | 67.8 | 2.93 | 17 | 0
2027 |  | 36.47 | 6.19 | 4.57 | 134 | 76.2 | 3.42 | 18.6 | 0
2028 |  | 43.73 | 7.86 | 6.51 | 145 | 82.2 | 4.07 | 19.9 | 0
2029 |  | 48.38 | 10.14 | 8.46 | 148 | 85.9 | 4.72 | 20.3 | 0
2030 |  | 53.03 | 15.79 | 11.04 | 152 | 88 | 5.38 | 20.7 | 0
Forecast Demand 50% POE (MW)
2026 |  | 28.97 | 5.42 | 3.11 | 114.95 | 64.41 | 2.78 | 16.15 | 0
2027 |  | 34.65 | 5.88 | 4.34 | 127.3 | 72.39 | 3.25 | 17.67 | 0
2028 |  | 41.54 | 7.47 | 6.18 | 137.75 | 78.09 | 3.87 | 18.91 | 0
2029 |  | 45.96 | 9.63 | 8.04 | 140.6 | 81.61 | 4.48 | 19.29 | 0
2030 |  | 50.38 | 15 | 10.49 | 144.4 | 83.6 | 5.11 | 19.67 | 0
Forecast Demand 10% POE (MVA)
2026 |  | 30.5 | 5.7 | 3.27 | 121 | 74.58 | 2.93 | 18.7 | 0
2027 |  | 36.47 | 6.19 | 4.57 | 134 | 83.82 | 3.42 | 20.46 | 0
2028 |  | 43.73 | 7.86 | 6.51 | 145 | 90.42 | 4.07 | 21.89 | 0
2029 |  | 48.38 | 10.14 | 8.46 | 148 | 94.49 | 4.72 | 22.33 | 0
2030 |  | 53.03 | 15.79 | 11.04 | 152 | 96.8 | 5.38 | 22.77 | 0
Forecast Demand 10% POE (MW)
2026 |  | 28.97 | 5.42 | 3.11 | 114.95 | 70.85 | 2.78 | 17.77 | 0
2027 |  | 34.65 | 5.88 | 4.34 | 127.3 | 79.63 | 3.25 | 19.44 | 0
2028 |  | 41.54 | 7.47 | 6.18 | 137.75 | 85.9 | 3.87 | 20.8 | 0
2029 |  | 45.96 | 9.63 | 8.04 | 140.6 | 89.77 | 4.48 | 21.21 | 0
2030 |  | 50.38 | 15 | 10.49 | 144.4 | 91.96 | 5.11 | 21.63 | 0
Maximum Load at risk (MW)
2026 |  | 7.88 | 0.5 | 0 | 26.6 | 16.91 | 0.51 | 1.05 | 0
2027 |  | 17.36 | 0.97 | 0 | 38.95 | 24.89 | 0.99 | 2.57 | 0
2028 |  | 24.25 | 2.56 | 0 | 49.4 | 30.59 | 1.62 | 3.8 | 0
2029 |  | 28.67 | 4.72 | 0.1 | 52.25 | 34.11 | 2.25 | 4.18 | 0
2030 |  | 33.09 | 10.09 | 2.55 | 56.05 | 36.1 | 2.89 | 4.56 | 0
Expected Unserved Energy (MWh)
2026 |  | 0 | 2.6 | 0 | 1.4 | 0.6 | 0.07 | 0.48 | 0
2027 |  | 0 | 6.3 | 0 | 6.2 | 3.1 | 0.34 | 12.71 | 0
2028 |  | 0.27 | 12.3 | 0 | 42.6 | 8.8 | 1.39 | 28.46 | 0
2029 |  | 12.68 | 89.1 | 0 | 74.6 | 35.5 | 3.96 | 34 | 0
2030 |  | 101.66 | 200.2 | 15 | 699.3 | 82.2 | 20.56 | 35.39 | 0