## Introduction & Notes
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2025)
This workbook presents primary distribution feeders which are currently experiencing overload or are forecast to experience an overload in the next 2 years.
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2025 (DAPR) and should be read in conjunction with the report.
Contents
The 'Distribution Feeder Limitations' tab of this workbook includes the following information for each constrained distribution feeder. -Ergon Energy region -Distribution feeder name, ID & Location -Load exceedance after 2 yrs (MVA) -Forecast season that exceedance occurs (Summer/Winter) -Forecast year that exceedance occurs -Load reduction needed to delay the exceedance by 12 months (MW) (assumed power factor of 0.9)
1. Potential Solutions
Suggest solutions, in order or preference, are included under the 'Potential Solutions' tab.
2. Committed Solutions
Committed investments to address current distribution network limitations are included under the 'Committed Solutions' tab
Connection points for possible load reduction:
In all cases, the connection point to apply load reduction would be downstream of the substation exit feeder cable and/or first section of line.
Exclusions
Dedicated customer connection assets are excluded from the analysis.
NOTE: All financials presented in this document are correct at the time of writing (October 2025) and represent the existing organisational accounting treatment, which may be subject to change.

## Disclaimer
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2025)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2025 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the 'Introduction & Notes' section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy's Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitations, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except tot the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information on this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change.
All presented project costings and milestones (as of October 2025) are subject to change.

## Potential Solutions
Solutions
Distribution feeder capacity problems can be solved in a number of ways, depending on the local characteristics of the distribution feeder. The constraints identified in this document are a trigger for further planning studies and in many cases do not constitute plant risk, are acceptable, and do not require augmentation due to multiple factors such as: -Minimal load growth on the feeder and/or adjacent feeders. -Customer density or feeder topology constraints that do not allow for planning constrains to be met. -Short term customer behaviour changes (such as abnormal weather conditions). -Medium term network topology changes due to planned works in a region.
Where action is required to solve a feeder constraint, possible solutions (in approximate order of preference based on network cost) include:
Network Reconfiguration -Transferring existing load to adjacent feeders if capacity is available: and -Re-rating or dynamic rating of the underground exit cable or overhead feeder.
Demand Management initiatives that reduce customer loading -Energy efficient appliances -Power factor correction -Shit loads (e.g. pool pumps, HW storage etc.) to control load tariff -Shift loads to a time-of-use tariff -Air conditioning 'peak Smart' -Customer EG units -Call off load -Commercial and industrial demand management -Customer embedded generation to 'peak lop' -Network embedded generation to 'peak lop' -Energy storage
Network Augmentation -Replacing the underground exit cable or overhead feeder -Creating new substations and/or feeders and transferring existing load
In each instance, actual solutions are subject to a detailed study and business case. In some cases, a committed project is already in place.

## Distribution Feeder Limit 2025
Distribution Feeder Limitations (Ergon Energy Distribution Annual Planning Report 2025)
Region | Feeder name | Feeder ID | Feeder Location | Load exceedance after 2 yrs (MVA) | Season of exceedance | Year of exceedance | Month of exceedance | Load reduction to defer exceedance by 12 mths (MW) @ 0.9pf | Connection Point | Potenital Solutions
Southern | BK206 | 40216323 | Tambo | 1.1634 | Summer | 2024/2025 | Dec-Feb | 1.0546 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | SB202 | 40200483 | ROLLESTON NORTH | 0.16532 | Summer | 2024/2025 | Dec-Feb | 0.14958 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | FV111 | 40001100 | FRENCHVILLE RD | 1.6029 | Summer | 2024/2025 | Dec-Feb | 1.4664 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | GE-01 | 25273297 | CORFIELD SWER | 0.05705 | Summer | 2024/2025 | Dec-Feb | 0.051824 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | GE-03 | 25273293 | GLENELG SWER | 0.024339 | Summer | 2024/2025 | Dec-Feb | 0.032699 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | BLRI-05 | 84737242 | BLRI-05 FDR | 1.401 | Summer | 2024/2025 | Dec-Feb | 1.2125 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | PA-16 | 25267836 | PETERARLETT NO.16 | 1.1952 | Summer | 2024/2025 | Dec-Feb | 1.0332 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | EM214 | 40001004 | Hospital Road | 1.6936 | Summer | 2024/2025 | Dec-Feb | 1.5243 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F133R | 60026691 | ROMA COLLEGE | 0.50813 | Summer | 2024/2025 | Dec-Feb | 0.46463 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | DG-07 | 20004796 | DANGLEESON NO.07 | 1.0314 | Summer | 2024/2025 | Dec-Feb | 0.9078 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 3220 | 84653808 | 19.1KV BELYANDO FDR 3220 | 0.008365 | Summer | 2024/2025 | Dec-Feb | 0.0077238 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | SF-03 | 25272938 | Stamford No.03 Tangorin SWER | 0.020893 | Summer | 2024/2025 | Dec-Feb | 0.024968 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 2HAM | 83896573 | HAMBLEDON FDR | 2.1292 | Summer | 2024/2025 | Dec-Feb | 1.7779 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | HP-05 | 20007358 | HERMITPARK NO.05 | 0.7321 | Summer | 2024/2025 | Dec-Feb | 0.72022 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F049R | 60026666 | ROMA NORTH | 1.8376 | Summer | 2024/2025 | Dec-Feb | 1.6538 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F060T | 60026667 | TARA | 0.8164 | Summer | 2024/2025 | Dec-Feb | 0.75768 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 304 | 30053814 | GOLDSMITH ST FDR | 0.86467 | Summer | 2024/2025 | Dec-Feb | 0.78526 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F206C | 60026701 | AUGATHELLA | 0.67887 | Summer | 2024/2025 | Dec-Feb | 0.6188 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | AV-10 | 20001178 | AITKENVALE NO.10 | 0.72453 | Summer | 2024/2025 | Dec-Feb | 0.65841 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 2NOR | 10020673 | NORMANTON | 0.41961 | Summer | 2024/2025 | Dec-Feb | 0.37263 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F4555 | 60026840 | WEETWOOD STREET | 1.2882 | Winter | 2024/2025 | Mar-Nov | 1.2453 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | CB-05 | 20003317 | CRANBROOK NO.05 | 0.55405 | Summer | 2024/2025 | Dec-Feb | 0.51748 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 215 | 30053782 | Township No 1 | 0.6109 | Summer | 2024/2025 | Dec-Feb | 0.54402 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | BO-07 | 20003026 | BOHLE NO.07 | 0.54512 | Summer | 2024/2025 | Dec-Feb | 0.49061 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | BG-C | 82556069 | KELLY'S CREEK 1774 | 0.33818 | Summer | 2024/2025 | Dec-Feb | 0.21707 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | GF111 | 40001194 | HOSPITAL TIE | 0.69271 | Summer | 2024/2025 | Dec-Feb | 0.65191 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | AL-10 | 25274650 | Alan Sherriff No.10 11kV feeder | 0.92595 | Summer | 2024/2025 | Dec-Feb | 0.82866 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | RM-04 | 20011598 | RASMUSSEN NO.04 | 0.55741 | Summer | 2024/2025 | Dec-Feb | 0.51072 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | CB-07 | 20003349 | CRANBROOK NO.07 | 0.54846 | Summer | 2024/2025 | Dec-Feb | 0.50265 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | GF105 | 40001189 | WEST GLADSTONE | 0.57815 | Summer | 2024/2025 | Dec-Feb | 0.53338 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F3055 | 60026754 | HARLAXTON | 0.73187 | Summer | 2024/2025 | Dec-Feb | 0.63941 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | WB-J | 50000211 | AVOCA ST | 0.81629 | Summer | 2024/2025 | Dec-Feb | 0.73951 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | CI104 | 40001177 | CI104 Clinton Park | 0.73517 | Summer | 2024/2025 | Dec-Feb | 0.65714 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | IN-08 | 25273220 | INGHAM NO.08 | 0.62818 | Summer | 2024/2025 | Dec-Feb | 0.59896 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 385 | 30187535 | Rural View | 0.68619 | Summer | 2024/2025 | Dec-Feb | 0.57559 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | PB-A | 84571892 | URRAWEEN ROAD | 0.44662 | Summer | 2024/2025 | Dec-Feb | 0.44629 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | YP116 | 40000970 | Rockhampton Rd | 0.73688 | Summer | 2024/2025 | Dec-Feb | 0.57454 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | DG-06 | 20004751 | DANGLEESON NO.06 | 0.34139 | Summer | 2024/2025 | Dec-Feb | 0.31572 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | GS108 | 40001202 | SUNVALLEY | 0.61332 | Summer | 2024/2025 | Dec-Feb | 0.53288 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | WB-F | 50000207 | FOUNDRY | 0.52007 | Summer | 2024/2025 | Dec-Feb | 0.47271 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 2MNR | 84326665 | MANOORA FDR | 1.05 | Summer | 2024/2025 | Dec-Feb | 0.87236 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | PH106 | 40001122 | UNIVERSITY | 0.29648 | Summer | 2024/2025 | Dec-Feb | 0.26961 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F3160 | 60026767 | HURSLEY ROAD | 0.5077 | Winter | 2024/2025 | Mar-Nov | 0.47757 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 2CO3 | 10020832 | COOK NO 3 | 1.0183 | Summer | 2024/2025 | Dec-Feb | 0.92643 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | KR-C | 50000092 | KINGAROY NORTH | 0.43533 | Winter | 2024/2025 | Mar-Nov | 0.42133 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | BN-05 | 20002622 | BOWEN NO.05 | 0.37344 | Summer | 2024/2025 | Dec-Feb | 0.3326 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F4185 | 60026824 | SOUTHBROOK | 0.072637 | Summer | 2024/2025 | Dec-Feb | 0.063348 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | CT-04 | 20004592 | HOSPITAL | 0.23385 | Summer | 2024/2025 | Dec-Feb | 0.23748 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | 14169 | 112330157 | CAMBOOYA | 0.14192 | Winter | 2024/2025 | Mar-Nov | 0.12256 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F200C | 60026697 | PARTRIDGE STREET | 0.28825 | Summer | 2024/2025 | Dec-Feb | 0.27353 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 398 | 82649845 | PALUMA RD | 0.36671 | Summer | 2024/2025 | Dec-Feb | 0.33004 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | BL104 | 40001247 | Prairie St | 0.23409 | Summer | 2024/2025 | Dec-Feb | 0.23492 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | RS-J | 50000169 | TOWN | 0.27275 | Summer | 2024/2025 | Dec-Feb | 0.25244 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | BR107 | 40001175 | BR107 Tarcoola | 0.3595 | Summer | 2024/2025 | Dec-Feb | 0.31077 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F4370 | 60026830 | THULIMBAH | 0.0016474 | Summer | 2024/2025 | Dec-Feb | 0.0027612 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F4610 | 60330968 | WESTBROOK FDR | 0.41816 | Winter | 2024/2025 | Mar-Nov | 0.322 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | BLRI-08 | 82914276 | BLRI-08 FDR | 0.26582 | Summer | 2024/2025 | Dec-Feb | 0.26568 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | 14142 | 91445024 | BRIFFNEY | 0.41948 | Summer | 2024/2025 | Dec-Feb | 0.31114 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | EB-G | 50000035 | KEPNOCK | 0.12625 | Summer | 2024/2025 | Dec-Feb | 0.12261 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 103 | 30053746 | Proserpine | 0.15511 | Summer | 2024/2025 | Dec-Feb | 0.14854 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | CP103 | 40001232 | BEECHER FDR | 0.27393 | Summer | 2024/2025 | Dec-Feb | 0.22206 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 363 | 30053872 | Eimeo | 0.19242 | Summer | 2024/2025 | Dec-Feb | 0.16636 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | RS-G | 50000167 | NEPTUNE STREET | 0.14711 | Summer | 2024/2025 | Dec-Feb | 0.14708 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | CL203 | 40000998 | Clermont Town | 0.17148 | Summer | 2024/2025 | Dec-Feb | 0.1505 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | RM-05 | 20011656 | RASMUSSEN NO.05 | 0.10976 | Summer | 2024/2025 | Dec-Feb | 0.098783 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | TB223 | 85221946 | KINKA FDR TB223 | 0.43828 | Summer | 2024/2025 | Dec-Feb | 0.27584 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 417 | 83909007 | TOWN NO 5 | 0.20338 | Summer | 2024/2025 | Dec-Feb | 0.15495 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 333 | 30053843 | Abattoir | 0.18356 | Summer | 2024/2025 | Dec-Feb | 0.12182 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F203C | 60026699 | PARRY STREET | 0.058895 | Summer | 2024/2025 | Dec-Feb | 0.072888 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 2GO3 | 10020782 | GORDONVALE NO3 | 0.14437 | Summer | 2024/2025 | Dec-Feb | 0.14566 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | PB-D | 50000155 | PIALBA | 0.033979 | Summer | 2024/2025 | Dec-Feb | 0.047688 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 2FOG | 10134605 | FOREST GARDENS | 0.14733 | Summer | 2024/2025 | Dec-Feb | 0.12602 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | F2415 | 60026718 | CABARLAH | 0.34183 | Summer | 2024/2025 | Dec-Feb | 0.17321 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | RS-E | 50000165 | ULULAH | 0.0595 | Summer | 2024/2025 | Dec-Feb | 0.057981 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 1851 | 82649838 | ABLE ROAD | 0.12266 | Summer | 2024/2025 | Dec-Feb | 0.08867 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Southern | YP111 | 40001226 | Farnborough Rd | 0.19682 | Summer | 2024/2025 | Dec-Feb | 0.10306 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | 2HAR | 10134518 | HARDY RD | 0.035689 | Summer | 2024/2025 | Dec-Feb | 0.047696 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet
Northern | BN-07 | 20002698 | BOWEN NO.07 | 0.038202 | Summer | 2024/2025 | Dec-Feb | 0.023075 | Refer to "Introduction & notes" Sheet | Refer to "Potential Solutions" Sheet

## Committed Solutions 2025
WR Ref. | Proj Number | Limitation | Location | Committed Solution | Region
1118136 | 351458 | Distribution Feeder Limitation Address capacity and protection constraints | POVE - Point Vernon | Extend 11kV Point Vernon feeder by 4.5km, install new 11kV automatic circuit recloser and reconfigure network. -Target Comissioning: Jul-26 -Cost: $2.4M ± 30% | ERG - South - Fraser Burnett
1716716 | 411111 | Distribution Feeder Limitation Address capacity and voltage constraints | BARG - Bargara | Install 11kV regulators and re-rate 3.5km of conductor. -Target Comissioning: Jan-28 -Cost: $0.6M ± 30% | ERG - South - Bundaberg Burnett
1784097 | 455549 | Distribution Feeder Limitation Address protection constraints | MORA - Moranbah | Convert sections of SWER feeder to single phase and convert sections of SWER feeder to isolated. Upgrade conductors and SWER substations. -Target Comissioning: Nov-27 -Cost: $0.9M ± 30% | ERG - North - Pioneer
1869034 | 515130 | Distribution Feeder Limitation Address voltage constraints | BILO - Biloela | Recover and reconductor 450m of three-phase 11kV and 1.5km of single-phase 11kV. Build new single-phase section and relocate fuses. -Target Comissioning: Jul-27 -Cost: $0.5M ± 30% | ERG - South - Capricornia
1870697 | 516522 | Distribution Feeder Limitation Address capacity and voltage constraints | BLAK - Blackall | Recover and reconductor 1.5km of conductor on Tambo 22kV (BK206), install new regulators and update settings for a regulator. -Target Comissioning: Jul-27 -Cost: $0.7M ± 30% | ERG - South - WZ- Central West
1872437 | 524177 | Distribution Feeder Limitation Address protection and voltage constraints | MONT - Monto | Install a new SWER regulator, and upgrade recloser and isolator on 11kV feeder (MT-103) -Target Comissioning: Dec-27 -Cost: $0.3M ± 30% | ERG - South - Capricornia
1869673 | 515719 | Distribution Feeder Limitation Address voltage constraints | BLAC - Blackwater | Install new SWER regulator and 2km of OHEW on 22kV feeder (BW-209). -Comissioning Date: Sep-27 -Cost: $0.2M ± 30% | ERG - South - Central West
1872976 | 523795 | Distribution Feeder Limitation Address voltage constraints | CALL - Calliope | Reconductor 1.75km of 11kV single phase conductor and install new 1 tank regulator on 11kV feeder (CP107). -Target Comissioning: Sep-27 -Cost: $0.4M ± 30% | ERG - South - Capricornia
1856640 | 515879 | Distribution Feeder Limitation Address capacity and protection constraints | ALSH - Alan Sheriff | Reconductor 300m of 11kV conductor and uprate 4km of 11kV conductor. Install fuses, replace gas switch and permanentley reconfigure network. -Target Comissioning: Aug-27 -Cost: $0.8M ± 30% | ERG - North - Herbert
1872521 | 524507 | Distribution Feeder Limitation Address voltage constraints | LONG - Longreach | Install new SWER regulator and upgrade SER recloser on 22kV feeder (LR209) -Target Comissioning: Nov-27 -Cost: $0.3M ± 30% | ERG - South - WZ- Central West
1883880 | 524516 | Distribution Feeder Limitation Address voltage constraints | EMDE - Emerald | Install new SWER regulator and 1.05km of OHEW on 22kV feeder (EM215). -Target Comissioning: Sep-27 -Cost: $0.2M ± 30% | ERG - South - Capricornia
1896948 | 528502 | Distribution Feeder Limitation Address protection, reliability and capacity constraints | BLRI - Black River | Reconductor 700m of 11kV conductor, uprate 4km of existing conductor, update protection settings and reconfigure network on 11kV feeder (BLRI-05) -Target Comissioning: Mar-27 -Cost: $0.4M ± 30% | ERG - North - Herbert
1876363 | 520182 | Distribution Feeder Limitation Address protection, voltage and capacity constraints | MURG - Murgon | Install 7 new fuses and replace existing fuse with solid link switch on 11kV feeder (MG-C). -Target Comissionning: Jul-27 -Cost: $0.35M ± 30% | ERG - South - Fraser Burnett
1604728 | 359549 | Distribution Feeder Limitation Address capacity and reliability constraints | GAYN - Gayndah | Uprate 720m of 11kV conductor and reconductor 280m of 11kV conductor on 11kV feeder Gayndah. -Target Comissioning: Feb-27 -Cost: $0.17M ± 30% | ERG - South - Bundaberg Burnett
1946984 | 568109 | Distribution Feeder Limitation Address capacity constraints | TANB - Tanby | Uprate 3.5km on 11kV conductor, modify protection settings, move fuse and reconfigure network on 22kV feeder (TB223). -Target Comissioning: Mar-27 -Cost: $0.4M ± 30% | ERG - South - Capricornia
1945659 | 565856 | Distribution Feeder Limitation Address reliability and protection constraints | WEWA - Wast Warwick | Install remote controlled gas switch, install two new ACR, install four new fuses, recover two fuses, reconductor 2.1km of conductor and modify protection settings on 11kV feeder (F4115). -Target Comissioning: Jul-27 -Cost: $0.3M ± 30% | ERG - South - Darling Downs
1912540 | 568092 | Distribution Feeder Limitation Address voltage constraints | BARC - Barcaldine | Upgrade SWER regulator, install 1.1km of OHEW and upgrade 1.5km of 19.1kV SWER conductor on 22kV feeder (BB210). -Target Comissioning: May-27 -Cost: $0.34M ± 30% | ERG - South - WZ- Central West
1949796 | 568340 | Distribution Feeder Limitation Address protection, reliability and capacity constraints | BLRI - Black River | Recover ABS and install new NOJA ACR, reconductor 75m of 11kV conductor, install new NOJA ACR, modify protection settings and uprate 2.7km of 11kV conductor. -Target Comissioning: Mar-27 -Cost: $0.36M ± 30% | ERG - North - Herbert
1949797 | 568574 | Distribution Feeder Limitation Address protection, reliability and capacity constraints | BLRI - Black River | Install 10/30K fuses, reconductor 100m of 11kV conductor, replace fuses, uprate 5.6km of conductor on 11kV feeder (BLRI-15). -Target Comissioning: Mar-27 -Cost: $0.28M ± 30% | ERG - North - Herbert
1950408 | 569036 | Distribution Feeder Limitation Address voltage constraints | YEPP - Yeppoon | Upgrade regulator to 100A 11kV closed delta and install new 50A 11kV closed delta regulator on 11kV feeder (YP108). -Target Comissioning: Jun-27 -Cost: $0.16M ± 30% | ERG - South - Capricornia
1945653 | 567842 | Distribution Feeder Limitation Address protection constraints | MERN - Meringandan | Install two new NOJA ACRs, modify protection settings on two NJOA sectionalisers to convert the devices to ACRs, reconductor 820m of 11kV conductor and install four HV fuses on 11kV feeder (F3505). -Target Comissioning: Jan-28 -Cost: $0.3M ± 30% | ERG - South - Darling Downs
1951776 | 569642 | Distribution Feeder Limitation Address reliability issues | WETO - West Toowoomba | Setting change to convert remote controlled gas switch to ACR, reconductor 270m of 11kV conductor and modify protection settings on 11kV feeder (F4650). -Target Comissioning: Apr-27 -Cost: $0.3M ± 30% | ERG - South - Darling Downs
1948556 | 567291 | Distribution Feeder Limitation Address capacity and reliability constraints | WETO - West Toowoomba | Replace manual gas switch with NOJA LBS, install new manual gas switch, reconfigure network, uprate 1.4km of 11kV conductor, reconductor 200m of 11kV conductor and modify protection settings for 11kV feeder (F4555). -Target Comissioning: Feb-27 -Cost: $0.3M ± 30% | ERG - South - Darling Downs
1958573 | 574825 | Distribution Feeder Limitation Address capacity and voltage constraints | CLER - Clermont | Uprate 1.4km of 11kV conductor, install new 50A SWER regulator and install 560m of OHEW on 22kV feeder (CL203). -Target Comissioning: Jun-27 -Cost: $0.2M ± 30% | ERG - South - WZ- Central West
1951239 | 575284 | Distribution Feeder Limitation Address capacity constraints | TORQ - Torquay | install 350m of 11kV underground cable on 11kV feeder (TQ-D). -Target Comissioning: Jul-27 -Cost: $0.14M ± 30% | ERG - South - Fraser Burnett
1961302 | 577666 | Distribution Feeder Limitation Address voltage constraints | BARC - Barcaldine | Reconductor 6km of SWER 19.1kV, install a 19.1kV 50A regulator and install 1.9km of OHEW on 22kV feeder (BB208). -Target Comissioning: Jul-27 -Cost: $0.27M ± 30% | ERG - South - WZ- Central West
1935392 | 556175 | Distribution Feeder Limitation Address protection constraints | MACT - Mackay City | Install a new NOJA ACR with remote communications. -Target Comissioning: May-27 -Cost: $0.12M ± 30% | ERG - North - Pioneer
1961326 | 578348 | Distribution Feeder Limitation Address capacity constraints | SOBL - South Blackwater | Install 13km of SWER conductor, a 200kVA isolator, 2 regulators, one ACR, 2 HV fuses and reconfigure network on 22kV feeder (SB202). -Target Comissioning: Feb-27 -Cost: $0.9M ± 30% | ERG - South - Central West
1944563 | 571460 | Distribution Feeder Limitation Address protection and voltage constraints | MASO - Marion South | Upgrade regulator, install 3 new three-phase ACRs and install 3 new HV fuses on 11kV feeder (14108). -Target Comissioning: May-27 -Cost: $0.25M ± 30% | ERG - North - Pioneer
1976044 | 586888 | Distribution Feeder Limitation Address capacity constraints | ROST - Rocky St | Replace existing 100A regulator with a 200A close delta regulator with comms and SCADA. -Target Comissioning: Aug-27 -Cost: $0.1M ± 30% | ERG - South - Fraser Burnett
1953632 | 571372 | Distribution Feeder Limitation Address reliability and protection constraints | WOWA - Wowan | Reconductor 3.4km of 22kV conductor, replace three-phase 22kV ACR, replace gas switch with recloser, upgrade fuse to 10K and install 3/10K fuse on 22kV feeder (WN211). -Target Comissioning: Mar-27 -Cost: $0.42M ± 30% | ERG - South - Capricornia
1951755 | 570964 | Distribution Feeder Limitation Address reliability and protection constraints | WOWA - Wowan | Install 3 new 22kV 3 phase ACR w VT, Recover one fuse, replace two 20K fuses, replace one 6/20K fuse, Replace one 3/10K fuse, assess and replace other fuses and replace links with a 31.5K fuse on 22kV Baralaba (WN212) Feeder. - Target Commissioning: Dec-27 - Cost: $0.4M ± 30% | ERG - South - Capricornia
1961564 | 576380 | Distribution Feeder Limitation Address voltage constraints | NEBO - Nebo | Install three new 19.1kV 50A SWER regulator w remonte comms, recover two exsiting 11kV 50A VR, install new 200kVA 11/19.1kV SWER isolating TX and relocated exsiting SWER tee-off on 11kV Nebo (210) Feeder. - Target Commissioning: Nov-27 - Cost: $0.6M ± 30% | ERG - North - Pioneer
1961565 | 576309 | Distribution Feeder Limitation Address reliability and protection constraints | PINN - Pinnacle | Recover & install new upgraded support pole, upgrade existing 50A VR from two-tank to 100A three-tank VR and upgrade to CL-7 controller on 11kV Gargett (352) Feeder. - Target Commissioning: Nov-27 - Cost: $0.4M ± 30% | ERG - North - Pioneer
1956214 | 573615 | Distribution Feeder Limitation Address reliability and protection constraints | ETON - Eton | Reconductor 0.85km, install 4 new fuses, instal 2 new ACRs, recover and install one Regulator and setting changes on existing protection on 11kV Hannans Rd (388) Feeder. - Target Commissioning: Oct-27 - Cost: $0.9M ± 30% | ERG - North - Pioneer
1870631 | 576674 | Distribution Feeder Limitation Address capacity constraints | BLRI - Black River | Uprate 0.71km of conductor, reconductor 0.06km, install new ACR, install one fuse, recover one switch and complete network reconfiguration on 11kV Black River No.8 (BLRI-08) Feeder - Target Commissioning: Nov-27 - Cost: $0.3M ± 30% | ERG - North - Herbert
1965181 | 578406 | Distribution Feeder Limitation Address capacity and protection constraints | CHIN - Chinchilla | Install new 12.7kV SWER ACR, adjust existing SWER ACR settings on 33kV Brigalow (F069C) Feeder - Target Commissioning: Nov-27 - Cost: $0.2M ± 30% | ERG - South - WZ - South West
1965184 | 578358 | Distribution Feeder Limitation Address protection, voltage and capacity constraints | CHTW - Chinchilla Town | Install a new 50A 12.7kVA SWER VR, Recover S295 and install a new 12.7kV SWER ACR, recover DO & install a new 12.7kV SWER ACR and change ACR settings on 33kV Rywung (F071C) Feeder - Target Commissioning: Jan-28 - Cost: $0.4M ± 30% | ERG - South - WZ - South West
1965183 | 578339 | Distribution Feeder Limitation Address capacity and protection constraints | CUNN - Cunnamulla | Install two new 19.1kV SWER ACRs, relocate existing SWER ACR and update existing SWER ACR settings on 22kV South East Rural (F306C) Feeder - Target Commissioning: Apr-28 - Cost: $0.11M ± 30% | ERG - South - WZ - South West
1993049 | 592315 | Distribution Feeder Limitation Address capacity and protection constraints | PLEY - Pleystone | Uprate 3.1km of conductor, reconductor 1.21km, install 20K,16K,31.5K & 10/30K fuses, and updated protection settings on 11kV Walkerston (4001) Feeder - Target Commissioning: Jul-28 - Cost: $0.6M ± 30% | ERG - North - Pioneer
2017746 | 605287 | Distribution Feeder Limitation Address voltage constraints | MALC - Malchi | Install new 50A SWER regulator w CL-7 controller w comms and recover existing links on 11kV Stanwell (MA111) feeder. - Target Commissioning: Jan-28 - Cost: $0.3M ± 30% | ERG - South - Capricornia
1964381 | 577883 | Distribution Feeder Limitation Address reliability issues | STUA - Stuart | Reconductor 5.8km, Uprate 0.3km of conductor, Update regulator to 200A closed Delta w CL7 multiphase controller, Install 3 new 6/20K fuse, install 2 new 12K fuses, install new 20K fuse, replace existing 31.5K fuse with solid links on 11kV Serene Valley (ST-05) feeder. - Target Commissioning: Jul-27 - Cost: $0.9M ± 30% | ERG - North - Herbert
1975609 | 587994 | Distribution Feeder Limitation Address capacity and reliability constraints | NOMA - North Mackay | Uprate 3.51km of conductor, replace solid links w 6/20K EDO, instal new 6/20K EDO, install 2 new 16K EDOs, recover and reinstall exisiting EDO on new pole and transfer loads on Beaconsfield feeder downstream to Glenella's Richmond feeder on 11kV Beaconsfield RD (323) Feeder - Target Commissioning: Jul-27 - Cost : $0.5M ± 30% | ERG - North - Pioneer
2018565 | 606107 | Distribution Feeder Limitation Address voltage constraints | PAND - Pandoin | Install 50A SWER regulator & CL-7 controller with comms on a pole on 22kV Alton Downs (PD203) Feeder - Target Commissioning: Jun-28 - Cost : $0.4M ± 30% | ERG - South - Capricornia
1965186 | 578383 | Distribution Feeder Limitation Address capacity and protection constraints | SAGE - Saint George | Install 2 new 19.1kV SWER ACRs, update protection settings and bypass fuses on 33kV St George Meatworks (F079S) Feeder - Target Commissioning: Jan-28 - Cost : $0.32M ± 30% | ERG - South - WZ - South West
2021721 | 403876 | Distribution Feeder Limitation Address voltage constraints | PAND - Pandoin | Install 50A SWER regulator & CL-7 controller with comms on a pole on 22kV Alton Downs (PD209) Feeder - Target Commissioning: Dec-27 - Cost : $0.3M ± 30% | ERG - South - Capricornia
2000242 | 595281 | Distribution Feeder Limitation Address capacity constraints | RASM - Rasmussen | Uprate 0.17km of conductor, install 0.550km of cable, switch open and closed LBS on 11kV Rasmussen (RM-05) Feeder - Target Commissioning: Dec-27 - Cost : $0.7M ± 30% | ERG - North - Herbert
1995491 | 595308 | Distribution Feeder Limitation Address capacity constraints | RASM - Rasmussen | Uprate 0.94km of conductor, Install 0.055km of conductor, install 0.210km of cable, install one gas switch and open and close LBS on 11kV Rasmussen (RM-04) Feeder - Target Commissioning: Nov-27 - Cost : $0.5M ± 30% | ERG - North - Herbert
1649778 | 516781 | Distribution Feeder Limitation Address capacity and reliability constraints | SAGE - Saint George | Install three 33kV 100A Voltage reglators and change regulator and protection settings on 11kV Main Camp (F077S) Feeder - Target Commissioning: Jan-28 - Cost : $0.7M ± 30% | ERG - South - WZ - South West
2009278 | 600122 | Distribution Feeder Limitation Address voltage constraints | KING - Kingaroy | Relocation of two poles and update VR settings on 11kV Kumbia (KR-E) Feeder - Target Commissioning: Feb-28 - Cost : $0.4M ± 30% | ERG - South - Fraser Burnett
2009279 | 599889 | Distribution Feeder Limitation Address reliability and voltage constraints | KING - Kingaroy | Reconductor 3.8km on 11kV Kumbia (KR-E) Feeder - Target Commissioning: Jun-28 - Cost : $0.7M ± 30% | ERG - South - Fraser Burnett
1936668 | 576255 | Distribution Feeder Limitation Address capacity and protection constraints | MORA - Moranbah | Recover and Replace 0.05km of cable, uprate 0.63km of 11kV conductor, Install 0.1km of conductor, Install 4 switches (1 solid link, 3 gas), recover 2 fuses and one gas switch on 11kV Township Feeders No.1,2,3,5,6 (215, 216, 212, 417, 1988) - Target Commissioning: Dec-27 - Cost : $0.66M ± 30% | ERG - North - Pioneer
1965185 | 578367 | Distribution Feeder Limitation Address capacity and protection constraints | ROMA - Roma | Recover exisitng SWER ACR, Install two 12.7kV SWER ACRs, Install 200kVA TX, Reconductor 3.3km of conductor and update protection settings on 12.7kV SWER North Wallumbilla (F001R) Feeder - Target Commissioning: Mar-28 - Cost : $0.4M ± 30% | ERG - South - WZ - South West
1944842 | 565844 | Distribution Feeder Limitation Address reliability issues | HOWA - Burrum Heads | Reconductor 5km of single phase to 3 phase, Uprate 1.3km of conductor, Extend 1.2km of conductor to create tie between HOWA & Burrun Head feeders, Install two ACRS and install 3 11kV 200A Voltage regulators on 11kV Burrum Heads (HD-D) Feeder - Target Commissioning: May-28 - Cost : $1.5M ± 30% | ERG - South - Fraser Burnett
2044397 | 623393 | Distribution Feeder Limitation Address protection constraints | MOBA - Mount Bassett | Reconductor 0.34km on 11kV Harbour (321) Feeder - Target Commissioning: Aug-29 - Cost : $0.2M ± 30% | ERG - North - Pioneer
1944830 | 565878 | Distribution Feeder Limitation Address reliability issues | YARR - Yarraman | Reconductor 3.6km on 11kV Blackbutt (YR-E) Feeder - Target Commissioning: Dec-29 - Cost : $0.5M ± 30% | ERG - South - Fraser Burnett
1960936 | 580512 | Distribution Feeder Limitation Address capacity and protection constraints | BOHL - Bohle | Recover existing LBS, install ACR with VT on 11kV Bohle 11 Feeder - Target Commissioning: Jun-28 -Cost : $0.23M ± 30% | ERG - North - Herbert