## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extend that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
The Network Modeling Team makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be taken into account when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modeling Team obtain these forecast values as populated by the Strategic Forecasting Team, the accuracy of these values are as per their quality assurance processes.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The studies results contained are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using PowerFactory 2024 SP5. The reported studies were calculated in PowerFactory 2024 SP5
· For the Energex network the model is running from External Grids representing the Powerlink Network at the common coupling points.
· For the Ergon network the model is running using the current years Powerlink Transmission TAPR model connected to the Ergon Subtransmission Model at the points of connection between the two utilities.
· The Mount Isa North West Power System network is running self contained within the Ergon Subtransmission model and is supplied by the large required generators in the system
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model as required by the study (most generation is excluded due to current settings)
· The Forecasts are extracted from SIFT or Tableau depending on where the current data is stored. 10PoE and 50PoE Forecasts from SIFT the Minimum Forecasts and Ergon Energy Daily Load Profiles are from Tableau
· Python automation was used to pull demand forecasts into PowerFactory model
· Load Flow studies were run for each of the following senarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLF_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Export Packaged Master Model
2. Import and Activate Extracted Model
3. Activate Load Characterstic Application Study Case
4. Run appropraite Forecast Load script for the given study
5. Run the DAPR Feeder Association Script to identify elements required for the new Feeder Voltage Attributes
6. Run The Setup Task Automation Script to create the command required for each individual year/Time Combination
7. Run the Task Automation Command with Parallel Computing turned on to calculate multiple studies at once
7. Repeat 4-6 for other characterstic combinations (such as SEQ Night Forecasts after running SEQ Day forecasts) required in the report.
8. Run a Python Interpreter that reads the output files and produces the formatted document
This entire process is completed with the RunExternalPowerFactoryGooey custom tool to run PowerFactory in external mode to minimise failed calculations due to momentary license outages.
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.
NNC | Normal Network Configuration
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor at the constrained conductor. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.

## Important Info-10POE_EE_NNC
2. Important Information
2.1 Study Information - 10PoE_EE_NNC - Known Issues and Limitations
· The List of Subtransmission Projects to be stored as Variations has been produced manually from Copperleaf for the next 10 years.
· This report does not offer details of active Generators considered for each project
· Time Periods are based on Day (6am-5pm), Evening (5pm-10pm) and Night. This means that SN sift forecasts run at 7:30pm will be labelled as SE. This is unlikely to change
3. Additional Information
3.1 Information About Variables
The Values for a given timeslot shown are calculated as follows. All of the values will be for the line element in PowerFactory with the Loading Constraint.
This means that the Power Factor and Voltage values are recorded at the line that is considered the most "limited" not the minimum voltage on the feeder or the minimum Power Factor on the feeder
For each Contingency Event the values for each line are recorded with them eventually ending up in the following fields
% of Rated A: The % Utilisation called "loading" in PowerFactory [c:loading]
Limiting Line Name: The name of the line the results come from. It is nominally the most constrainted line. See later information for more details
Loading (A): Absolute Maximum Current for Both Ends in kA
Loading (MVA): Absolute Maximum Apparent Power for Both Ends in MVA
Loading (MW): Absolute Maximum Real Power for Both Ends in MW
Power Factor: Absolute Min PowerFactor for Both Ends
Rating (A): Line Nominal Rating using [e:Inom_a]
Time: The time at which the limiting study was completed
Min Voltage at Constrained Conductor: Min Voltage seen on both sides of line for the constrained line
Min Feeder Voltage: The minimum voltage seen on the ElmFeeder object associated with the line. Includes Open End Branch voltages and Feeder End Terminals
Min Feeder End Terminal Voltage: The Feeder voltage at the end terminals of a feeder. Does not include Open End Branches
Min Feeder Associated Sift-Load or Customer Terminal Voltage: The minimum voltage at terminals connected to a SIFT-load that the ElmFeeder can get to without traversing another feeder or at the Terminal Connected to a Customer site with an ElmOwner association starting with NMI_
Min Feeder Voltage at MV Connected TXs: The Minimum Voltage at any MV Terminals of Transformers within the ElmFeeder object
Once they are calculated for each feeder and Timeslot the Limiting entry is determined. This will be the values for a single line limited in the following order.
At each step all lines that share the "limiting" value will be recorded, provided their float representative is identical.
Minor differences in the float representation will result in the Min or Max value being utilised even if the value when considering real life significant figures are otherwise identical
1. % of Rated A - Max
2. Rating (A) - Min
3. Loading (MVA) - Max
The following limit calculations are applied to ensure only 1 line's values are recorded even if all entries have the same electrical loading characteristics
4. For N-1 results. Contingency Outage: Alphabetical Max
Note that "_NNC" is used with is a "Normal Network Configuration" contingency where nothing is taken out of service. If it is displayed then taking a feeder out of service did not make a recordable difference to the feeder loading.
If multiple feeder outage contingencies have the same affect on the feeder then the higher alphabetical name will be recorded.
5. Limiting Line Name: Alphabetical Min: This is to ensure there is a unique value
6. Current Study Case Time: Alphabetical Min: This is a stopgap to ensure there is a unique value

## 10PoE_EE_NNC_2025
Region | PF Feeder Obj Name | Variable | 2026 SD | 2026 SE | 2026 SN | 2027 SD | 2027 SE | 2027 SN | 2028 SD | 2028 SE | 2028 SN | 2029 SD | 2029 SE | 2029 SN | 2030 SD | 2030 SE | 2030 SN
CA | 6011_Blackwater - Comet 66 kV | % of Rated A | 67.29% | 64.17% | 47.45% | 67.29% | 64.17% | 47.47% | 67.46% | 64.32% | 47.57% | 67.12% | 64.02% | 47.39% | 68.85% | 65.58% | 48.39%
CA | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1
CA | 6011_Blackwater - Comet 66 kV | Loading (A) | 186.3892 | 189.304 | 124.8022 | 186.3805 | 189.2924 | 124.8391 | 186.8537 | 189.7449 | 125.1002 | 185.933 | 188.8681 | 124.6252 | 190.7206 | 193.4493 | 127.2624
CA | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 22.1309 | 22.6612 | 15.0211 | 22.1321 | 22.6623 | 15.0257 | 22.1873 | 22.7155 | 15.057 | 22.0823 | 22.6151 | 15.0004 | 22.6335 | 23.1463 | 15.3147
CA | 6011_Blackwater - Comet 66 kV | Loading (MW) | 22.0802 | 22.5856 | 14.5324 | 22.0808 | 22.5858 | 14.5369 | 22.1375 | 22.6408 | 14.5706 | 22.0289 | 22.5361 | 14.5091 | 22.5977 | 23.0887 | 14.8578
CA | 6011_Blackwater - Comet 66 kV | Power Factor | 0.9977 | 0.99665 | 0.96746 | 0.99767 | 0.99662 | 0.96745 | 0.99775 | 0.9967 | 0.96769 | 0.99757 | 0.9965 | 0.96723 | 0.99841 | 0.9975 | 0.97015
CA | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 6011_Blackwater - Comet 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6011_Blackwater - Comet 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0385 | 1.0471 | 1.0528 | 1.0387 | 1.0472 | 1.0528 | 1.0386 | 1.0471 | 1.0528 | 1.0388 | 1.0473 | 1.0529 | 1.038 | 1.0466 | 1.0526
CA | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 44.64% | 41.28% | 37.51% | 44.64% | 41.28% | 37.51% | 44.64% | 41.28% | 37.51% | 44.63% | 41.27% | 37.51% | 45% | 41.61% | 37.77%
CA | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 124.102 | 122.1958 | 99.029 | 124.0879 | 122.1812 | 99.0277 | 124.0942 | 122.1873 | 99.0287 | 124.0664 | 122.1645 | 99.0241 | 125.087 | 123.1511 | 99.7114
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 14.3892 | 14.2039 | 11.7005 | 14.3891 | 14.2038 | 11.7005 | 14.3892 | 14.2038 | 11.7005 | 14.389 | 14.2037 | 11.7005 | 14.4929 | 14.3048 | 11.7777
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 13.6578 | 13.4852 | 11.1291 | 13.6578 | 13.4852 | 11.1291 | 13.6578 | 13.4852 | 11.1291 | 13.6578 | 13.4851 | 11.1291 | 13.7549 | 13.5796 | 11.202
CA | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.94917 | 0.9494 | 0.95116 | 0.94918 | 0.94941 | 0.95116 | 0.94918 | 0.9494 | 0.95116 | 0.94919 | 0.94941 | 0.95116 | 0.94908 | 0.94931 | 0.95111
CA | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 6012_Blackwater - Bedford Weir 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
CA | 6012_Blackwater - Bedford Weir 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0142 | 1.0167 | 1.0335 | 1.0143 | 1.0168 | 1.0335 | 1.0142 | 1.0168 | 1.0335 | 1.0144 | 1.017 | 1.0335 | 1.0134 | 1.016 | 1.0332
CA | 6014_Blackwater - South Blackwater 66 kV | % of Rated A | 12.34% | 10.14% | 13.22% | 12.34% | 10.14% | 13.22% | 12.34% | 10.14% | 13.22% | 12.34% | 10.14% | 13.22% | 12.34% | 10.15% | 13.22%
CA | 6014_Blackwater - South Blackwater 66 kV | Limiting Line Name | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (A) | 61.4514 | 55.6806 | 65.8332 | 61.4508 | 55.6763 | 65.8354 | 61.4511 | 55.6789 | 65.8358 | 61.4494 | 55.667 | 65.834 | 61.459 | 55.7095 | 65.8386
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MVA) | 7.2976 | 6.5737 | 7.8123 | 7.2976 | 6.5737 | 7.8123 | 7.2976 | 6.5737 | 7.8123 | 7.2976 | 6.5737 | 7.8123 | 7.2977 | 6.5739 | 7.8123
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MW) | 6.662 | 6.0082 | 7.1261 | 6.662 | 6.0082 | 7.1261 | 6.662 | 6.0082 | 7.1261 | 6.662 | 6.0082 | 7.1261 | 6.662 | 6.0083 | 7.1261
CA | 6014_Blackwater - South Blackwater 66 kV | Power Factor | 0.90755 | 0.90911 | 0.90643 | 0.90755 | 0.90912 | 0.90643 | 0.90755 | 0.90911 | 0.90643 | 0.90755 | 0.90912 | 0.90643 | 0.90755 | 0.90909 | 0.90643
CA | 6014_Blackwater - South Blackwater 66 kV | Rating (A) | 498 | 549 | 498 | 498 | 549 | 498 | 498 | 549 | 498 | 498 | 549 | 498 | 498 | 549 | 498
CA | 6014_Blackwater - South Blackwater 66 kV | Time | 07:30:00 | 18:30:00 | 03:30:00 | 07:30:00 | 18:30:00 | 03:30:00 | 07:30:00 | 18:30:00 | 03:30:00 | 07:30:00 | 18:30:00 | 03:30:00 | 07:30:00 | 18:30:00 | 03:30:00
CA | 6014_Blackwater - South Blackwater 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0388 | 1.0328 | 1.0381 | 1.0388 | 1.0328 | 1.038 | 1.0388 | 1.0328 | 1.038 | 1.0389 | 1.033 | 1.0381 | 1.0387 | 1.0323 | 1.038
CA | 6056_Comet - Emerald 66 kV | % of Rated A | 58.7% | 56.16% | 40.69% | 58.7% | 56.16% | 40.7% | 58.86% | 56.3% | 40.8% | 58.55% | 56.03% | 40.63% | 59.95% | 57.27% | 41.38%
CA | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1
CA | 6056_Comet - Emerald 66 kV | Loading (A) | 162.5953 | 165.6676 | 107.0172 | 162.5977 | 165.6685 | 107.0541 | 163.0456 | 166.0965 | 107.2939 | 162.1852 | 165.2791 | 106.8607 | 166.0479 | 168.9518 | 108.8299
CA | 6056_Comet - Emerald 66 kV | Loading (MVA) | 18.6113 | 19.1324 | 12.6761 | 18.6141 | 19.1354 | 12.6806 | 18.6614 | 19.181 | 12.708 | 18.5733 | 19.0969 | 12.659 | 18.9658 | 19.4722 | 12.8783
CA | 6056_Comet - Emerald 66 kV | Loading (MW) | 18.093 | 18.5267 | 11.3218 | 18.0937 | 18.5271 | 11.326 | 18.1457 | 18.5775 | 11.358 | 18.0463 | 18.4816 | 11.2997 | 18.4817 | 18.9006 | 11.5525
CA | 6056_Comet - Emerald 66 kV | Power Factor | 0.97214 | 0.96833 | 0.89315 | 0.97203 | 0.9682 | 0.89317 | 0.97236 | 0.96852 | 0.89377 | 0.97162 | 0.96777 | 0.89262 | 0.97446 | 0.97063 | 0.89705
CA | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 6056_Comet - Emerald 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6056_Comet - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0013 | 1.0102 | 1.0362 | 1.0014 | 1.0104 | 1.0362 | 1.0012 | 1.0102 | 1.0361 | 1.0018 | 1.0107 | 1.0363 | 0.99913 | 1.0082 | 1.0351
CA | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 13.94% | 13.4% | 13.85% | 13.94% | 13.4% | 13.85% | 13.94% | 13.4% | 13.85% | 13.94% | 13.4% | 13.85% | 13.95% | 13.41% | 13.86%
CA | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 38.7556 | 39.6761 | 36.5693 | 38.751 | 39.6707 | 36.5688 | 38.753 | 39.6725 | 36.5692 | 38.744 | 39.6637 | 36.5674 | 38.7867 | 39.7045 | 36.5813
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 4.4396 | 4.5695 | 4.273 | 4.4396 | 4.5694 | 4.273 | 4.4396 | 4.5695 | 4.273 | 4.4395 | 4.5694 | 4.273 | 4.4399 | 4.5697 | 4.2731
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 4.0589 | 4.1975 | 3.9041 | 4.0589 | 4.1975 | 3.9041 | 4.0589 | 4.1975 | 3.9041 | 4.0589 | 4.1975 | 3.9041 | 4.0589 | 4.1976 | 3.9041
CA | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.9142 | 0.91855 | 0.91363 | 0.9142 | 0.91856 | 0.91363 | 0.9142 | 0.91856 | 0.91363 | 0.91421 | 0.91857 | 0.91363 | 0.91415 | 0.91851 | 0.91361
CA | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 6058_Bedford Weir - Bingegang 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
CA | 6058_Bedford Weir - Bingegang 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0021 | 1.0075 | 1.0221 | 1.0022 | 1.0076 | 1.0222 | 1.0022 | 1.0076 | 1.0221 | 1.0024 | 1.0078 | 1.0222 | 1.0013 | 1.0068 | 1.0218
CA | 6059_Leichardt - Cook Colliery 66 kV | % of Rated A | 36.07% | 23.41% | 25.4% | 36.07% | 23.41% | 25.4% | 36.07% | 23.41% | 25.4% | 36.06% | 23.41% | 25.4% | 36.08% | 23.42% | 25.4%
CA | 6059_Leichardt - Cook Colliery 66 kV | Limiting Line Name | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (A) | 51.5789 | 49.3993 | 52.8234 | 51.575 | 49.3955 | 52.8252 | 51.5764 | 49.3978 | 52.8255 | 51.5691 | 49.3872 | 52.8241 | 51.5899 | 49.425 | 52.8278
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MVA) | 6.0403 | 5.8044 | 6.2461 | 6.0403 | 5.8043 | 6.2462 | 6.0403 | 5.8044 | 6.2462 | 6.0403 | 5.8043 | 6.2461 | 6.0403 | 5.8045 | 6.2462
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MW) | 5.6913 | 5.4586 | 5.882 | 5.6913 | 5.4586 | 5.882 | 5.6913 | 5.4586 | 5.882 | 5.6913 | 5.4585 | 5.882 | 5.6913 | 5.4586 | 5.882
CA | 6059_Leichardt - Cook Colliery 66 kV | Power Factor | 0.93713 | 0.93557 | 0.93653 | 0.93714 | 0.93557 | 0.93653 | 0.93714 | 0.93557 | 0.93653 | 0.93714 | 0.93558 | 0.93653 | 0.93713 | 0.93555 | 0.93653
CA | 6059_Leichardt - Cook Colliery 66 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
CA | 6059_Leichardt - Cook Colliery 66 kV | Time | 14:30:00 | 18:30:00 | 03:30:00 | 14:30:00 | 18:30:00 | 03:30:00 | 14:30:00 | 18:30:00 | 03:30:00 | 14:30:00 | 18:30:00 | 03:30:00 | 14:30:00 | 18:30:00 | 03:30:00
CA | 6059_Leichardt - Cook Colliery 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0244 | 1.0278 | 1.0344 | 1.0245 | 1.0279 | 1.0343 | 1.0245 | 1.0279 | 1.0343 | 1.0246 | 1.0281 | 1.0344 | 1.0242 | 1.0273 | 1.0343
CA | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 47.62% | 42.66% | 34.86% | 47.61% | 42.65% | 34.86% | 47.61% | 42.66% | 34.86% | 47.6% | 42.65% | 34.86% | 48.4% | 43.35% | 35.28%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 115.7169 | 116.042 | 86.4447 | 115.6938 | 116.0176 | 86.4442 | 115.7029 | 116.0267 | 86.4453 | 115.6651 | 115.9971 | 86.4427 | 117.607 | 117.9253 | 87.4985
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 13.6889 | 13.7482 | 10.3797 | 13.6886 | 13.7478 | 10.3797 | 13.6887 | 13.748 | 10.3797 | 13.6882 | 13.7476 | 10.3796 | 13.9036 | 13.9625 | 10.5052
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 13.2972 | 13.3503 | 10.0792 | 13.297 | 13.3501 | 10.0792 | 13.2971 | 13.3502 | 10.0792 | 13.2968 | 13.3499 | 10.0792 | 13.5053 | 13.5581 | 10.2022
CA | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.97138 | 0.97106 | 0.97002 | 0.97139 | 0.97107 | 0.97002 | 0.97139 | 0.97106 | 0.97002 | 0.97141 | 0.97108 | 0.97002 | 0.97135 | 0.97103 | 0.97017
CA | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 6065_Lilyvale - Tieri Tee 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
CA | 6065_Lilyvale - Tieri Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0287 | 1.0302 | 1.0469 | 1.0289 | 1.0304 | 1.0469 | 1.0288 | 1.0304 | 1.0469 | 1.0291 | 1.0306 | 1.0469 | 1.0279 | 1.0294 | 1.0467
CA | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 81.69% | 60.71% | 43.06% | 81.67% | 60.7% | 43.05% | 81.85% | 60.83% | 43.13% | 81.47% | 60.55% | 42.97% | 83.2% | 61.84% | 43.72%
CA | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 278.5645 | 273.8208 | 186.03 | 278.5049 | 273.7596 | 185.9936 | 279.1033 | 274.3477 | 186.3232 | 277.8211 | 273.093 | 185.6159 | 283.7064 | 278.8815 | 188.8896
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 32.9872 | 32.4774 | 22.402 | 32.9858 | 32.476 | 22.3977 | 33.0536 | 32.5427 | 22.4371 | 32.9127 | 32.4027 | 22.3526 | 33.5672 | 33.0492 | 22.7436
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 32.7398 | 32.2552 | 22.3531 | 32.7383 | 32.2537 | 22.3489 | 32.8006 | 32.3153 | 22.3898 | 32.6706 | 32.1854 | 22.3023 | 33.2704 | 32.7807 | 22.7073
CA | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.9925 | 0.99316 | 0.99032 | 0.9925 | 0.99315 | 0.99033 | 0.99235 | 0.99301 | 0.99044 | 0.99264 | 0.99329 | 0.99023 | 0.99116 | 0.99187 | 0.9913
CA | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432
CA | 6067 Lilyvale - Emerald 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
CA | 6067 Lilyvale - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97674 | 0.97999 | 1.0311 | 0.97692 | 0.98018 | 1.0311 | 0.97655 | 0.97981 | 1.0309 | 0.97746 | 0.98065 | 1.0313 | 0.9734 | 0.97671 | 1.0296
CA | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 83.41% | 91.97% | 62.43% | 82.17% | 92.44% | 61.74% | 82.18% | 92.45% | 61.74% | 81.04% | 91.07% | 61.07% | 83.24% | 91.79% | 62.37%
CA | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1
CA | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 83.4111 | 91.9727 | 62.4308 | 82.1738 | 92.4441 | 61.7354 | 82.1808 | 92.4534 | 61.7355 | 81.0366 | 91.0742 | 61.0664 | 83.2434 | 91.7896 | 62.3721
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 9.9603 | 10.9821 | 7.4546 | 9.8583 | 11.0071 | 7.3843 | 9.8584 | 11.0072 | 7.3843 | 9.7573 | 10.8903 | 7.3145 | 9.9588 | 11.1006 | 7.4544
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 9.9527 | 10.9818 | 7.3857 | 9.8485 | 11.0069 | 7.3122 | 9.8486 | 11.007 | 7.3122 | 9.745 | 10.8896 | 7.2385 | 9.9507 | 11.0999 | 7.3856
CA | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.99923 | 0.99997 | 0.99076 | 0.99901 | 0.99998 | 0.99022 | 0.99901 | 0.99998 | 0.99022 | 0.99874 | 0.99994 | 0.9896 | 0.99918 | 0.99994 | 0.99077
CA | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CA | 6079_Barcaldine - Longreach 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6079_Barcaldine - Longreach 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0446 | 1.0445 | 1.0445 | 1.0494 | 1.0416 | 1.0463 | 1.0494 | 1.0415 | 1.0463 | 1.0533 | 1.046 | 1.0478 | 1.0465 | 1.0579 | 1.0455
CA | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 11.85% | 12.78% | 9.414% | 11.57% | 12.63% | 9.252% | 11.57% | 12.63% | 9.252% | 11.53% | 12.58% | 9.243% | 11.6% | 12.65% | 9.257%
CA | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 22366_1 | TR_LINE 22366_1 | TR_LINE 22558_1 | TR_LINE 22366_1 | TR_LINE 22366_1 | TR_LINE 22558_1 | TR_LINE 22366_1 | TR_LINE 22366_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22366_1 | TR_LINE 22558_1 | TR_LINE 22366_1 | TR_LINE 22366_1 | TR_LINE 22558_1
CA | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 44.3258 | 49.2105 | 31.8191 | 43.2806 | 48.6317 | 31.2701 | 43.2842 | 48.6362 | 31.2702 | 43.1392 | 48.4401 | 31.2414 | 43.3987 | 48.7041 | 31.2898
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 4.9853 | 5.4856 | 3.7278 | 4.8939 | 5.4268 | 3.6693 | 4.8939 | 5.4268 | 3.6693 | 4.9882 | 5.4273 | 3.6705 | 4.894 | 5.4269 | 3.6691
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 4.9713 | 5.4691 | 3.5524 | 4.8806 | 5.4106 | 3.4863 | 4.8806 | 5.4106 | 3.4863 | 4.9742 | 5.4109 | 3.4861 | 4.8806 | 5.4107 | 3.4863
CA | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.99719 | 0.99698 | 0.95296 | 0.99726 | 0.99701 | 0.95012 | 0.99726 | 0.99701 | 0.95012 | 0.99719 | 0.99697 | 0.94977 | 0.99724 | 0.997 | 0.95016
CA | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 374 | 385 | 338 | 374 | 385 | 338 | 374 | 385 | 338 | 374 | 385 | 338 | 374 | 385 | 338
CA | 6080_Barcaldine - Blackall 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6080_Barcaldine - Blackall 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98383 | 0.97512 | 1.0248 | 0.98913 | 0.97614 | 1.0265 | 0.98905 | 0.97605 | 1.0265 | 1.0061 | 0.98009 | 1.0277 | 0.98647 | 0.9747 | 1.0258
CA | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 8.048% | 7.214% | 4.49% | 8.046% | 7.213% | 4.49% | 8.047% | 7.214% | 4.49% | 8.045% | 7.212% | 4.49% | 8.407% | 7.536% | 4.687%
CA | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 19.5564 | 19.6234 | 11.1362 | 19.5528 | 19.6196 | 11.1362 | 19.5542 | 19.621 | 11.1363 | 19.5484 | 19.6165 | 11.136 | 20.4281 | 20.4979 | 11.6244
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 2.2964 | 2.3077 | 1.3317 | 2.2964 | 2.3077 | 1.3317 | 2.2964 | 2.3077 | 1.3317 | 2.2964 | 2.3077 | 1.3317 | 2.3967 | 2.4085 | 1.3898
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 2.2619 | 2.273 | 1.3127 | 2.2619 | 2.273 | 1.3127 | 2.2619 | 2.273 | 1.3127 | 2.2619 | 2.273 | 1.3127 | 2.3605 | 2.3721 | 1.3699
CA | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.98383 | 0.98383 | 0.98512 | 0.98383 | 0.98383 | 0.98512 | 0.98383 | 0.98383 | 0.98512 | 0.98384 | 0.98383 | 0.98512 | 0.9837 | 0.9837 | 0.98503
CA | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 6085_Tieri Tee - Tieri 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
CA | 6085_Tieri Tee - Tieri 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0272 | 1.0287 | 1.0461 | 1.0274 | 1.0289 | 1.0461 | 1.0273 | 1.0289 | 1.0461 | 1.0276 | 1.0291 | 1.0461 | 1.0263 | 1.0279 | 1.0458
CA | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 40.25% | 38.19% | 31.08% | 40.24% | 38.18% | 31.08% | 40.24% | 38.18% | 31.08% | 40.23% | 38.17% | 31.08% | 40.66% | 38.58% | 31.31%
CA | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 97.8006 | 98.1475 | 77.0762 | 97.7811 | 98.1254 | 77.0757 | 97.7888 | 98.1332 | 77.0767 | 97.7568 | 98.0997 | 77.0744 | 98.8157 | 99.1612 | 77.637
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 11.2037 | 11.2976 | 9.0204 | 11.2036 | 11.2974 | 9.0204 | 11.2036 | 11.2975 | 9.0204 | 11.2034 | 11.2973 | 9.0204 | 11.3085 | 11.4025 | 9.0836
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 10.762 | 10.852 | 8.6015 | 10.7619 | 10.8519 | 8.6015 | 10.762 | 10.852 | 8.6015 | 10.7619 | 10.8519 | 8.6015 | 10.8649 | 10.955 | 8.6645
CA | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.95981 | 0.96028 | 0.95118 | 0.95982 | 0.96028 | 0.95118 | 0.95982 | 0.96028 | 0.95118 | 0.95982 | 0.96029 | 0.95118 | 0.96007 | 0.96047 | 0.95154
CA | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248
CA | 6086_Tieri Tee - Middlemount 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
CA | 6086_Tieri Tee - Middlemount 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99584 | 1.0069 | 1.0207 | 0.99603 | 1.0071 | 1.0207 | 0.99595 | 1.0071 | 1.0207 | 0.99627 | 1.0074 | 1.0207 | 0.99468 | 1.0059 | 1.0203
CA | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 28.7% | 29.64% | 25.94% | 28.51% | 29.43% | 25.84% | 28.51% | 29.43% | 25.84% | 28.33% | 29.23% | 25.75% | 28.64% | 29.57% | 25.91%
CA | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 203.1786 | 214.5785 | 165.2309 | 201.8678 | 213.0956 | 164.6185 | 201.8754 | 213.1053 | 164.6185 | 200.6057 | 211.6283 | 164.0073 | 202.7914 | 214.1012 | 165.0544
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 48.6526 | 51.4691 | 40.0111 | 48.3466 | 51.1189 | 39.8631 | 48.3463 | 51.1191 | 39.863 | 48.0531 | 50.7767 | 39.7153 | 48.5407 | 51.3347 | 39.968
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 48.1654 | 51.2815 | 36.9663 | 47.794 | 50.9067 | 36.7397 | 47.7945 | 50.9073 | 36.7397 | 47.4431 | 50.5242 | 36.52 | 48.027 | 51.1344 | 36.8888
CA | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.98999 | 0.99636 | 0.9239 | 0.98857 | 0.99585 | 0.92165 | 0.98859 | 0.99586 | 0.92165 | 0.98731 | 0.99503 | 0.91955 | 0.98942 | 0.9961 | 0.92296
CA | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637
CA | 7153_Lilyvale - Clermont 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 7153_Lilyvale - Clermont 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0443 | 1.0444 | 1.0591 | 1.0448 | 1.0447 | 1.0591 | 1.0447 | 1.0446 | 1.0591 | 1.0452 | 1.0451 | 1.0592 | 1.044 | 1.0441 | 1.0591
CA | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 31.34% | 30.65% | 25.9% | 31.02% | 30.29% | 25.79% | 31.02% | 30.29% | 25.79% | 30.81% | 30.05% | 25.71% | 31.14% | 30.43% | 25.82%
CA | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 112.8143 | 119.832 | 90.9236 | 111.6679 | 118.4284 | 90.5055 | 111.671 | 118.4333 | 90.5055 | 110.9152 | 117.4849 | 90.2579 | 112.0973 | 118.9652 | 90.6443
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 26.7044 | 28.2429 | 22.2123 | 26.4631 | 27.9334 | 22.1189 | 26.4625 | 27.9331 | 22.1188 | 26.3109 | 27.7424 | 22.0661 | 26.5349 | 28.037 | 22.1476
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 25.6254 | 27.6201 | 17.5312 | 25.2706 | 27.2644 | 17.3108 | 25.271 | 27.2649 | 17.3108 | 25.0316 | 27.0013 | 17.1623 | 25.3959 | 27.3792 | 17.3906
CA | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.9596 | 0.97795 | 0.78925 | 0.95494 | 0.97605 | 0.78263 | 0.95497 | 0.97608 | 0.78263 | 0.95138 | 0.97329 | 0.77777 | 0.95708 | 0.97654 | 0.78521
CA | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351
CA | 7154_Clermont - Barcaldine 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 7154_Clermont - Barcaldine 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0345 | 1.0296 | 1.0685 | 1.0358 | 1.0305 | 1.0689 | 1.0357 | 1.0304 | 1.0689 | 1.0369 | 1.0317 | 1.0693 | 1.0346 | 1.0296 | 1.0687
CA | 7286_Blackwater - Memooloo 132 kV | % of Rated A | 18.14% | 15.19% | 15.52% | 18.08% | 15.13% | 15.47% | 18.08% | 15.13% | 15.47% | 18.08% | 15.13% | 15.47% | 18.15% | 15.19% | 15.52%
CA | 7286_Blackwater - Memooloo 132 kV | Limiting Line Name | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2
CA | 7286_Blackwater - Memooloo 132 kV | Loading (A) | 127.9015 | 111.6386 | 101.1596 | 127.4851 | 111.1911 | 100.8604 | 127.4897 | 111.1952 | 100.861 | 127.4683 | 111.1759 | 100.8582 | 127.9503 | 111.6803 | 101.1695
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MVA) | 30.1286 | 26.3982 | 24.14 | 30.0353 | 26.297 | 24.0698 | 30.0353 | 26.297 | 24.0699 | 30.0351 | 26.2968 | 24.0698 | 30.1291 | 26.3987 | 24.1401
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MW) | 29.9305 | 26.2209 | 23.939 | 29.8385 | 26.1211 | 23.8697 | 29.8385 | 26.1211 | 23.8697 | 29.8385 | 26.1211 | 23.8697 | 29.9306 | 26.221 | 23.939
CA | 7286_Blackwater - Memooloo 132 kV | Power Factor | 0.99338 | 0.99324 | 0.99164 | 0.99341 | 0.99327 | 0.99165 | 0.9934 | 0.99327 | 0.99165 | 0.99341 | 0.99328 | 0.99165 | 0.99337 | 0.99323 | 0.99163
CA | 7286_Blackwater - Memooloo 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
CA | 7286_Blackwater - Memooloo 132 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
CA | 7286_Blackwater - Memooloo 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0303 | 1.0343 | 1.0437 | 1.0305 | 1.0344 | 1.0438 | 1.0304 | 1.0344 | 1.0438 | 1.0306 | 1.0346 | 1.0438 | 1.0299 | 1.0339 | 1.0437
CA | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 13.48% | 13.3% | 14.3% | 13.44% | 13.25% | 14.26% | 13.44% | 13.25% | 14.26% | 13.44% | 13.24% | 14.26% | 13.49% | 13.31% | 14.3%
CA | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1
CA | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 95.0526 | 97.7864 | 93.251 | 94.7423 | 97.3514 | 92.986 | 94.7437 | 97.3548 | 92.9863 | 94.7355 | 97.3383 | 92.9846 | 95.0715 | 97.8221 | 93.2391
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 22.3286 | 22.9198 | 21.987 | 22.2583 | 22.8219 | 21.9305 | 22.2583 | 22.8219 | 21.9305 | 22.2583 | 22.8218 | 21.9305 | 22.3287 | 22.9199 | 21.987
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 21.5376 | 22.2442 | 21.1352 | 21.467 | 22.1464 | 21.0782 | 21.467 | 22.1464 | 21.0782 | 21.467 | 22.1464 | 21.0782 | 21.5376 | 22.2442 | 21.1352
CA | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.96457 | 0.97052 | 0.96125 | 0.96444 | 0.9704 | 0.96113 | 0.96444 | 0.9704 | 0.96113 | 0.96444 | 0.9704 | 0.96113 | 0.96457 | 0.97052 | 0.96126
CA | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
CA | 7450_Memooloo - Rolleston 132 kV | Time | 13:00:00 | 18:30:00 | 01:00:00 | 13:00:00 | 18:30:00 | 01:00:00 | 13:00:00 | 18:30:00 | 01:00:00 | 13:00:00 | 18:30:00 | 01:00:00 | 13:00:00 | 18:30:00 | 01:00:00
CA | 7450_Memooloo - Rolleston 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0275 | 1.0252 | 1.0313 | 1.0276 | 1.0254 | 1.0316 | 1.0276 | 1.0253 | 1.0316 | 1.0276 | 1.0255 | 1.0316 | 1.0273 | 1.0248 | 1.0314
CA | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 16.42% | 19.65% | 14.95% | 16.56% | 19.88% | 15.76% | 16.82% | 20.26% | 16.03% | 16.99% | 20.51% | 16.21% | 17.02% | 21.15% | 16.63%
CA | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 65.8357 | 82.1453 | 55.6034 | 66.402 | 83.0963 | 58.6377 | 67.462 | 84.6777 | 59.6358 | 68.1411 | 85.7378 | 60.2853 | 68.267 | 88.414 | 61.8584
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 7.7753 | 9.8141 | 6.6185 | 7.8419 | 9.9243 | 7.0126 | 7.9661 | 10.1077 | 7.1296 | 8.0472 | 10.2327 | 7.2071 | 8.1575 | 10.5192 | 7.3842
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 7.4082 | 9.5378 | 6.5681 | 7.4734 | 9.6429 | 6.8017 | 7.589 | 9.8127 | 6.9126 | 7.6681 | 9.9318 | 6.9881 | 7.9354 | 10.2095 | 7.1599
CA | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.94929 | 0.97025 | 0.99038 | 0.94958 | 0.9701 | 0.96652 | 0.94933 | 0.96934 | 0.9661 | 0.94964 | 0.96918 | 0.96621 | 0.97025 | 0.96931 | 0.96638
CA | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6001_Glenmore - Parkhurst 66 kV | Time | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6001_Glenmore - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0327 | 1.0417 | 1.0399 | 1.0326 | 1.0412 | 1.0462 | 1.0323 | 1.0405 | 1.0458 | 1.0323 | 1.0402 | 1.0457 | 1.0437 | 1.0366 | 1.0438
CA | 6003_Glenmore - Berserker 66 kV | % of Rated A | 78.48% | 79.67% | 61.06% | 78.79% | 80.05% | 60.9% | 79.07% | 80.41% | 61.09% | 79.2% | 80.61% | 61.23% | 81.15% | 82.82% | 62.46%
CA | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1
CA | 6003_Glenmore - Berserker 66 kV | Loading (A) | 314.6947 | 333.0366 | 227.1478 | 315.9603 | 334.6284 | 226.5512 | 317.0635 | 336.0942 | 227.263 | 317.6084 | 336.9664 | 227.7595 | 325.4093 | 346.1935 | 232.3475
CA | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 37.8942 | 39.894 | 27.1115 | 38.0374 | 40.0706 | 27.2244 | 38.1555 | 40.2247 | 27.3031 | 38.2191 | 40.3237 | 27.361 | 39.0418 | 41.2905 | 27.8669
CA | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 37.7601 | 39.8423 | 26.4733 | 37.9106 | 40.0245 | 26.7154 | 38.0357 | 40.1842 | 26.8059 | 38.1047 | 40.2875 | 26.8743 | 39.0056 | 41.2885 | 27.5213
CA | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.99644 | 0.99869 | 0.97642 | 0.99664 | 0.99884 | 0.98127 | 0.99684 | 0.99898 | 0.98175 | 0.99698 | 0.99909 | 0.98217 | 0.99906 | 0.99995 | 0.98757
CA | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6003_Glenmore - Berserker 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
CA | 6003_Glenmore - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0532 | 1.0477 | 1.044 | 1.053 | 1.0473 | 1.0511 | 1.0525 | 1.0468 | 1.0509 | 1.0525 | 1.0466 | 1.0508 | 1.0494 | 1.0431 | 1.0491
CA | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 18.13% | 14.44% | 9.981% | 17.92% | 14.23% | 9.078% | 17.69% | 14.02% | 8.952% | 17.49% | 13.82% | 8.841% | 19.71% | 13.93% | 8.857%
CA | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 66.5365 | 53.7002 | 33.7368 | 65.7535 | 52.939 | 30.682 | 64.9401 | 52.1608 | 30.2561 | 64.2037 | 51.4168 | 29.8819 | 72.3302 | 51.8081 | 29.9374
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 7.8808 | 6.445 | 4.0177 | 7.7867 | 6.3518 | 3.6434 | 7.6883 | 6.2555 | 3.5924 | 7.6012 | 6.1657 | 3.5479 | 8.683 | 6.1933 | 3.5681
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 6.9738 | 5.8977 | 3.4804 | 6.8855 | 5.8106 | 3.3074 | 6.7967 | 5.7253 | 3.2609 | 6.7144 | 5.6407 | 3.2181 | 7.1464 | 5.697 | 3.2499
CA | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.88488 | 0.91354 | 0.86626 | 0.88424 | 0.91324 | 0.90777 | 0.88401 | 0.91367 | 0.90771 | 0.88331 | 0.91327 | 0.90704 | 0.82301 | 0.91828 | 0.9108
CA | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338
CA | 6004_Glenmore - Rockhampton South 66 kV | Time | 16:00:00 | 17:00:00 | 05:30:00 | 16:00:00 | 17:00:00 | 05:30:00 | 16:00:00 | 17:00:00 | 05:30:00 | 16:00:00 | 17:00:00 | 05:30:00 | 16:00:00 | 17:00:00 | 05:30:00
CA | 6004_Glenmore - Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0361 | 1.0499 | 1.0418 | 1.0359 | 1.0496 | 1.0388 | 1.0357 | 1.0491 | 1.0386 | 1.0357 | 1.049 | 1.0386 | 1.0501 | 1.0457 | 1.0426
CA | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 30.89% | 33.11% | 25.91% | 30.86% | 33.07% | 25.84% | 30.83% | 33.04% | 25.81% | 30.66% | 32.85% | 25.67% | 31.46% | 33.7% | 26.32%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 123.2381 | 137.3934 | 95.8567 | 123.1134 | 137.2291 | 95.5924 | 123.0116 | 137.1166 | 95.5027 | 122.3369 | 136.3282 | 94.9928 | 125.511 | 139.8698 | 97.3857
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 14.8398 | 16.4438 | 11.4411 | 14.8212 | 16.4179 | 11.4872 | 14.8032 | 16.3953 | 11.4736 | 14.7213 | 16.2982 | 11.4116 | 15.0585 | 16.6666 | 11.6801
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 14.8296 | 16.4435 | 11.1033 | 14.8109 | 16.4175 | 11.4028 | 14.7925 | 16.3948 | 11.3881 | 14.7097 | 16.2975 | 11.3239 | 15.0484 | 16.6663 | 11.5856
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.99931 | 0.99998 | 0.97047 | 0.9993 | 0.99997 | 0.99265 | 0.99927 | 0.99997 | 0.99255 | 0.99921 | 0.99995 | 0.99231 | 0.99933 | 0.99998 | 0.99191
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 1.053 | 1.0465 | 1.0439 | 1.0527 | 1.0461 | 1.051 | 1.0523 | 1.0455 | 1.0507 | 1.0523 | 1.0454 | 1.0506 | 1.0492 | 1.0419 | 1.0489
CA | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 31.94% | 38.58% | 28.31% | 32.19% | 38.88% | 28.81% | 32.48% | 39.2% | 29.04% | 32.67% | 39.42% | 29.18% | 33.6% | 40.55% | 29.92%
CA | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1
CA | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 128.0629 | 161.2557 | 105.3166 | 129.0959 | 162.5224 | 107.1864 | 130.2448 | 163.8746 | 108.0161 | 131.013 | 164.7755 | 108.5585 | 134.7242 | 169.5088 | 111.3172
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 15.3391 | 19.1684 | 12.5185 | 15.4584 | 19.3104 | 12.8226 | 15.5889 | 19.4586 | 12.918 | 15.6794 | 19.5612 | 12.9818 | 16.073 | 20.0523 | 13.2884
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 15.2178 | 18.9918 | 12.4792 | 15.3349 | 19.1304 | 12.7063 | 15.4597 | 19.2714 | 12.798 | 15.5478 | 19.3706 | 12.8603 | 15.937 | 19.856 | 13.1632
CA | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.99209 | 0.99079 | 0.99686 | 0.99201 | 0.99068 | 0.99093 | 0.99171 | 0.99038 | 0.9907 | 0.99161 | 0.99025 | 0.99064 | 0.99154 | 0.99021 | 0.99058
CA | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6006_Glenmore - Frenchville 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6006_Glenmore - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0477 | 1.0398 | 1.0398 | 1.0474 | 1.0393 | 1.0464 | 1.047 | 1.0386 | 1.0461 | 1.0469 | 1.0384 | 1.046 | 1.0436 | 1.0348 | 1.0442
CA | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 43.37% | 39.3% | 28.75% | 43.43% | 39.37% | 28.77% | 43.42% | 39.36% | 28.77% | 43.41% | 39.35% | 28.76% | 44.04% | 39.91% | 29.18%
CA | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1 | TR_LINE 18952_1
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 57.2548 | 65.6372 | 45.7189 | 57.3236 | 65.7412 | 45.7426 | 57.3206 | 65.7379 | 45.7409 | 57.3066 | 65.7213 | 45.7343 | 58.1313 | 66.6576 | 46.3979
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 6.5794 | 7.503 | 5.3323 | 6.5842 | 7.5106 | 5.3333 | 6.5842 | 7.5106 | 5.3333 | 6.5841 | 7.5104 | 5.3333 | 6.6748 | 7.6125 | 5.409
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 6.5498 | 7.4546 | 5.323 | 6.545 | 7.4493 | 5.3188 | 6.545 | 7.4493 | 5.3188 | 6.5449 | 7.4492 | 5.3188 | 6.6441 | 7.5626 | 5.3992
CA | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.99549 | 0.99354 | 0.99823 | 0.99402 | 0.99182 | 0.99726 | 0.99402 | 0.99182 | 0.99726 | 0.99403 | 0.99183 | 0.99726 | 0.99539 | 0.99343 | 0.99817
CA | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6007_Biloela - Coominglah Tee 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6007_Biloela - Coominglah Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0052 | 0.99984 | 1.0202 | 1.0047 | 0.99928 | 1.0199 | 1.0047 | 0.99932 | 1.0199 | 1.005 | 0.99955 | 1.02 | 1.0043 | 0.9989 | 1.0197
CA | 6008_Biloela - Wowan 66 kV | % of Rated A | 41.85% | 35.5% | 26.04% | 41.86% | 35.5% | 26.04% | 41.85% | 35.5% | 26.04% | 41.17% | 34.92% | 25.63% | 41.86% | 35.51% | 26.05%
CA | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1
CA | 6008_Biloela - Wowan 66 kV | Loading (A) | 55.2474 | 59.2847 | 41.4114 | 55.2499 | 59.2882 | 41.4109 | 55.247 | 59.2852 | 41.4094 | 54.35 | 58.3165 | 40.7533 | 55.2602 | 59.3002 | 41.4122
CA | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 6.39 | 6.8381 | 4.8585 | 6.39 | 6.8381 | 4.8585 | 6.39 | 6.8381 | 4.8585 | 6.2907 | 6.7315 | 4.7839 | 6.3901 | 6.8382 | 4.8585
CA | 6008_Biloela - Wowan 66 kV | Loading (MW) | 6.3414 | 6.7776 | 4.842 | 6.3414 | 6.7776 | 4.842 | 6.3414 | 6.7776 | 4.842 | 6.2446 | 6.674 | 4.7686 | 6.3415 | 6.7777 | 4.842
CA | 6008_Biloela - Wowan 66 kV | Power Factor | 0.99131 | 0.99015 | 0.99539 | 0.99131 | 0.99015 | 0.99539 | 0.99131 | 0.99015 | 0.99539 | 0.99158 | 0.99043 | 0.99558 | 0.99131 | 0.99014 | 0.99538
CA | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6008_Biloela - Wowan 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
CA | 6008_Biloela - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0083 | 1.0051 | 1.0241 | 1.0083 | 1.005 | 1.0242 | 1.0083 | 1.0051 | 1.0242 | 1.0091 | 1.0059 | 1.0247 | 1.0081 | 1.0048 | 1.0241
CA | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 50.64% | 28.49% | 43.86% | 50.62% | 28.54% | 43.71% | 50.68% | 28.55% | 43.87% | 50.38% | 28.59% | 43.66% | 50.83% | 28.86% | 43.9%
CA | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 21764_1
CA | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 124.0762 | 97.4326 | 124.9868 | 124.0138 | 97.622 | 124.5777 | 124.1579 | 97.6398 | 125.0223 | 123.4226 | 97.7786 | 124.425 | 124.5233 | 98.6871 | 125.1086
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 14.8609 | 11.5742 | 15.019 | 14.8562 | 11.5953 | 14.9723 | 14.8727 | 11.597 | 15.027 | 14.7855 | 11.6139 | 14.954 | 14.9164 | 11.7146 | 15.0418
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 10.0365 | 3.6282 | 1.1121 | 10.0247 | 3.7248 | 0.86578 | 10.0454 | 3.7251 | 1.0782 | 9.9419 | 3.8881 | 0.78476 | 10.0793 | 4.138 | 0.90985
CA | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.67535 | 0.31345 | 0.074011 | 0.67477 | 0.32121 | 0.057792 | 0.67542 | 0.32119 | 0.071714 | 0.6724 | 0.33476 | 0.052444 | 0.67571 | 0.35321 | 0.060454
CA | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285
CA | 6019_Gladstone South - Friend St 66 kV | Time | 11:00:00 | 18:30:00 | 03:00:00 | 11:00:00 | 18:30:00 | 02:30:00 | 11:00:00 | 18:30:00 | 03:00:00 | 11:00:00 | 18:30:00 | 02:30:00 | 11:00:00 | 18:30:00 | 03:00:00
CA | 6019_Gladstone South - Friend St 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0477 | 1.0392 | 1.0511 | 1.0479 | 1.039 | 1.0513 | 1.0478 | 1.039 | 1.0514 | 1.0479 | 1.039 | 1.0513 | 1.0478 | 1.0384 | 1.0517
CA | 6020_Gladstone South - BORE 66 kV | % of Rated A | 70.58% | 60.92% | 53.54% | 70.94% | 61.24% | 53.79% | 70.94% | 61.24% | 53.79% | 70.94% | 61.24% | 53.79% | 72.5% | 62.65% | 54.94%
CA | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1
CA | 6020_Gladstone South - BORE 66 kV | Loading (A) | 148.9307 | 179.7122 | 131.1774 | 149.6792 | 180.6633 | 131.7885 | 149.6845 | 180.6714 | 131.7904 | 149.6801 | 180.6679 | 131.7895 | 152.9756 | 184.8218 | 134.5934
CA | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 17.6331 | 21.17 | 15.5851 | 17.7193 | 21.2783 | 15.6576 | 17.7194 | 21.2784 | 15.6576 | 17.7193 | 21.2783 | 15.6576 | 18.0981 | 21.7485 | 15.9839
CA | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 17.5719 | 21.0699 | 15.5412 | 17.6574 | 21.177 | 15.6134 | 17.6575 | 21.177 | 15.6134 | 17.6574 | 21.177 | 15.6134 | 18.0324 | 21.6407 | 15.937
CA | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.99653 | 0.99527 | 0.99719 | 0.99651 | 0.99524 | 0.99717 | 0.99651 | 0.99524 | 0.99717 | 0.99651 | 0.99524 | 0.99717 | 0.99637 | 0.99504 | 0.99706
CA | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 6020_Gladstone South - BORE 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6020_Gladstone South - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0348 | 1.0294 | 1.0386 | 1.0347 | 1.0292 | 1.0386 | 1.0347 | 1.0292 | 1.0385 | 1.0347 | 1.0292 | 1.0385 | 1.034 | 1.0283 | 1.0381
CA | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 27.71% | 30.59% | 25.92% | 27.82% | 30.73% | 26.01% | 27.82% | 30.73% | 26.01% | 27.82% | 30.73% | 26.01% | 28.37% | 31.38% | 26.49%
CA | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1
CA | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 172.6125 | 203.1252 | 155.2378 | 173.3292 | 204.0436 | 155.8134 | 173.3354 | 204.053 | 155.8156 | 173.3303 | 204.0489 | 155.8145 | 176.7299 | 208.3791 | 158.6852
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 20.2407 | 23.6602 | 18.2826 | 20.3213 | 23.7619 | 18.3498 | 20.3213 | 23.7619 | 18.3498 | 20.3213 | 23.7619 | 18.3498 | 20.7032 | 24.2389 | 18.6772
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 19.3532 | 22.5918 | 17.4904 | 19.4301 | 22.6882 | 17.5551 | 19.4301 | 22.6882 | 17.5551 | 19.4301 | 22.6882 | 17.5551 | 19.7929 | 23.1384 | 17.8673
CA | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.95615 | 0.95484 | 0.95667 | 0.95615 | 0.95482 | 0.95669 | 0.95614 | 0.95481 | 0.95669 | 0.95615 | 0.95481 | 0.95669 | 0.95604 | 0.9546 | 0.95664
CA | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599
CA | 6022_Gladstone South - Calliope 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6022_Gladstone South - Calliope 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0257 | 1.0189 | 1.0302 | 1.0255 | 1.0186 | 1.0302 | 1.0255 | 1.0186 | 1.0301 | 1.0255 | 1.0186 | 1.0302 | 1.0247 | 1.0175 | 1.0296
CA | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 45.09% | 45.95% | 46.8% | 45.1% | 46.09% | 45.59% | 45.09% | 46.1% | 45.59% | 45.05% | 46.06% | 45.59% | 45.82% | 46.99% | 46.17%
CA | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 175.418 | 220.5492 | 182.0442 | 197.9782 | 221.2424 | 177.3426 | 197.9547 | 221.2562 | 177.3452 | 197.7829 | 221.1045 | 177.3384 | 201.1618 | 225.5381 | 179.5894
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 20.9894 | 26.1345 | 21.8037 | 23.517 | 26.2141 | 21.2411 | 23.5134 | 26.2146 | 21.2405 | 23.4948 | 26.1985 | 21.241 | 23.8865 | 26.7083 | 21.3948
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 9.9562 | 22.997 | 11.7196 | 19.7902 | 23.0937 | 10.195 | 19.784 | 23.0937 | 10.1932 | 19.7489 | 23.0657 | 10.1723 | 20.2859 | 23.6982 | 16.6979
CA | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.47428 | 0.87988 | 0.53744 | 0.84146 | 0.8809 | 0.4799 | 0.84133 | 0.88088 | 0.47983 | 0.8405 | 0.88036 | 0.47883 | 0.8492 | 0.88723 | 0.7804
CA | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 389 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
CA | 6023_Friend St-Clinton Industrial 66 kV | Time | 06:00:00 | 18:00:00 | 01:00:00 | 16:30:00 | 18:00:00 | 02:00:00 | 16:30:00 | 18:00:00 | 02:00:00 | 16:30:00 | 18:00:00 | 02:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6023_Friend St-Clinton Industrial 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0467 | 1.0366 | 1.0477 | 1.0391 | 1.0365 | 1.0477 | 1.0391 | 1.0364 | 1.0477 | 1.0391 | 1.0365 | 1.0477 | 1.0387 | 1.0359 | 1.0421
CA | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 13.48% | 13.68% | 9.69% | 13.48% | 13.68% | 9.69% | 13.48% | 13.68% | 9.69% | 13.48% | 13.68% | 9.69% | 14.02% | 14.24% | 10.08%
CA | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16031_1
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 17.7928 | 22.8392 | 15.4069 | 17.796 | 22.8447 | 15.4074 | 17.7966 | 22.8457 | 15.4076 | 17.7961 | 22.8453 | 15.4075 | 18.5128 | 23.7808 | 16.0218
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 2.0619 | 2.6121 | 1.7989 | 2.0619 | 2.6121 | 1.7989 | 2.0619 | 2.6121 | 1.7989 | 2.0619 | 2.6121 | 1.7989 | 2.1415 | 2.7132 | 1.8684
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 2.0516 | 2.5975 | 1.7906 | 2.0516 | 2.5975 | 1.7906 | 2.0516 | 2.5975 | 1.7906 | 2.0516 | 2.5975 | 1.7906 | 2.1307 | 2.6976 | 1.8595
CA | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.99502 | 0.99437 | 0.99535 | 0.99502 | 0.99437 | 0.99535 | 0.99502 | 0.99437 | 0.99535 | 0.99502 | 0.99437 | 0.99535 | 0.99492 | 0.99424 | 0.99527
CA | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6029_Littlemore - Miriam Vale 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6029_Littlemore - Miriam Vale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0137 | 1.0005 | 1.0214 | 1.0135 | 1.0002 | 1.0214 | 1.0135 | 1.0002 | 1.0213 | 1.0135 | 1.0002 | 1.0213 | 1.0119 | 0.99805 | 1.0201
CA | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.355% | 4.1% | 4.384% | 5.356% | 4.1% | 4.387% | 5.355% | 4.1% | 4.387% | 5.356% | 4.1% | 4.387% | 5.355% | 4.095% | 4.383%
CA | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1
CA | 6030_Littlemore - Monto 66 kV | Loading (A) | 7.0693 | 6.8477 | 6.9699 | 7.0693 | 6.847 | 6.9748 | 7.0693 | 6.8468 | 6.9748 | 7.0694 | 6.8469 | 6.9748 | 7.0681 | 6.8388 | 6.9694
CA | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 0.85432 | 0.80162 | 0.83046 | 0.85433 | 0.80144 | 0.83164 | 0.85432 | 0.8014 | 0.83164 | 0.85434 | 0.80143 | 0.83163 | 0.85403 | 0.79953 | 0.83036
CA | 6030_Littlemore - Monto 66 kV | Loading (MW) | 0.0015622 | 0.0014659 | 0.0015186 | 0.0015623 | 0.0014656 | 0.0015208 | 0.0015623 | 0.0014655 | 0.0015208 | 0.0015623 | 0.0014655 | 0.0015208 | 0.0015617 | 0.0014621 | 0.0015184
CA | 6030_Littlemore - Monto 66 kV | Power Factor | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768
CA | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6030_Littlemore - Monto 66 kV | Time | 11:30:00 | 21:30:00 | 05:30:00 | 11:30:00 | 21:30:00 | 05:30:00 | 11:30:00 | 21:30:00 | 05:30:00 | 11:30:00 | 21:30:00 | 05:30:00 | 11:30:00 | 21:30:00 | 05:30:00
CA | 6030_Littlemore - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0572 | 1.024 | 1.0423 | 1.0572 | 1.0239 | 1.043 | 1.0572 | 1.0239 | 1.043 | 1.0572 | 1.0239 | 1.043 | 1.057 | 1.0227 | 1.0422
CA | 6031_Calliope - Littlemore 66 kV | % of Rated A | 18.51% | 17.35% | 14.12% | 18.51% | 17.36% | 14.12% | 18.51% | 17.36% | 14.12% | 18.51% | 17.36% | 14.12% | 18.93% | 17.84% | 14.4%
CA | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA | 6031_Calliope - Littlemore 66 kV | Loading (A) | 24.4267 | 28.9791 | 22.446 | 24.428 | 28.9829 | 22.4461 | 24.4283 | 28.9836 | 22.4461 | 24.4281 | 28.9833 | 22.4461 | 24.9867 | 29.7854 | 22.8885
CA | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 2.8642 | 3.3753 | 2.6434 | 2.8638 | 3.375 | 2.6433 | 2.8638 | 3.3749 | 2.6433 | 2.8638 | 3.3749 | 2.6433 | 2.9269 | 3.4644 | 2.6939
CA | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 2.4979 | 3.157 | 2.1662 | 2.4979 | 3.157 | 2.1662 | 2.4979 | 3.157 | 2.1662 | 2.4979 | 3.157 | 2.1662 | 2.5799 | 3.262 | 2.2372
CA | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.87213 | 0.93533 | 0.81946 | 0.87224 | 0.93542 | 0.81948 | 0.87226 | 0.93544 | 0.81949 | 0.87224 | 0.93543 | 0.81949 | 0.88142 | 0.94158 | 0.8305
CA | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6031_Calliope - Littlemore 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6031_Calliope - Littlemore 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0256 | 1.0187 | 1.0301 | 1.0254 | 1.0184 | 1.0301 | 1.0254 | 1.0184 | 1.0301 | 1.0254 | 1.0184 | 1.0301 | 1.0246 | 1.0173 | 1.0295
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 25.08% | 20.34% | 21.6% | 25.09% | 20.35% | 21.6% | 25.09% | 20.35% | 21.6% | 25.09% | 20.35% | 21.6% | 25.61% | 20.81% | 22.02%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 52.9098 | 59.9918 | 52.9106 | 52.9353 | 60.0319 | 52.9249 | 52.9373 | 60.0348 | 52.9254 | 52.9357 | 60.0335 | 52.9251 | 54.0294 | 61.3906 | 53.9444
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 6.1929 | 6.9704 | 6.2383 | 6.1948 | 6.9734 | 6.2396 | 6.1949 | 6.9734 | 6.2396 | 6.1948 | 6.9734 | 6.2396 | 6.3171 | 7.1223 | 6.3563
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 6.1836 | 6.9623 | 6.2145 | 6.1857 | 6.9656 | 6.2161 | 6.1858 | 6.9656 | 6.2161 | 6.1857 | 6.9656 | 6.2161 | 6.3078 | 7.1141 | 6.332
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.99849 | 0.99883 | 0.99618 | 0.99853 | 0.99888 | 0.99622 | 0.99853 | 0.99888 | 0.99622 | 0.99853 | 0.99888 | 0.99622 | 0.99851 | 0.99885 | 0.99618
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 16:30:00 | 18:30:00 | 23:30:00 | 16:30:00 | 18:30:00 | 23:30:00 | 16:30:00 | 18:30:00 | 23:30:00 | 16:30:00 | 18:30:00 | 23:30:00 | 16:30:00 | 18:30:00 | 23:30:00
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0239 | 1.0164 | 1.0314 | 1.0237 | 1.0161 | 1.0313 | 1.0237 | 1.0161 | 1.0313 | 1.0237 | 1.0161 | 1.0313 | 1.0228 | 1.0149 | 1.0307
CA | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 58.39% | 53.87% | 44.4% | 58.83% | 54.28% | 44.73% | 58.83% | 54.28% | 44.73% | 58.83% | 54.28% | 44.73% | 60.17% | 55.54% | 45.74%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 96.3423 | 120.13 | 81.7051 | 97.068 | 121.0459 | 82.3071 | 97.0713 | 121.0512 | 82.3082 | 97.0686 | 121.0489 | 82.3077 | 99.2768 | 123.8559 | 84.1551
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 11.2707 | 13.9407 | 9.608 | 11.3531 | 14.043 | 9.6782 | 11.3531 | 14.043 | 9.6782 | 11.3531 | 14.043 | 9.6782 | 11.6007 | 14.3504 | 9.8888
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 11.2018 | 13.8357 | 9.557 | 11.2833 | 13.9364 | 9.6265 | 11.2833 | 13.9364 | 9.6265 | 11.2833 | 13.9364 | 9.6265 | 11.5279 | 14.2389 | 9.835
CA | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.99389 | 0.99247 | 0.99468 | 0.99385 | 0.99241 | 0.99465 | 0.99385 | 0.99241 | 0.99465 | 0.99385 | 0.99241 | 0.99465 | 0.99372 | 0.99223 | 0.99455
CA | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184
CA | 6034_Boyne Residential Tee - BORE 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6034_Boyne Residential Tee - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0232 | 1.015 | 1.0286 | 1.023 | 1.0147 | 1.0285 | 1.023 | 1.0146 | 1.0285 | 1.023 | 1.0146 | 1.0285 | 1.022 | 1.0133 | 1.0278
CA | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 1.981% | 1.664% | 1.984% | 1.982% | 1.664% | 1.985% | 1.982% | 1.664% | 1.985% | 1.982% | 1.664% | 1.985% | 1.982% | 1.663% | 1.984%
CA | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 4.5948 | 4.5918 | 4.6022 | 4.598 | 4.5917 | 4.6047 | 4.5979 | 4.5916 | 4.6046 | 4.5981 | 4.5918 | 4.6047 | 4.598 | 4.5909 | 4.6031
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 0.54697 | 0.54625 | 0.54874 | 0.54773 | 0.54624 | 0.54933 | 0.54771 | 0.54622 | 0.54932 | 0.54775 | 0.54626 | 0.54934 | 0.54773 | 0.54603 | 0.54894
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 0.00026862 | 0.00026826 | 0.00026949 | 0.00026899 | 0.00026826 | 0.00026978 | 0.00026898 | 0.00026825 | 0.00026977 | 0.000269 | 0.00026827 | 0.00026978 | 0.00026899 | 0.00026816 | 0.00026958
CA | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527
CA | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 232 | 276 | 232 | 232 | 276 | 232 | 232 | 276 | 232 | 232 | 276 | 232 | 232 | 276 | 232
CA | 6039_Clinton Industrial - Beecher 66 kV | Time | 07:00:00 | 21:30:00 | 00:30:00 | 07:30:00 | 21:30:00 | 01:00:00 | 07:30:00 | 21:30:00 | 01:00:00 | 07:30:00 | 21:30:00 | 01:00:00 | 07:30:00 | 21:30:00 | 01:30:00
CA | 6039_Clinton Industrial - Beecher 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0413 | 1.0407 | 1.043 | 1.0421 | 1.0407 | 1.0436 | 1.042 | 1.0406 | 1.0436 | 1.0421 | 1.0407 | 1.0436 | 1.0421 | 1.0405 | 1.0432
CA | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 2.772% | 2.187% | 2.302% | 2.772% | 2.187% | 2.304% | 2.772% | 2.187% | 2.304% | 2.772% | 2.187% | 2.304% | 2.772% | 2.187% | 2.303%
CA | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 3.6591 | 3.6526 | 3.6609 | 3.6594 | 3.6526 | 3.6629 | 3.6593 | 3.6525 | 3.6628 | 3.6594 | 3.6526 | 3.6629 | 3.6585 | 3.6518 | 3.6616
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 0.43621 | 0.43464 | 0.43662 | 0.43627 | 0.43464 | 0.43709 | 0.43625 | 0.43461 | 0.43708 | 0.43628 | 0.43465 | 0.4371 | 0.43606 | 0.43447 | 0.43678
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 0.00017532 | 0.00017469 | 0.00017548 | 0.00017534 | 0.00017469 | 0.00017567 | 0.00017533 | 0.00017468 | 0.00017567 | 0.00017534 | 0.00017469 | 0.00017568 | 0.00017526 | 0.00017462 | 0.00017555
CA | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831
CA | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6041_Yarwun - Boat Creek 66 kV | Time | 12:30:00 | 21:30:00 | 00:30:00 | 12:30:00 | 21:30:00 | 01:00:00 | 12:30:00 | 21:30:00 | 01:00:00 | 12:30:00 | 21:30:00 | 01:00:00 | 12:00:00 | 21:30:00 | 01:30:00
CA | 6041_Yarwun - Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0428 | 1.0409 | 1.0433 | 1.0429 | 1.0409 | 1.0439 | 1.0429 | 1.0409 | 1.0439 | 1.0429 | 1.041 | 1.0439 | 1.0426 | 1.0407 | 1.0435
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 13.43% | 8.289% | 3.448% | 13.42% | 8.292% | 3.426% | 13.42% | 8.297% | 3.427% | 13.42% | 8.297% | 3.427% | 13.44% | 8.332% | 3.434%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 21443_1 | TR_LINE 126258_1 | TR_LINE 126258_1 | TR_LINE 21443_1 | TR_LINE 126258_1 | TR_LINE 126258_1 | TR_LINE 21443_1 | TR_LINE 126258_1 | TR_LINE 126258_1 | TR_LINE 21443_1 | TR_LINE 126258_1 | TR_LINE 126258_1 | TR_LINE 21443_1 | TR_LINE 126258_1 | TR_LINE 126258_1
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 17.9963 | 13.843 | 5.4816 | 17.9876 | 13.8478 | 5.4469 | 17.9886 | 13.8552 | 5.4485 | 17.9878 | 13.8567 | 5.4488 | 18.0144 | 13.9151 | 5.4603
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 2.0815 | 1.6173 | 0.64427 | 2.0814 | 1.6174 | 0.64373 | 2.0814 | 1.6175 | 0.64376 | 2.0814 | 1.6175 | 0.64377 | 2.0816 | 1.6184 | 0.64383
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 1.5453 | 1.2569 | 0.53774 | 1.5453 | 1.2569 | 0.53775 | 1.5453 | 1.2569 | 0.53775 | 1.5453 | 1.2569 | 0.53775 | 1.5453 | 1.2569 | 0.53774
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.74082 | 0.77713 | 0.83465 | 0.74085 | 0.7771 | 0.83536 | 0.74084 | 0.77705 | 0.83532 | 0.74085 | 0.77704 | 0.83531 | 0.74076 | 0.77663 | 0.83521
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 09:00:00 | 17:00:00 | 22:00:00 | 09:00:00 | 17:00:00 | 22:00:00 | 09:00:00 | 17:00:00 | 22:00:00 | 09:00:00 | 17:00:00 | 22:00:00 | 09:00:00 | 17:00:00 | 22:00:00
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0118 | 1.022 | 1.0281 | 1.0122 | 1.0217 | 1.0338 | 1.0122 | 1.0212 | 1.0336 | 1.0122 | 1.0211 | 1.0335 | 1.0108 | 1.0174 | 1.0315
CA | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 34.3% | 31.03% | 22.91% | 34.35% | 31.09% | 22.94% | 34.35% | 31.09% | 22.94% | 34.34% | 31.08% | 22.93% | 34.95% | 31.63% | 23.34%
CA | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 18411_1
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 45.2745 | 51.8248 | 36.4309 | 45.3424 | 51.9154 | 36.4723 | 45.34 | 51.9128 | 36.4709 | 45.329 | 51.8998 | 36.4657 | 46.1395 | 52.8291 | 37.1071
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 5.0543 | 5.7275 | 4.1547 | 5.0569 | 5.7309 | 4.1564 | 5.0569 | 5.7309 | 4.1564 | 5.0569 | 5.7309 | 4.1564 | 5.1435 | 5.8287 | 4.2279
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 5.0413 | 5.7112 | 4.1457 | 5.0363 | 5.7056 | 4.1416 | 5.0363 | 5.7056 | 4.1416 | 5.0363 | 5.7056 | 4.1416 | 5.13 | 5.8118 | 4.2186
CA | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.99736 | 0.9971 | 0.99774 | 0.99585 | 0.99552 | 0.99632 | 0.99585 | 0.99552 | 0.99632 | 0.99585 | 0.99552 | 0.99632 | 0.99732 | 0.99705 | 0.99771
CA | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6045_Coominglah Tee - Monto 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97632 | 0.96647 | 0.99746 | 0.97538 | 0.96536 | 0.99675 | 0.97543 | 0.96541 | 0.99679 | 0.97566 | 0.96565 | 0.99693 | 0.97491 | 0.96484 | 0.99653
CA | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 81.42% | 54.3% | 42.45% | 81.41% | 54.32% | 42.46% | 81.42% | 54.35% | 42.47% | 81.41% | 54.36% | 42.47% | 81.03% | 54.55% | 42.52%
CA | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 107.4727 | 90.6741 | 67.5017 | 107.4649 | 90.7093 | 67.5091 | 107.4689 | 90.7653 | 67.5221 | 107.4634 | 90.7762 | 67.5229 | 106.955 | 91.0998 | 67.6144
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 12.2117 | 10.4363 | 7.8492 | 12.2117 | 10.4364 | 7.8492 | 12.2117 | 10.4364 | 7.8492 | 12.2117 | 10.4364 | 7.8492 | 12.2115 | 10.4365 | 7.8492
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 10.1142 | 8.6449 | 6.5033 | 10.1142 | 8.6449 | 6.5033 | 10.1142 | 8.6449 | 6.5033 | 10.1142 | 8.6449 | 6.5033 | 10.1141 | 8.6449 | 6.5034
CA | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.82823 | 0.82833 | 0.82851 | 0.82823 | 0.82832 | 0.82851 | 0.82823 | 0.82832 | 0.82851 | 0.82823 | 0.82832 | 0.82851 | 0.82823 | 0.82832 | 0.82851
CA | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6046_Mt Morgan - Wowan 66 kV | Time | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00
CA | 6046_Mt Morgan - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99392 | 1.0068 | 1.0172 | 0.99399 | 1.0064 | 1.0171 | 0.99395 | 1.0058 | 1.0169 | 0.994 | 1.0057 | 1.0169 | 0.99871 | 1.0021 | 1.0155
CA | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 8.637% | 7.382% | 5.213% | 8.642% | 7.387% | 5.215% | 8.641% | 7.386% | 5.214% | 8.639% | 7.384% | 5.214% | 8.645% | 7.389% | 5.213%
CA | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 13.3016 | 15.2811 | 10.3734 | 13.3081 | 15.2901 | 10.3769 | 13.3074 | 15.2894 | 10.3765 | 13.3043 | 15.2857 | 10.375 | 13.3128 | 15.2962 | 10.3733
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 1.5284 | 1.7465 | 1.2098 | 1.5284 | 1.7466 | 1.2098 | 1.5284 | 1.7466 | 1.2098 | 1.5284 | 1.7466 | 1.2098 | 1.5284 | 1.7466 | 1.2092
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 1.3646 | 1.5548 | 1.084 | 1.3646 | 1.5548 | 1.084 | 1.3646 | 1.5548 | 1.084 | 1.3646 | 1.5548 | 1.084 | 1.3646 | 1.5549 | 1.0839
CA | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.89284 | 0.89023 | 0.89604 | 0.89283 | 0.8902 | 0.89603 | 0.89283 | 0.89021 | 0.89603 | 0.89284 | 0.89022 | 0.89603 | 0.89282 | 0.89019 | 0.89636
CA | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199
CA | 6047_Coominglah Sub Tee 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6047_Coominglah Sub Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0051 | 0.99981 | 1.0202 | 1.0047 | 0.99926 | 1.0199 | 1.0047 | 0.9993 | 1.0199 | 1.0049 | 0.99953 | 1.02 | 1.0043 | 0.99888 | 1.0197
CA | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 6.189% | 6.48% | 3.247% | 6.125% | 6.428% | 3.837% | 5.885% | 6.221% | 3.756% | 5.962% | 6.068% | 3.691% | 6.004% | 6.148% | 3.75%
CA | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 22210_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 13284_1
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 24.8186 | 27.0866 | 12.0775 | 24.562 | 26.8678 | 14.2724 | 23.5986 | 26.0024 | 13.9714 | 23.9073 | 25.3652 | 13.7298 | 24.0753 | 25.6998 | 13.9502
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 2.9318 | 3.2205 | 1.4358 | 2.9008 | 3.193 | 1.7069 | 2.7861 | 3.0879 | 1.6703 | 2.837 | 3.0115 | 1.6412 | 2.8539 | 3.0404 | 1.6646
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 2.9287 | 2.9859 | 1.3479 | 2.8983 | 2.9481 | 1.1839 | 2.7853 | 2.8069 | 1.0923 | 2.7073 | 2.7077 | 1.0299 | 2.7265 | 2.7245 | 1.0435
CA | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.99895 | 0.92715 | 0.93877 | 0.99913 | 0.92329 | 0.6936 | 0.99971 | 0.909 | 0.65393 | 0.95427 | 0.89912 | 0.6275 | 0.95535 | 0.89609 | 0.62688
CA | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6050_Parkhurst - Frenchville 66 kV | Time | 16:00:00 | 18:00:00 | 22:00:00 | 16:00:00 | 18:00:00 | 22:00:00 | 16:00:00 | 18:00:00 | 22:00:00 | 09:30:00 | 18:00:00 | 22:00:00 | 09:30:00 | 18:00:00 | 22:00:00
CA | 6050_Parkhurst - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0334 | 1.0401 | 1.0399 | 1.0331 | 1.0396 | 1.0462 | 1.0328 | 1.0388 | 1.0458 | 1.0381 | 1.0386 | 1.0457 | 1.037 | 1.0349 | 1.0438
CA | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 96.95% | 85.31% | 63.91% | 98.09% | 86.38% | 64.15% | 99.42% | 87.65% | 64.99% | 100.5% | 88.7% | 65.7% | 104.6% | 92.41% | 68.17%
CA | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 205.5417 | 252.5151 | 157.2217 | 207.9454 | 255.694 | 157.8193 | 210.7752 | 259.4468 | 159.8831 | 213.1169 | 262.5624 | 161.6332 | 221.6775 | 273.5227 | 167.6978
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 23.4978 | 28.2267 | 18.0737 | 23.7474 | 28.5384 | 18.2535 | 24.0369 | 28.9003 | 18.4746 | 24.2832 | 29.2092 | 18.6649 | 25.1078 | 30.2107 | 19.2948
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 23.4535 | 28.0877 | 18.0702 | 23.6991 | 28.3905 | 18.2504 | 23.9837 | 28.7417 | 18.4704 | 24.2257 | 29.0412 | 18.6597 | 25.0327 | 30.0179 | 19.2847
CA | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.99812 | 0.99508 | 0.99981 | 0.99796 | 0.99481 | 0.99983 | 0.99779 | 0.99451 | 0.99977 | 0.99763 | 0.99425 | 0.99972 | 0.99701 | 0.99362 | 0.99948
CA | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 6051_Parkhurst - Keppel 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6051_Parkhurst - Keppel 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9959 | 0.97249 | 1.0026 | 0.99478 | 0.97091 | 1.0087 | 0.99331 | 0.96889 | 1.0077 | 0.9924 | 0.96754 | 1.007 | 0.98623 | 0.96029 | 1.0032
CA | 6052_Pandoin - Kunwarara 66 kV | % of Rated A | 19.11% | 17.91% | 18.79% | 19.11% | 17.91% | 18.77% | 19.12% | 17.92% | 18.78% | 19.12% | 17.93% | 18.78% | 19.15% | 17.99% | 18.76%
CA | 6052_Pandoin - Kunwarara 66 kV | Limiting Line Name | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (A) | 61.5457 | 64.6429 | 60.4917 | 61.5452 | 64.6712 | 60.4378 | 61.5544 | 64.706 | 60.4562 | 61.5543 | 64.7219 | 60.4619 | 61.655 | 64.9483 | 60.3983
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MVA) | 7.0006 | 7.41 | 6.9113 | 7.0006 | 7.4103 | 6.9098 | 7.0007 | 7.4106 | 6.91 | 7.0007 | 7.4108 | 6.91 | 7.0018 | 7.413 | 6.9095
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MW) | 5.3188 | 5.7556 | 5.3748 | 5.3188 | 5.7556 | 5.383 | 5.3188 | 5.7557 | 5.383 | 5.3188 | 5.7558 | 5.383 | 5.3191 | 5.7563 | 5.3829
CA | 6052_Pandoin - Kunwarara 66 kV | Power Factor | 0.75266 | 0.76931 | 0.77072 | 0.75266 | 0.76929 | 0.77208 | 0.75265 | 0.76926 | 0.77207 | 0.75265 | 0.76924 | 0.77206 | 0.75254 | 0.76903 | 0.77212
CA | 6052_Pandoin - Kunwarara 66 kV | Rating (A) | 322 | 361 | 322 | 322 | 361 | 322 | 322 | 361 | 322 | 322 | 361 | 322 | 322 | 361 | 322
CA | 6052_Pandoin - Kunwarara 66 kV | Time | 08:30:00 | 19:00:00 | 22:00:00 | 08:30:00 | 19:00:00 | 22:30:00 | 08:30:00 | 19:00:00 | 22:30:00 | 08:30:00 | 19:00:00 | 22:30:00 | 08:30:00 | 19:00:00 | 22:30:00
CA | 6052_Pandoin - Kunwarara 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99502 | 1.0027 | 0.99945 | 0.99503 | 1.0023 | 1.0001 | 0.99489 | 1.0019 | 0.99984 | 0.9949 | 1.0016 | 0.99976 | 0.99343 | 0.99844 | 1.0007
CA | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 50.07% | 47.18% | 32.7% | 50.29% | 47.45% | 32.59% | 50.51% | 47.72% | 32.72% | 50.58% | 47.85% | 32.78% | 52.24% | 49.57% | 33.74%
CA | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 261.8754 | 279.3018 | 178.5598 | 263.0311 | 280.9015 | 177.9656 | 264.1697 | 282.4976 | 178.6389 | 264.5454 | 283.2564 | 178.9698 | 273.2328 | 293.4545 | 184.216
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 31.4905 | 33.3624 | 21.2709 | 31.6215 | 33.5406 | 21.2967 | 31.7446 | 33.7112 | 21.3712 | 31.7866 | 33.7945 | 21.4089 | 32.7447 | 34.9066 | 22.0046
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 31.4486 | 33.36 | 21.1652 | 31.5834 | 33.5394 | 20.75 | 31.7125 | 33.711 | 20.8457 | 31.7566 | 33.7945 | 20.8925 | 32.7383 | 34.8986 | 21.59
CA | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.99792 | 0.99966 | 0.99434 | 0.99807 | 0.99974 | 0.97277 | 0.99831 | 0.99984 | 0.97387 | 0.9984 | 0.99988 | 0.97435 | 0.99944 | 0.99977 | 0.97971
CA | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546
CA | 6053_Parkhurst - Pandoin 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6053_Parkhurst - Pandoin 66 kV | Min Voltage at Constrained Conductor (pu) | 1.048 | 1.0401 | 1.0399 | 1.0477 | 1.0396 | 1.0462 | 1.0472 | 1.0388 | 1.0458 | 1.047 | 1.0386 | 1.0457 | 1.0437 | 1.0349 | 1.0438
CA | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 46.92% | 33.36% | 33.83% | 46.93% | 33.37% | 33.83% | 46.93% | 33.37% | 33.83% | 46.93% | 33.37% | 33.83% | 46.97% | 33.41% | 33.86%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 79.2925 | 80.0593 | 79.1683 | 79.3083 | 80.0802 | 79.1711 | 79.3114 | 80.0841 | 79.1723 | 79.3089 | 80.0824 | 79.1717 | 79.3833 | 80.187 | 79.2245
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 9.1593 | 9.188 | 9.1842 | 9.1596 | 9.1884 | 9.1843 | 9.1596 | 9.1885 | 9.1843 | 9.1596 | 9.1884 | 9.1843 | 9.1609 | 9.1903 | 9.1852
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 8.0557 | 8.0775 | 8.0803 | 8.0558 | 8.0776 | 8.0804 | 8.0558 | 8.0776 | 8.0804 | 8.0558 | 8.0776 | 8.0804 | 8.0561 | 8.0781 | 8.0806
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.87177 | 0.87166 | 0.87197 | 0.87176 | 0.87164 | 0.87197 | 0.87175 | 0.87164 | 0.87197 | 0.87176 | 0.87164 | 0.87197 | 0.87169 | 0.87154 | 0.87192
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0064 | 0.99941 | 1.0109 | 1.0063 | 0.99917 | 1.0109 | 1.0062 | 0.99913 | 1.0109 | 1.0063 | 0.99915 | 1.0109 | 1.0054 | 0.99797 | 1.0103
CA | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 42.4% | 51.82% | 35.81% | 43.01% | 52.6% | 36.08% | 43.75% | 53.53% | 36.67% | 44.36% | 54.31% | 37.18% | 46.22% | 56.64% | 38.64%
CA | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 169.1563 | 215.0541 | 132.496 | 171.6026 | 218.2853 | 133.4948 | 174.545 | 222.1358 | 135.695 | 177.0005 | 225.3728 | 137.5559 | 184.435 | 235.0638 | 142.9639
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 20.0895 | 25.3688 | 15.6548 | 20.3727 | 25.7356 | 15.8708 | 20.7116 | 26.1705 | 16.1272 | 20.9997 | 26.5429 | 16.346 | 21.8002 | 27.5703 | 16.9523
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 19.5909 | 24.4947 | 15.3878 | 19.8553 | 24.8292 | 15.5959 | 20.1714 | 25.225 | 15.8394 | 20.4401 | 25.5639 | 16.0471 | 21.1883 | 26.5145 | 16.6233
CA | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.97518 | 0.96555 | 0.98295 | 0.9746 | 0.96478 | 0.98268 | 0.97392 | 0.96387 | 0.98216 | 0.97336 | 0.96312 | 0.98171 | 0.97193 | 0.96171 | 0.98059
CA | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 6074_Lakes Creek - Tanby 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
CA | 6074_Lakes Creek - Tanby 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0122 | 0.99544 | 1.0144 | 1.0113 | 0.99416 | 1.0207 | 1.0102 | 0.99256 | 1.0199 | 1.0095 | 0.9915 | 1.0194 | 1.0041 | 0.9852 | 1.016
CA | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.3457% | 0.2746% | 0.3445% | 0.3456% | 0.2744% | 0.3443% | 0.3454% | 0.2741% | 0.3435% | 0.3454% | 0.2739% | 0.3441% | 0.3445% | 0.2726% | 0.3445%
CA | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.1649 | 1.1398 | 1.1611 | 1.1646 | 1.1387 | 1.1603 | 1.1641 | 1.1374 | 1.1576 | 1.1639 | 1.1365 | 1.1595 | 1.161 | 1.1314 | 1.1611
CA | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.13611 | 0.13031 | 0.13522 | 0.13605 | 0.13007 | 0.13506 | 0.13594 | 0.12977 | 0.13443 | 0.13588 | 0.12956 | 0.13486 | 0.13521 | 0.12839 | 0.13524
CA | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.3917e-06 | 3.2472e-06 | 3.3696e-06 | 3.3903e-06 | 3.2412e-06 | 3.3655e-06 | 3.3875e-06 | 3.2337e-06 | 3.3497e-06 | 3.3859e-06 | 3.2286e-06 | 3.3606e-06 | 3.3693e-06 | 3.1994e-06 | 3.3701e-06
CA | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.1894e-06 | 2.1944e-06 | 2.1908e-06 | 2.1929e-06 | 2.1923e-06 | 2.1918e-06 | 2.1919e-06 | 2.1932e-06 | 2.1909e-06 | 2.1869e-06 | 2.1922e-06 | 2.1933e-06 | 2.1909e-06 | 2.1929e-06 | 2.193e-06
CA | 6075_Keppel - Farnborough 66 kV | Rating (A) | 337 | 415 | 337 | 337 | 415 | 337 | 337 | 415 | 337 | 337 | 415 | 337 | 337 | 415 | 337
CA | 6075_Keppel - Farnborough 66 kV | Time | 08:30:00 | 21:30:00 | 01:00:00 | 08:30:00 | 21:30:00 | 03:00:00 | 08:30:00 | 21:30:00 | 01:30:00 | 08:30:00 | 21:30:00 | 03:00:00 | 08:30:00 | 21:30:00 | 04:00:00
CA | 6075_Keppel - Farnborough 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0222 | 1.0001 | 1.0188 | 1.0219 | 0.99922 | 1.0182 | 1.0215 | 0.99805 | 1.0158 | 1.0213 | 0.99727 | 1.0174 | 1.0188 | 0.99275 | 1.0189
CA | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 97% | 85.36% | 63.92% | 98.13% | 86.43% | 64.17% | 99.47% | 87.7% | 65.01% | 100.6% | 88.76% | 65.72% | 104.6% | 92.46% | 68.19%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 205.6341 | 252.6584 | 157.2549 | 208.0412 | 255.8408 | 157.8508 | 210.8748 | 259.5973 | 159.9186 | 213.2196 | 262.7162 | 161.6724 | 221.792 | 273.6829 | 167.7495
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 23.2745 | 27.8734 | 17.9473 | 23.5183 | 28.175 | 18.1261 | 23.8008 | 28.5247 | 18.3438 | 24.0412 | 28.8233 | 18.5312 | 24.8435 | 29.7882 | 19.1504
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 23.2367 | 27.7605 | 17.9434 | 23.4772 | 28.0549 | 18.1226 | 23.7558 | 28.3962 | 18.3392 | 23.9926 | 28.6874 | 18.5256 | 24.7805 | 29.6339 | 19.1404
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.99838 | 0.99595 | 0.99978 | 0.99825 | 0.99574 | 0.9998 | 0.99811 | 0.9955 | 0.99975 | 0.99798 | 0.99528 | 0.9997 | 0.99746 | 0.99482 | 0.99948
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98995 | 0.96485 | 0.99825 | 0.98874 | 0.96316 | 1.0044 | 0.98717 | 0.961 | 1.0033 | 0.98617 | 0.95953 | 1.0026 | 0.97968 | 0.9519 | 0.99852
CA | 6087_Glenmore - QMAG Tee 66 kV | % of Rated A | 26.16% | 23.75% | 18.66% | 26.32% | 24.01% | 19.62% | 26.62% | 24.44% | 19.92% | 26.81% | 24.72% | 20.11% | 25.47% | 25.45% | 20.59%
CA | 6087_Glenmore - QMAG Tee 66 kV | Limiting Line Name | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (A) | 104.9008 | 99.2802 | 69.3972 | 105.5366 | 100.3534 | 72.9697 | 106.7383 | 102.1403 | 74.0961 | 107.496 | 103.3348 | 74.8264 | 102.1539 | 106.3672 | 76.6064
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MVA) | 12.384 | 11.8446 | 8.2565 | 12.4576 | 11.9675 | 8.7339 | 12.5963 | 12.1728 | 8.8661 | 12.686 | 12.3123 | 8.9527 | 12.0713 | 12.6311 | 9.1503
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MW) | 11.5477 | 11.473 | 8.1488 | 11.6207 | 11.5907 | 8.4196 | 11.7504 | 11.7811 | 8.5442 | 11.839 | 11.9146 | 8.6289 | 11.6484 | 12.2252 | 8.8214
CA | 6087_Glenmore - QMAG Tee 66 kV | Power Factor | 0.93231 | 0.96849 | 0.98665 | 0.93267 | 0.96838 | 0.96355 | 0.9327 | 0.96771 | 0.96323 | 0.9331 | 0.9676 | 0.96338 | 0.96485 | 0.9678 | 0.96364
CA | 6087_Glenmore - QMAG Tee 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6087_Glenmore - QMAG Tee 66 kV | Time | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00
CA | 6087_Glenmore - QMAG Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0316 | 1.0426 | 1.0403 | 1.0314 | 1.0421 | 1.0467 | 1.0311 | 1.0414 | 1.0463 | 1.0311 | 1.0412 | 1.0462 | 1.0326 | 1.0376 | 1.0444
CA | 6088_QMAG Tee - Parkhurst 66 kV | % of Rated A | 25.39% | 17.67% | 10.95% | 25.3% | 17.96% | 11.51% | 25.11% | 18.44% | 11.85% | 25% | 18.76% | 12.07% | 24.29% | 19.57% | 12.6%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Limiting Line Name | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (A) | 88.0933 | 63.7983 | 35.2457 | 87.7879 | 64.8441 | 37.0708 | 87.1326 | 66.5667 | 38.1532 | 86.7388 | 67.7404 | 38.8761 | 84.2789 | 70.6432 | 40.5823
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MVA) | 10.4176 | 7.5996 | 4.1909 | 10.3819 | 7.7206 | 4.4334 | 10.3033 | 7.9202 | 4.5613 | 10.257 | 8.0578 | 4.6472 | 9.9761 | 8.3742 | 4.8427
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MW) | 8.5636 | 7.5296 | 4.1466 | 8.5248 | 7.6469 | 4.4166 | 8.448 | 7.8368 | 4.5409 | 8.3979 | 7.9699 | 4.6255 | 8.1163 | 8.2795 | 4.8176
CA | 6088_QMAG Tee - Parkhurst 66 kV | Power Factor | 0.82159 | 0.9906 | 0.98942 | 0.82068 | 0.99027 | 0.99593 | 0.81948 | 0.98928 | 0.99524 | 0.81829 | 0.98891 | 0.99503 | 0.81308 | 0.98853 | 0.99452
CA | 6088_QMAG Tee - Parkhurst 66 kV | Rating (A) | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322
CA | 6088_QMAG Tee - Parkhurst 66 kV | Time | 10:30:00 | 18:30:00 | 22:00:00 | 10:30:00 | 18:30:00 | 22:00:00 | 10:30:00 | 18:30:00 | 22:00:00 | 10:30:00 | 18:30:00 | 22:00:00 | 10:00:00 | 18:30:00 | 22:00:00
CA | 6088_QMAG Tee - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0342 | 1.0417 | 1.0399 | 1.0342 | 1.0412 | 1.0462 | 1.0341 | 1.0405 | 1.0458 | 1.0341 | 1.0402 | 1.0457 | 1.0352 | 1.0366 | 1.0438
CA | 6089_QMAG Tee - QMAG 66 kV | % of Rated A | 39.97% | 23.75% | 18.66% | 39.98% | 24.01% | 19.62% | 39.99% | 24.44% | 19.92% | 39.99% | 24.72% | 20.11% | 39.93% | 25.45% | 20.59%
CA | 6089_QMAG Tee - QMAG 66 kV | Limiting Line Name | TR_LINE 22236_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 22236_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 22236_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 22236_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 22236_1 | TR_LINE 20870_1 | TR_LINE 20870_1
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (A) | 160.2893 | 99.2806 | 69.3974 | 160.3112 | 100.3538 | 72.9701 | 160.3555 | 102.1407 | 74.0965 | 160.3548 | 103.3351 | 74.8267 | 160.1315 | 106.3675 | 76.6068
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MVA) | 18.9014 | 11.8326 | 8.2526 | 18.9014 | 11.9552 | 8.7308 | 18.9014 | 12.1598 | 8.8627 | 18.9014 | 12.2989 | 8.9491 | 18.9014 | 12.6164 | 9.1461
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MW) | 16.6897 | 11.4598 | 8.1424 | 16.6897 | 11.5772 | 8.4125 | 16.6897 | 11.7671 | 8.5368 | 16.6897 | 11.9003 | 8.6214 | 16.6897 | 12.2101 | 8.8136
CA | 6089_QMAG Tee - QMAG 66 kV | Power Factor | 0.88299 | 0.96849 | 0.98665 | 0.88299 | 0.96838 | 0.96354 | 0.88299 | 0.96771 | 0.96323 | 0.88299 | 0.96759 | 0.96338 | 0.88299 | 0.9678 | 0.96364
CA | 6089_QMAG Tee - QMAG 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6089_QMAG Tee - QMAG 66 kV | Time | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00 | 15:00:00 | 18:30:00 | 22:00:00
CA | 6089_QMAG Tee - QMAG 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0315 | 1.0426 | 1.0403 | 1.0313 | 1.0421 | 1.0467 | 1.031 | 1.0414 | 1.0463 | 1.031 | 1.0411 | 1.0462 | 1.0325 | 1.0376 | 1.0444
CA | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 32.59% | 26.11% | 20.31% | 32.6% | 26.12% | 20.2% | 32.62% | 26.13% | 20.2% | 32.62% | 26.13% | 20.2% | 33.29% | 26.7% | 20.67%
CA | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 22121_1
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 43.0242 | 43.604 | 32.2918 | 43.035 | 43.6176 | 32.1106 | 43.0523 | 43.6387 | 32.1185 | 43.0543 | 43.643 | 32.1202 | 43.9493 | 44.5892 | 32.86
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 5.064 | 5.1154 | 3.801 | 5.0641 | 5.1155 | 3.8005 | 5.0642 | 5.1156 | 3.8005 | 5.0642 | 5.1156 | 3.8005 | 5.1519 | 5.2078 | 3.8803
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 4.9244 | 4.9914 | 3.78 | 4.9244 | 4.9914 | 3.7799 | 4.9244 | 4.9914 | 3.7799 | 4.9244 | 4.9914 | 3.7799 | 5.0119 | 5.0827 | 3.8591
CA | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.97238 | 0.97571 | 0.99444 | 0.97237 | 0.97569 | 0.99456 | 0.97235 | 0.97567 | 0.99456 | 0.97235 | 0.97567 | 0.99455 | 0.97278 | 0.97594 | 0.99452
CA | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6090_Egan's Hill - Raglan 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
CA | 6090_Egan's Hill - Raglan 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0296 | 1.0262 | 1.0297 | 1.0294 | 1.0259 | 1.0353 | 1.029 | 1.0255 | 1.0351 | 1.0289 | 1.0254 | 1.035 | 1.0254 | 1.0217 | 1.033
CA | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 72.67% | 45.14% | 34.4% | 72.67% | 45.16% | 34.4% | 72.67% | 45.19% | 34.41% | 72.67% | 45.19% | 34.41% | 72.3% | 45.37% | 34.46%
CA | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 103.9233 | 87.1157 | 63.9826 | 103.9153 | 87.1522 | 63.9903 | 103.9194 | 87.2101 | 64.0038 | 103.9137 | 87.2214 | 64.0046 | 103.3903 | 87.556 | 64.1001
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 12.2427 | 10.3273 | 7.5955 | 12.2425 | 10.3279 | 7.5956 | 12.2426 | 10.3288 | 7.5958 | 12.2425 | 10.329 | 7.5959 | 12.234 | 10.3344 | 7.5974
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 10.4496 | 8.8813 | 6.6318 | 10.4495 | 8.8815 | 6.6318 | 10.4496 | 8.8818 | 6.6319 | 10.4495 | 8.8818 | 6.6319 | 10.4461 | 8.8837 | 6.6322
CA | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.8529 | 0.85908 | 0.87173 | 0.8529 | 0.85905 | 0.87172 | 0.8529 | 0.859 | 0.8717 | 0.8529 | 0.85899 | 0.8717 | 0.8532 | 0.85874 | 0.87157
CA | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186
CA | 6091_Egan's Hill - Gavial 66 kV | Time | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00
CA | 6091_Egan's Hill - Gavial 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0282 | 1.0355 | 1.0382 | 1.0283 | 1.0351 | 1.0381 | 1.0282 | 1.0345 | 1.038 | 1.0283 | 1.0344 | 1.0379 | 1.0328 | 1.031 | 1.0366
CA | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 79.47% | 52.75% | 40.83% | 79.46% | 52.77% | 40.84% | 79.47% | 52.8% | 40.85% | 79.46% | 52.81% | 40.85% | 79.07% | 53.01% | 40.91%
CA | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 104.8994 | 88.0853 | 64.9235 | 104.8915 | 88.1215 | 64.9311 | 104.8956 | 88.1789 | 64.9445 | 104.8899 | 88.1901 | 64.9453 | 104.3702 | 88.5221 | 65.0399
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 12.138 | 10.2707 | 7.5893 | 12.1379 | 10.2712 | 7.5894 | 12.138 | 10.2719 | 7.5896 | 12.1379 | 10.272 | 7.5896 | 12.1315 | 10.2762 | 7.5909
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 10.3315 | 8.7982 | 6.5869 | 10.3314 | 8.7984 | 6.587 | 10.3315 | 8.7986 | 6.587 | 10.3314 | 8.7986 | 6.587 | 10.3292 | 8.7998 | 6.5873
CA | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.84822 | 0.85241 | 0.86124 | 0.84822 | 0.85239 | 0.86124 | 0.84822 | 0.85236 | 0.86122 | 0.84822 | 0.85235 | 0.86122 | 0.84842 | 0.85218 | 0.86113
CA | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6093_Gavial - Mt Morgan 66 kV | Time | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00 | 10:30:00 | 18:00:00 | 23:30:00
CA | 6093_Gavial - Mt Morgan 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99791 | 1.0102 | 1.0197 | 0.99798 | 1.0098 | 1.0196 | 0.99795 | 1.0092 | 1.0194 | 0.998 | 1.009 | 1.0194 | 1.0027 | 1.0055 | 1.018
CA | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 50.44% | 42.74% | 28.63% | 50.45% | 42.75% | 28.48% | 50.9% | 43.14% | 28.72% | 50.48% | 42.78% | 28.48% | 51.91% | 44.01% | 29.25%
CA | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 85.2476 | 102.5687 | 67 | 85.2676 | 102.6073 | 66.6342 | 86.0245 | 103.5408 | 67.2135 | 85.3033 | 102.6805 | 66.6535 | 87.7351 | 105.6341 | 68.4535
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 10.1954 | 12.163 | 7.9527 | 10.1955 | 12.1632 | 7.9516 | 10.2819 | 12.2669 | 8.0188 | 10.1956 | 12.1635 | 7.9517 | 10.4557 | 12.4724 | 8.1534
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 10.1164 | 12.0491 | 7.9036 | 10.1165 | 12.0492 | 7.903 | 10.2016 | 12.1508 | 7.9693 | 10.1165 | 12.0493 | 7.903 | 10.3722 | 12.3536 | 8.1021
CA | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.99159 | 0.99043 | 0.99265 | 0.99159 | 0.99043 | 0.99269 | 0.99154 | 0.99036 | 0.99266 | 0.99159 | 0.99042 | 0.99269 | 0.99142 | 0.99036 | 0.99258
CA | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 6094_Malchi Tee - Malchi 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6094_Malchi Tee - Malchi 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0411 | 1.0306 | 1.035 | 1.0409 | 1.0302 | 1.0406 | 1.0404 | 1.0295 | 1.0403 | 1.0404 | 1.0295 | 1.0403 | 1.0372 | 1.0258 | 1.0385
CA | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 27.64% | 19.82% | 16.03% | 27.6% | 19.85% | 12.41% | 27.59% | 19.9% | 12.44% | 27.5% | 19.92% | 12.46% | 27.08% | 20.47% | 15.98%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 68.5473 | 49.5517 | 35.2637 | 68.4372 | 49.6374 | 27.3125 | 68.4145 | 49.7443 | 27.3761 | 68.2015 | 49.7941 | 27.4072 | 67.155 | 51.1813 | 35.1482
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 8.1457 | 5.9347 | 4.2102 | 8.1319 | 5.943 | 3.2813 | 8.1278 | 5.9528 | 3.2881 | 8.1029 | 5.9581 | 3.2917 | 7.981 | 6.1042 | 4.2024
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 7.7861 | 5.619 | 3.4554 | 7.7739 | 5.6271 | 3.1193 | 7.7688 | 5.6326 | 3.124 | 7.7463 | 5.6387 | 3.1285 | 7.7203 | 5.7473 | 3.451
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.95537 | 0.94588 | 0.82001 | 0.9555 | 0.94592 | 0.95008 | 0.95535 | 0.94529 | 0.94955 | 0.9555 | 0.94548 | 0.94986 | 0.96691 | 0.94061 | 0.82048
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:30:00
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0385 | 1.0476 | 1.0444 | 1.0384 | 1.0473 | 1.0509 | 1.0383 | 1.0467 | 1.0507 | 1.0383 | 1.0466 | 1.0506 | 1.0386 | 1.0432 | 1.0459
CA | 6096_Egan's Hill - Lakes Creek 66 kV | % of Rated A | 48.59% | 50.83% | 38.56% | 48.91% | 51.22% | 38.34% | 49.2% | 51.58% | 38.54% | 49.48% | 51.92% | 38.77% | 51.03% | 53.66% | 39.85%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Limiting Line Name | TR_LINE 19724_1 | 6096_Egan's Hill | TR_LINE 19717_1 | TR_LINE 19734_1 | 6096_Egan's Hill | TR_LINE 19717_1 | 6096_Egan's Hill | 6096_Egan's Hill | TR_LINE 19717_1 | 6096_Egan's Hill | 6096_Egan's Hill | TR_LINE 19717_1 | 6096_Egan's Hill | 6096_Egan's Hill | TR_LINE 19717_1
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (A) | 155.9698 | 173.3267 | 118.3647 | 157.0129 | 174.6546 | 117.6954 | 157.9339 | 175.8742 | 118.3269 | 158.8183 | 177.0513 | 119.0235 | 163.798 | 182.9833 | 122.3394
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MVA) | 18.7117 | 20.4944 | 14.1134 | 18.8262 | 20.6405 | 14.1137 | 18.7984 | 20.7699 | 14.1855 | 18.9005 | 20.9027 | 14.2677 | 19.4193 | 21.5108 | 14.6386
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MW) | 18.7117 | 20.4797 | 14.1092 | 18.826 | 20.6232 | 14.0747 | 18.7984 | 20.7492 | 14.1496 | 18.9003 | 20.8792 | 14.2343 | 19.4123 | 21.4611 | 14.6227
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Power Factor | 1 | 0.99928 | 0.9997 | 0.99999 | 0.99916 | 0.99722 | 1 | 0.999 | 0.99745 | 0.99999 | 0.99888 | 0.99764 | 0.99964 | 0.99769 | 0.9989
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Rating (A) | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0492 | 1.0343 | 1.0424 | 1.0435 | 1.0337 | 1.0484 | 1.0412 | 1.033 | 1.0481 | 1.041 | 1.0327 | 1.048 | 1.037 | 1.0283 | 1.046
CA | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 34.72% | 33.55% | 25.52% | 34.76% | 33.65% | 23.94% | 34.82% | 33.74% | 24% | 34.74% | 33.73% | 23.98% | 34.9% | 34.67% | 24.66%
CA | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 20992_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 20992_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 20992_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1
CA | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 86.115 | 83.8845 | 56.1503 | 86.2013 | 84.1217 | 52.6594 | 86.3578 | 84.3602 | 52.7908 | 86.1553 | 84.3284 | 52.758 | 86.5594 | 86.6802 | 54.2539
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 10.2416 | 10.052 | 6.7054 | 10.2509 | 10.077 | 6.3315 | 10.2676 | 10.1003 | 6.3458 | 10.2441 | 10.0954 | 6.3416 | 10.2947 | 10.3427 | 6.4883
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 10.2139 | 10.0313 | 6.6238 | 10.2232 | 10.0558 | 6.3255 | 10.2392 | 10.0778 | 6.3403 | 10.2162 | 10.0729 | 6.336 | 10.2861 | 10.3093 | 6.4077
CA | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.99724 | 0.99789 | 0.98742 | 0.99725 | 0.99785 | 0.99905 | 0.99718 | 0.99772 | 0.99912 | 0.99723 | 0.99772 | 0.99912 | 0.99914 | 0.99672 | 0.98712
CA | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 6097_Egan's Hill - Canning 66 kV | Time | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:30:00
CA | 6097_Egan's Hill - Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0383 | 1.0462 | 1.0437 | 1.0382 | 1.0459 | 1.0514 | 1.038 | 1.0453 | 1.0511 | 1.038 | 1.0452 | 1.0511 | 1.0383 | 1.0417 | 1.0453
CA | 6100_Boat Creek - ICI 66 kV | % of Rated A | 9.01% | 7.402% | 9.026% | 9.024% | 7.426% | 9.05% | 9.024% | 7.426% | 9.05% | 9.024% | 7.426% | 9.051% | 9.023% | 7.427% | 9.05%
CA | 6100_Boat Creek - ICI 66 kV | Limiting Line Name | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1
CA | 6100_Boat Creek - ICI 66 kV | Loading (A) | 59.6442 | 59.7318 | 59.7532 | 59.738 | 59.9303 | 59.9142 | 59.7382 | 59.9307 | 59.914 | 59.738 | 59.9308 | 59.9146 | 59.7334 | 59.9334 | 59.9087
CA | 6100_Boat Creek - ICI 66 kV | Loading (MVA) | 6.8915 | 6.9449 | 6.9029 | 6.8843 | 6.9456 | 6.9049 | 6.8843 | 6.9456 | 6.9049 | 6.8843 | 6.9456 | 6.9049 | 6.8842 | 6.9456 | 6.9035
CA | 6100_Boat Creek - ICI 66 kV | Loading (MW) | 5.9757 | 6.0203 | 5.9855 | 5.9691 | 6.0204 | 5.9868 | 5.9691 | 6.0204 | 5.9868 | 5.9691 | 6.0204 | 5.9868 | 5.9691 | 6.0204 | 5.9855
CA | 6100_Boat Creek - ICI 66 kV | Power Factor | 0.86705 | 0.86682 | 0.86703 | 0.867 | 0.86674 | 0.86697 | 0.867 | 0.86674 | 0.86697 | 0.867 | 0.86674 | 0.86697 | 0.867 | 0.86674 | 0.86697
CA | 6100_Boat Creek - ICI 66 kV | Rating (A) | 662 | 807 | 662 | 662 | 807 | 662 | 662 | 807 | 662 | 662 | 807 | 662 | 662 | 807 | 662
CA | 6100_Boat Creek - ICI 66 kV | Time | 06:00:00 | 17:00:00 | 03:00:00 | 07:30:00 | 17:00:00 | 05:00:00 | 07:30:00 | 17:00:00 | 05:00:00 | 07:30:00 | 17:00:00 | 05:00:00 | 07:30:00 | 17:00:00 | 03:00:00
CA | 6100_Boat Creek - ICI 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0107 | 1.0171 | 1.0106 | 1.0081 | 1.0138 | 1.0081 | 1.0081 | 1.0138 | 1.0081 | 1.0081 | 1.0138 | 1.0081 | 1.0082 | 1.0138 | 1.008
CA | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 4.409% | 3.837% | 4.367% | 4.402% | 3.85% | 4.382% | 4.402% | 3.85% | 4.381% | 4.402% | 3.85% | 4.382% | 4.426% | 3.85% | 4.381%
CA | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 29.1878 | 30.9622 | 28.9115 | 29.1396 | 31.0659 | 29.0056 | 29.1395 | 31.0661 | 29.0054 | 29.1402 | 31.0662 | 29.0057 | 29.3025 | 31.0677 | 29.0041
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 3.375 | 3.5988 | 3.3611 | 3.3748 | 3.5993 | 3.3616 | 3.3748 | 3.5993 | 3.3616 | 3.3748 | 3.5993 | 3.3616 | 3.3745 | 3.5993 | 3.3616
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 2.8742 | 3.0863 | 2.8851 | 2.8742 | 3.0863 | 2.8852 | 2.8742 | 3.0863 | 2.8852 | 2.8742 | 3.0863 | 2.8852 | 2.8741 | 3.0863 | 2.8852
CA | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.8514 | 0.85736 | 0.85817 | 0.85145 | 0.85726 | 0.85807 | 0.85145 | 0.85725 | 0.85807 | 0.85145 | 0.85725 | 0.85807 | 0.8515 | 0.85725 | 0.85808
CA | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 662 | 807 | 662 | 662 | 807 | 662 | 662 | 807 | 662 | 662 | 807 | 662 | 662 | 807 | 662
CA | 6102_Boat Creek - Yarwun 66 kV | Time | 08:30:00 | 19:00:00 | 22:00:00 | 08:30:00 | 19:00:00 | 22:00:00 | 08:30:00 | 19:00:00 | 22:00:00 | 08:30:00 | 19:00:00 | 22:00:00 | 08:30:00 | 19:00:00 | 22:00:00
CA | 6102_Boat Creek - Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0115 | 1.0168 | 1.017 | 1.0131 | 1.0135 | 1.0138 | 1.0131 | 1.0135 | 1.0138 | 1.0131 | 1.0135 | 1.0138 | 1.0074 | 1.0134 | 1.0139
CA | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 85.12% | 76.91% | 86.37% | 85.4% | 77.16% | 86.56% | 85.4% | 77.16% | 86.56% | 85.4% | 77.16% | 86.56% | 85.42% | 77.17% | 86.55%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 238.3368 | 236.1233 | 237.5121 | 239.1162 | 236.893 | 238.0436 | 239.1171 | 236.8941 | 238.0499 | 239.1172 | 236.8946 | 238.0449 | 239.1812 | 236.9029 | 238.0144
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.5038 | 27.2508 | 27.2123 | 27.5039 | 27.2508 | 27.2123 | 27.5039 | 27.2508 | 27.2123 | 27.5039 | 27.2508 | 27.2123 | 27.5039 | 27.2508 | 27.2013
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 26.3757 | 26.133 | 26.0962 | 26.3757 | 26.1331 | 26.0962 | 26.3757 | 26.1331 | 26.0962 | 26.3757 | 26.1331 | 26.0962 | 26.3757 | 26.1331 | 26.0856
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 16:00:00 | 19:30:00 | 02:00:00 | 16:00:00 | 19:30:00 | 02:00:00 | 16:00:00 | 19:30:00 | 02:00:00 | 16:00:00 | 19:30:00 | 02:00:00 | 16:00:00 | 19:30:00 | 02:30:00
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0093 | 1.0094 | 1.0021 | 1.006 | 1.0061 | 0.99987 | 1.006 | 1.0061 | 0.99984 | 1.006 | 1.0061 | 0.99986 | 1.0058 | 1.0061 | 0.99959
CA | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 74.49% | 53.67% | 49.22% | 74.63% | 53.78% | 49.3% | 74.77% | 53.89% | 49.38% | 74.56% | 53.75% | 49.27% | 75.95% | 54.78% | 50.06%
CA | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1
CA | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 270.4086 | 292.5095 | 226.9124 | 270.8904 | 293.1161 | 227.2801 | 271.4116 | 293.6831 | 227.6345 | 270.6657 | 292.9644 | 227.1478 | 275.7097 | 298.5481 | 230.7827
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 32.114 | 34.6951 | 26.9797 | 32.1696 | 34.765 | 27.0251 | 32.2306 | 34.8311 | 27.067 | 32.1434 | 34.7473 | 27.0096 | 32.7373 | 35.3994 | 27.44
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 31.2141 | 33.9411 | 25.4237 | 31.273 | 34.015 | 25.4721 | 31.3413 | 34.0877 | 25.5214 | 31.2416 | 33.9937 | 25.4511 | 31.8697 | 34.6956 | 25.9388
CA | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.97143 | 0.97772 | 0.94172 | 0.97158 | 0.97788 | 0.94193 | 0.97186 | 0.97812 | 0.94229 | 0.97139 | 0.97777 | 0.94169 | 0.97295 | 0.97959 | 0.94468
CA | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 6109_Gladstone North - Clinton 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6109_Gladstone North - Clinton 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0387 | 1.0373 | 1.0401 | 1.0387 | 1.0373 | 1.0402 | 1.0387 | 1.0372 | 1.0402 | 1.0387 | 1.0373 | 1.0402 | 1.0385 | 1.037 | 1.0401
CA | 6110_Port Curtis 66 kV | % of Rated A | 16.75% | 11.97% | 15.29% | 16.77% | 12% | 15.21% | 16.78% | 12.01% | 15.28% | 16.77% | 11.99% | 15.21% | 16.99% | 12.18% | 15.25%
CA | 6110_Port Curtis 66 kV | Limiting Line Name | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1
CA | 6110_Port Curtis 66 kV | Loading (A) | 60.7983 | 65.262 | 70.4659 | 60.875 | 65.3807 | 70.1078 | 60.9276 | 65.4717 | 70.4361 | 60.8683 | 65.3671 | 70.1367 | 61.6836 | 66.3784 | 70.295
CA | 6110_Port Curtis 66 kV | Loading (MVA) | 7.2084 | 7.7354 | 8.3612 | 7.2171 | 7.749 | 8.3216 | 7.2231 | 7.7595 | 8.3599 | 7.2164 | 7.7475 | 8.3251 | 7.3118 | 7.8648 | 8.3465
CA | 6110_Port Curtis 66 kV | Loading (MW) | 3.9309 | 5.269 | 0.83571 | 3.9501 | 5.2923 | 0.72873 | 3.9724 | 5.3161 | 0.81551 | 3.9399 | 5.2845 | 0.73433 | 4.1449 | 5.5111 | 0.72477
CA | 6110_Port Curtis 66 kV | Power Factor | 0.54532 | 0.68116 | 0.099489 | 0.54733 | 0.68296 | 0.087111 | 0.54997 | 0.68511 | 0.097089 | 0.54596 | 0.68209 | 0.087747 | 0.56689 | 0.70072 | 0.086374
CA | 6110_Port Curtis 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 6110_Port Curtis 66 kV | Time | 16:30:00 | 17:30:00 | 03:00:00 | 16:30:00 | 17:30:00 | 02:30:00 | 16:30:00 | 17:30:00 | 03:00:00 | 16:30:00 | 17:30:00 | 02:30:00 | 16:30:00 | 17:30:00 | 03:00:00
CA | 6110_Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0371 | 1.0369 | 1.038 | 1.0371 | 1.0368 | 1.0383 | 1.0371 | 1.0368 | 1.0382 | 1.0371 | 1.0368 | 1.0383 | 1.0369 | 1.0365 | 1.0387
CA | 6111_Gladstone North - Port Curtis 66 kV | % of Rated A | 39.07% | 28.96% | 28.62% | 39.12% | 29% | 28.65% | 39.17% | 29.03% | 28.68% | 39.09% | 28.99% | 28.64% | 39.58% | 29.35% | 28.93%
CA | 6111_Gladstone North - Port Curtis 66 kV | Limiting Line Name | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (A) | 141.8366 | 157.8221 | 131.9593 | 142.007 | 158.0347 | 132.0841 | 142.204 | 158.2373 | 132.2239 | 141.9148 | 157.9717 | 132.0223 | 143.6797 | 159.9339 | 133.3899
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MVA) | 16.8334 | 18.7004 | 15.6796 | 16.8528 | 18.7245 | 15.6954 | 16.8756 | 18.748 | 15.7119 | 16.8421 | 18.7173 | 15.6882 | 17.0488 | 18.9444 | 15.8496
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MW) | 16.789 | 18.5928 | 15.6352 | 16.8083 | 18.6166 | 15.651 | 16.8306 | 18.6394 | 15.6672 | 16.798 | 18.6098 | 15.6441 | 17.0035 | 18.8324 | 15.8037
CA | 6111_Gladstone North - Port Curtis 66 kV | Power Factor | 0.99736 | 0.99424 | 0.99717 | 0.99736 | 0.99424 | 0.99717 | 0.99733 | 0.99421 | 0.99716 | 0.99738 | 0.99426 | 0.99719 | 0.99734 | 0.99409 | 0.99711
CA | 6111_Gladstone North - Port Curtis 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 6111_Gladstone North - Port Curtis 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
CA | 6111_Gladstone North - Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0371 | 1.0353 | 1.0385 | 1.0371 | 1.0352 | 1.0385 | 1.0371 | 1.0352 | 1.0385 | 1.0371 | 1.0352 | 1.0385 | 1.0369 | 1.0349 | 1.0385
CA | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 12.84% | 13.62% | 10.07% | 12.89% | 13.66% | 10.04% | 13.06% | 13.83% | 10.15% | 13.11% | 13.87% | 10.17% | 13.54% | 14.33% | 10.46%
CA | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1
CA | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 48.5504 | 56.5368 | 33.9401 | 48.7351 | 56.6997 | 33.83 | 49.3554 | 57.3842 | 34.1984 | 49.5629 | 57.5655 | 34.2702 | 51.1946 | 59.4565 | 35.236
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 5.4943 | 6.236 | 3.8764 | 5.5085 | 6.2429 | 3.8876 | 5.5697 | 6.3041 | 3.9257 | 5.5875 | 6.3144 | 3.931 | 5.7335 | 6.47 | 4.0256
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 5.4933 | 6.2325 | 3.8653 | 5.5075 | 6.2396 | 3.8768 | 5.5685 | 6.3003 | 3.9154 | 5.5863 | 6.3107 | 3.9204 | 5.7319 | 6.4671 | 4.0151
CA | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.99982 | 0.99945 | 0.99713 | 0.99982 | 0.99946 | 0.99724 | 0.99978 | 0.9994 | 0.99738 | 0.99978 | 0.99942 | 0.9973 | 0.99971 | 0.99955 | 0.99738
CA | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 6298_Tanby - Yeppoon 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6298_Tanby - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98995 | 0.96485 | 0.99905 | 0.98874 | 0.96316 | 1.0052 | 0.98717 | 0.961 | 1.0041 | 0.98617 | 0.95953 | 1.0034 | 0.97968 | 0.9519 | 0.99935
CA | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 32.33% | 39.6% | 31.01% | 32.66% | 40.02% | 31.38% | 32.95% | 40.41% | 31.6% | 33.32% | 40.86% | 31.89% | 34.52% | 42.4% | 32.93%
CA | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | 6310_Lakes Creek | 6310_Lakes Creek | TR_LINE 20950_1 | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek | 6310_Lakes Creek
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 129.6446 | 165.5158 | 115.3613 | 130.9755 | 167.2848 | 116.7502 | 132.1198 | 168.9234 | 117.5501 | 133.5984 | 170.8084 | 118.6262 | 138.4407 | 177.2244 | 122.4816
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 15.4442 | 19.5415 | 13.7296 | 15.5969 | 19.7391 | 13.926 | 15.725 | 19.9175 | 14.0167 | 15.8983 | 20.1328 | 14.1429 | 16.4121 | 20.7999 | 14.5706
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 15.384 | 19.3282 | 13.729 | 15.531 | 19.5126 | 13.9149 | 15.653 | 19.6766 | 14.0038 | 15.8199 | 19.8778 | 14.1279 | 16.324 | 20.5185 | 14.5497
CA | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.9961 | 0.98908 | 0.99996 | 0.99578 | 0.98853 | 0.9992 | 0.99542 | 0.9879 | 0.99908 | 0.99507 | 0.98734 | 0.99894 | 0.99463 | 0.98647 | 0.99856
CA | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6310_Lakes Creek - Berserker 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
CA | 6310_Lakes Creek - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0421 | 1.0328 | 1.0409 | 1.0417 | 1.0322 | 1.0434 | 1.0412 | 1.0314 | 1.0431 | 1.041 | 1.0311 | 1.0429 | 1.037 | 1.0267 | 1.0406
CA | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 14.91% | 13.25% | 15.6% | 17.34% | 15.35% | 18.05% | 17.34% | 15.35% | 18.05% | 17.34% | 15.35% | 18.05% | 17.38% | 15.35% | 18.04%
CA | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 125.1307 | 130.4271 | 130.8938 | 145.4717 | 151.063 | 151.4465 | 145.4722 | 151.064 | 151.4505 | 145.4718 | 151.0643 | 151.4473 | 145.7913 | 151.0708 | 151.3765
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 29.6802 | 31.1446 | 31.0453 | 34.4873 | 36.0318 | 35.9108 | 34.4873 | 36.0318 | 35.9109 | 34.4873 | 36.0318 | 35.9108 | 34.5567 | 36.0319 | 35.884
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 27.314 | 28.6612 | 28.5678 | 31.7437 | 33.181 | 33.0716 | 31.7437 | 33.181 | 33.0716 | 31.7437 | 33.181 | 33.0716 | 31.799 | 33.181 | 33.0474
CA | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.92025 | 0.92023 | 0.92016 | 0.92041 | 0.92084 | 0.9209 | 0.92041 | 0.92084 | 0.9209 | 0.92041 | 0.92084 | 0.9209 | 0.92016 | 0.92084 | 0.92091
CA | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 839 | 984 | 839 | 839 | 984 | 839 | 839 | 984 | 839 | 839 | 984 | 839 | 839 | 984 | 839
CA | 7290_Boat Creek - Yarwun 132 kV | Time | 06:00:00 | 17:00:00 | 01:30:00 | 07:30:00 | 17:00:00 | 02:00:00 | 07:30:00 | 17:00:00 | 02:00:00 | 07:30:00 | 17:00:00 | 02:00:00 | 08:30:00 | 17:00:00 | 02:30:00
CA | 7290_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0375 | 1.0444 | 1.0374 | 1.0369 | 1.0433 | 1.0371 | 1.0369 | 1.0433 | 1.0371 | 1.0369 | 1.0433 | 1.0371 | 1.0367 | 1.0432 | 1.0368
CA | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 14.99% | 13.32% | 15.68% | 17.42% | 15.43% | 18.14% | 17.42% | 15.43% | 18.14% | 17.42% | 15.43% | 18.14% | 17.46% | 15.43% | 18.13%
CA | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 125.7318 | 131.0536 | 131.5225 | 146.1705 | 151.7887 | 152.174 | 146.171 | 151.7897 | 152.178 | 146.1706 | 151.79 | 152.1748 | 146.4917 | 151.7965 | 152.1036
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 29.8237 | 31.2951 | 31.1954 | 34.6542 | 36.2062 | 36.0846 | 34.6542 | 36.2062 | 36.0847 | 34.6542 | 36.2062 | 36.0847 | 34.7239 | 36.2063 | 36.0577
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 27.4429 | 28.7965 | 28.7026 | 31.8934 | 33.3375 | 33.2277 | 31.8934 | 33.3375 | 33.2277 | 31.8934 | 33.3375 | 33.2277 | 31.9491 | 33.3376 | 33.2034
CA | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.92015 | 0.92013 | 0.92006 | 0.92031 | 0.92074 | 0.9208 | 0.92031 | 0.92074 | 0.92079 | 0.92031 | 0.92074 | 0.9208 | 0.92006 | 0.92074 | 0.92081
CA | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 839 | 984 | 839 | 839 | 984 | 839 | 839 | 984 | 839 | 839 | 984 | 839 | 839 | 984 | 839
CA | 7291_Boat Creek - Yarwun 132 kV | Time | 06:00:00 | 17:00:00 | 01:30:00 | 07:30:00 | 17:00:00 | 02:00:00 | 07:30:00 | 17:00:00 | 02:00:00 | 07:30:00 | 17:00:00 | 02:00:00 | 08:30:00 | 17:00:00 | 02:30:00
CA | 7291_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0375 | 1.0445 | 1.0374 | 1.037 | 1.0433 | 1.0372 | 1.037 | 1.0433 | 1.0371 | 1.037 | 1.0433 | 1.0372 | 1.0368 | 1.0432 | 1.0369
CA | 6026_Moura - Theodore 66 kV | % of Rated A | 15.9% | 14.9% | 13.82% | 15.76% | 14.78% | 13.7% | 15.76% | 14.78% | 13.7% | 15.62% | 14.65% | 13.58% | 15.9% | 14.91% | 13.82%
CA | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1
CA | 6026_Moura - Theodore 66 kV | Loading (A) | 115.8883 | 116.7037 | 98.087 | 114.911 | 115.7189 | 97.271 | 114.9104 | 115.7184 | 97.27 | 113.9038 | 114.7037 | 96.4437 | 115.9358 | 116.7536 | 98.0997
CA | 6026_Moura - Theodore 66 kV | Loading (MVA) | 13.0417 | 13.1145 | 11.2175 | 12.9385 | 13.0107 | 11.1291 | 12.9385 | 13.0107 | 11.1291 | 12.8353 | 12.9069 | 11.0408 | 13.0419 | 13.1147 | 11.2175
CA | 6026_Moura - Theodore 66 kV | Loading (MW) | 12.616 | 12.685 | 10.8753 | 12.5177 | 12.5862 | 10.7906 | 12.5177 | 12.5862 | 10.7906 | 12.4194 | 12.4873 | 10.7059 | 12.6161 | 12.685 | 10.8753
CA | 6026_Moura - Theodore 66 kV | Power Factor | 0.96736 | 0.96725 | 0.96948 | 0.96748 | 0.96737 | 0.96958 | 0.96748 | 0.96737 | 0.96958 | 0.9676 | 0.96749 | 0.96967 | 0.96735 | 0.96724 | 0.96948
CA | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
CA | 6026_Moura - Theodore 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
CA | 6026_Moura - Theodore 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98442 | 0.983 | 1.0004 | 0.98494 | 0.98352 | 1.0009 | 0.98495 | 0.98353 | 1.0009 | 0.98572 | 0.98431 | 1.0014 | 0.98403 | 0.98259 | 1.0003
FN | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 25.56% | 21.85% | 16.35% | 25.56% | 21.85% | 16.35% | 25.61% | 21.89% | 16.38% | 25.41% | 21.72% | 16.25% | 25.86% | 22.11% | 16.54%
FN | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 106.829 | 98.3172 | 66.6949 | 106.8305 | 98.3186 | 66.6959 | 107.0446 | 98.5154 | 66.8284 | 106.2005 | 97.7402 | 66.3069 | 108.1106 | 99.495 | 67.4878
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 25.6279 | 23.5878 | 16.0079 | 25.6282 | 23.5881 | 16.0082 | 25.6795 | 23.6353 | 16.04 | 25.4773 | 23.4495 | 15.9148 | 25.935 | 23.8701 | 16.1982
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 25.5947 | 23.5688 | 16.0074 | 25.5951 | 23.5691 | 16.0077 | 25.646 | 23.616 | 16.0395 | 25.4453 | 23.4313 | 15.9142 | 25.8993 | 23.8493 | 16.1979
FN | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99845 | 0.99896 | 0.99997 | 0.99845 | 0.99896 | 0.99997 | 0.99843 | 0.99894 | 0.99997 | 0.99848 | 0.99899 | 0.99996 | 0.99836 | 0.99889 | 0.99998
FN | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408
FN | 7206 Woree-Cairns Terminal-Cairns City | Time | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00
FN | 7206 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 1.0487 | 1.0488 | 1.0493 | 1.0487 | 1.0488 | 1.0493 | 1.0487 | 1.0488 | 1.0493 | 1.0487 | 1.0488 | 1.0493 | 1.0487 | 1.0488 | 1.0493
FN | 7227 Woree-Cairns Terminal-Cairns City | % of Rated A | 25.43% | 21.72% | 16.24% | 25.43% | 21.72% | 16.24% | 25.48% | 21.76% | 16.28% | 25.28% | 21.59% | 16.15% | 25.73% | 21.98% | 16.43%
FN | 7227 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 176513_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 176513_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 176513_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 176513_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 176513_1
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (A) | 106.2961 | 97.7459 | 66.278 | 106.2949 | 97.7447 | 66.2771 | 106.504 | 97.9363 | 66.4058 | 105.6581 | 97.1594 | 65.8831 | 107.5531 | 98.8984 | 67.0525
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 25.4934 | 23.4441 | 15.9047 | 25.4931 | 23.4438 | 15.9045 | 25.5431 | 23.4896 | 15.9353 | 25.3404 | 23.3034 | 15.8099 | 25.7943 | 23.7199 | 16.0903
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MW) | 25.4639 | 23.4281 | 15.9036 | 25.4636 | 23.4278 | 15.9033 | 25.5133 | 23.4734 | 15.9342 | 25.3121 | 23.2883 | 15.8086 | 25.7625 | 23.7024 | 16.0894
FN | 7227 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99861 | 0.99911 | 0.99993 | 0.99861 | 0.99911 | 0.99993 | 0.9986 | 0.9991 | 0.99993 | 0.99865 | 0.99914 | 0.99992 | 0.99853 | 0.99905 | 0.99994
FN | 7227 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408
FN | 7227 Woree-Cairns Terminal-Cairns City | Time | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00
FN | 7227 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 1.0484 | 1.0485 | 1.0496 | 1.0484 | 1.0485 | 1.0496 | 1.0484 | 1.0485 | 1.0496 | 1.0484 | 1.0485 | 1.0496 | 1.0484 | 1.0485 | 1.0496
FN | 7332_Cairns North 132 kV | % of Rated A | 27.68% | 28.09% | 25.47% | 27.8% | 28.22% | 25.58% | 28.05% | 28.47% | 25.8% | 28.17% | 28.6% | 25.91% | 28.95% | 29.39% | 26.6%
FN | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN | 7332_Cairns North 132 kV | Loading (A) | 130.9357 | 139.6231 | 113.587 | 131.514 | 140.2466 | 114.0746 | 132.6716 | 141.4945 | 115.0507 | 133.2509 | 142.119 | 115.5392 | 136.9274 | 146.0821 | 118.6403
FN | 7332_Cairns North 132 kV | Loading (MVA) | 31.4327 | 33.5182 | 27.2679 | 31.5715 | 33.6679 | 27.385 | 31.8494 | 33.9675 | 27.6193 | 31.9885 | 34.1174 | 27.7366 | 32.8711 | 35.0688 | 28.481
FN | 7332_Cairns North 132 kV | Loading (MW) | 31.1959 | 33.3578 | 26.8217 | 31.3403 | 33.5123 | 26.9459 | 31.6292 | 33.8213 | 27.1941 | 31.7737 | 33.9758 | 27.3183 | 32.6887 | 34.9545 | 28.1046
FN | 7332_Cairns North 132 kV | Power Factor | 0.99247 | 0.99521 | 0.98364 | 0.99268 | 0.99538 | 0.98396 | 0.99309 | 0.9957 | 0.9846 | 0.99328 | 0.99585 | 0.98492 | 0.99445 | 0.99674 | 0.98678
FN | 7332_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 7332_Cairns North 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
FN | 7332_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
FN | 7333_Cairns North 132 kV | % of Rated A | 26.4% | 26.79% | 24.29% | 26.51% | 26.91% | 24.39% | 26.75% | 27.15% | 24.6% | 26.86% | 27.27% | 24.71% | 27.6% | 28.03% | 25.37%
FN | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN | 7333_Cairns North 132 kV | Loading (A) | 124.8602 | 133.1371 | 108.3332 | 125.4112 | 133.7311 | 108.7977 | 126.514 | 134.9201 | 109.7275 | 127.0659 | 135.5151 | 110.1928 | 130.5687 | 139.2912 | 113.1468
FN | 7333_Cairns North 132 kV | Loading (MVA) | 29.9742 | 31.9612 | 26.0067 | 30.1065 | 32.1038 | 26.1182 | 30.3712 | 32.3892 | 26.3414 | 30.5037 | 32.532 | 26.4531 | 31.3446 | 33.4385 | 27.1623
FN | 7333_Cairns North 132 kV | Loading (MW) | 29.7459 | 31.8064 | 25.5769 | 29.8836 | 31.9537 | 25.6952 | 30.159 | 32.2482 | 25.9318 | 30.2967 | 32.3955 | 26.0501 | 31.1688 | 33.3282 | 26.7996
FN | 7333_Cairns North 132 kV | Power Factor | 0.99238 | 0.99516 | 0.98347 | 0.9926 | 0.99532 | 0.9838 | 0.99301 | 0.99565 | 0.98445 | 0.99321 | 0.9958 | 0.98476 | 0.99439 | 0.9967 | 0.98665
FN | 7333_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 7333_Cairns North 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
FN | 7333_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
FN | 3CRO_Croydon 66 kV | % of Rated A | 12.55% | 12.4% | 10.19% | 12.58% | 12.36% | 10.11% | 12.58% | 12.36% | 10.11% | 12.58% | 12.36% | 10.11% | 12.77% | 12.5% | 10.26%
FN | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN | 3CRO_Croydon 66 kV | Loading (A) | 57.3546 | 60.3664 | 48.0828 | 57.4709 | 60.1801 | 47.7108 | 57.4709 | 60.1801 | 47.7108 | 57.4709 | 60.1801 | 47.7108 | 58.3666 | 60.8774 | 48.4222
FN | 3CRO_Croydon 66 kV | Loading (MVA) | 6.8355 | 7.1885 | 5.7286 | 6.8449 | 7.1616 | 5.6958 | 6.8449 | 7.1616 | 5.6958 | 6.8449 | 7.1616 | 5.6958 | 6.9495 | 7.2651 | 5.7794
FN | 3CRO_Croydon 66 kV | Loading (MW) | 6.0758 | 6.4404 | 4.8738 | 6.0767 | 6.4024 | 4.8718 | 6.0767 | 6.4024 | 4.8718 | 6.0767 | 6.4024 | 4.8718 | 6.1829 | 6.5498 | 4.9567
FN | 3CRO_Croydon 66 kV | Power Factor | 0.88886 | 0.89593 | 0.85077 | 0.88777 | 0.894 | 0.85532 | 0.88777 | 0.894 | 0.85532 | 0.88777 | 0.894 | 0.85532 | 0.8897 | 0.90154 | 0.85765
FN | 3CRO_Croydon 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 3CRO_Croydon 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
FN | 3CRO_Croydon 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0426 | 1.0417 | 1.0422 | 1.0419 | 1.041 | 1.0443 | 1.0419 | 1.041 | 1.0443 | 1.0419 | 1.041 | 1.0443 | 1.0416 | 1.0438 | 1.0441
FN | 3NOR_Normanton 66 kV | % of Rated A | 10.13% | 10.1% | 7.979% | 10.15% | 10.07% | 7.929% | 10.15% | 10.07% | 7.929% | 10.15% | 10.07% | 7.929% | 10.35% | 10.24% | 8.085%
FN | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN | 3NOR_Normanton 66 kV | Loading (A) | 46.3128 | 49.2112 | 37.6586 | 46.3942 | 49.0221 | 37.425 | 46.3942 | 49.0222 | 37.425 | 46.3942 | 49.0222 | 37.425 | 47.3149 | 49.8731 | 38.1626
FN | 3NOR_Normanton 66 kV | Loading (MVA) | 5.5267 | 5.8649 | 4.5046 | 5.5341 | 5.8404 | 4.4825 | 5.5341 | 5.8404 | 4.4825 | 5.5341 | 5.8404 | 4.4825 | 5.6417 | 5.9509 | 4.5695
FN | 3NOR_Normanton 66 kV | Loading (MW) | 5.2462 | 5.5605 | 4.2738 | 5.2465 | 5.5304 | 4.2734 | 5.2465 | 5.5304 | 4.2734 | 5.2465 | 5.5304 | 4.2734 | 5.3467 | 5.6658 | 4.3544
FN | 3NOR_Normanton 66 kV | Power Factor | 0.94924 | 0.9481 | 0.94876 | 0.94802 | 0.94692 | 0.95336 | 0.94802 | 0.94692 | 0.95336 | 0.94802 | 0.94692 | 0.95336 | 0.94771 | 0.95209 | 0.95294
FN | 3NOR_Normanton 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 3NOR_Normanton 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
FN | 3NOR_Normanton 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0293 | 1.0284 | 1.0315 | 1.0292 | 1.0284 | 1.032 | 1.0292 | 1.0284 | 1.032 | 1.0292 | 1.0284 | 1.032 | 1.0289 | 1.0286 | 1.0318
FN | 4KID_Ross - Kidston 132 kV | % of Rated A | 21.42% | 20.22% | 21.22% | 22.02% | 20.66% | 21.38% | 22.02% | 20.66% | 21.38% | 22.02% | 20.66% | 21.38% | 22.14% | 20.62% | 21.47%
FN | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN | 4KID_Ross - Kidston 132 kV | Loading (A) | 76.0586 | 77.8375 | 73.6329 | 78.1649 | 79.5264 | 74.2 | 78.1651 | 79.5265 | 74.2001 | 78.1651 | 79.5266 | 74.2002 | 78.5798 | 79.387 | 74.5071
FN | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 18.2548 | 18.6816 | 17.673 | 18.7607 | 19.0874 | 17.8094 | 18.7608 | 19.0874 | 17.8094 | 18.7608 | 19.0874 | 17.8094 | 18.8602 | 19.0539 | 17.8831
FN | 4KID_Ross - Kidston 132 kV | Loading (MW) | 12.1848 | 12.7317 | 10.2577 | 9.5435 | 10.0841 | 7.833 | 9.5435 | 10.0841 | 7.833 | 9.5435 | 10.0841 | 7.833 | 9.7501 | 10.0649 | 8.0071
FN | 4KID_Ross - Kidston 132 kV | Power Factor | 0.66748 | 0.68151 | 0.58042 | 0.5087 | 0.52831 | 0.43982 | 0.5087 | 0.52831 | 0.43982 | 0.5087 | 0.52831 | 0.43982 | 0.51697 | 0.52823 | 0.44774
FN | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347
FN | 4KID_Ross - Kidston 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
FN | 4KID_Ross - Kidston 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498
FN | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 12.46% | 11.41% | 9.095% | 12.07% | 11.53% | 9.267% | 12.07% | 11.53% | 9.267% | 12.07% | 11.53% | 9.267% | 12.16% | 11.61% | 9.308%
FN | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 37.122 | 39.2506 | 31.1053 | 35.9631 | 39.6704 | 31.6926 | 35.963 | 39.6703 | 31.6925 | 35.963 | 39.6702 | 31.6925 | 36.2279 | 39.9489 | 31.8321
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 8.8453 | 9.3417 | 7.4986 | 8.7722 | 9.5963 | 7.7583 | 8.7721 | 9.5963 | 7.7583 | 8.7721 | 9.5963 | 7.7583 | 8.8324 | 9.6587 | 7.7893
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 7.8682 | 8.498 | 6.3471 | 7.8656 | 8.4956 | 6.3466 | 7.8656 | 8.4956 | 6.3466 | 7.8656 | 8.4956 | 6.3466 | 7.9728 | 8.6098 | 6.432
FN | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.88391 | 0.90357 | 0.8421 | 0.89133 | 0.87936 | 0.81381 | 0.89133 | 0.87936 | 0.81381 | 0.89133 | 0.87936 | 0.81381 | 0.89728 | 0.88539 | 0.82146
FN | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342
FN | 7216_4GEO (Georgetown) 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
FN | 7216_4GEO (Georgetown) 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0422 | 1.041 | 1.0544 | 1.0669 | 1.058 | 1.0707 | 1.0669 | 1.058 | 1.0707 | 1.0669 | 1.058 | 1.0707 | 1.0663 | 1.0575 | 1.0703
FN | 3AT1_Atherton No 1 66 kV | % of Rated A | 20.73% | 23.46% | 20.37% | 20.8% | 23.32% | 20.44% | 20.89% | 23.33% | 20.52% | 20.88% | 23.33% | 20.51% | 21.34% | 23.86% | 20.95%
FN | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1
FN | 3AT1_Atherton No 1 66 kV | Loading (A) | 113.5794 | 131.3626 | 106.1145 | 113.9968 | 130.6069 | 106.4942 | 114.4572 | 130.6707 | 106.8926 | 114.4352 | 130.6359 | 106.876 | 116.9472 | 133.6284 | 109.144
FN | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 13.4966 | 15.5979 | 12.5894 | 13.5397 | 15.518 | 12.6297 | 13.5828 | 15.6983 | 12.6701 | 13.5828 | 15.6983 | 12.6701 | 13.8403 | 16.005 | 12.9096
FN | 3AT1_Atherton No 1 66 kV | Loading (MW) | 13.4585 | 15.5815 | 12.528 | 13.5023 | 15.5004 | 12.5693 | 13.5463 | 15.6793 | 12.6106 | 13.5463 | 15.6792 | 12.6106 | 13.812 | 15.9893 | 12.8607
FN | 3AT1_Atherton No 1 66 kV | Power Factor | 0.99717 | 0.99895 | 0.99513 | 0.99724 | 0.99886 | 0.99521 | 0.99731 | 0.99879 | 0.99531 | 0.99731 | 0.99878 | 0.9953 | 0.99795 | 0.99902 | 0.99621
FN | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 3AT1_Atherton No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
FN | 3AT1_Atherton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0392 | 1.0385 | 1.0376 | 1.0387 | 1.0392 | 1.0372 | 1.0378 | 1.0507 | 1.0366 | 1.038 | 1.051 | 1.0368 | 1.0349 | 1.0476 | 1.0344
FN | 3AT2_Atherton No 2 66 kV | % of Rated A | 20.72% | 23.46% | 20.37% | 20.8% | 23.32% | 20.44% | 20.89% | 23.33% | 20.52% | 20.88% | 23.33% | 20.51% | 21.34% | 23.86% | 20.95%
FN | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1
FN | 3AT2_Atherton No 2 66 kV | Loading (A) | 113.573 | 131.354 | 106.1093 | 113.9904 | 130.5984 | 106.489 | 114.4507 | 130.6623 | 106.8873 | 114.4287 | 130.6276 | 106.8707 | 116.9403 | 133.6197 | 109.1383
FN | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 13.4958 | 15.5969 | 12.5888 | 13.5389 | 15.517 | 12.6291 | 13.582 | 15.6973 | 12.6694 | 13.582 | 15.6973 | 12.6695 | 13.8395 | 16.0039 | 12.9089
FN | 3AT2_Atherton No 2 66 kV | Loading (MW) | 13.4575 | 15.5804 | 12.5271 | 13.5013 | 15.4992 | 12.5684 | 13.5453 | 15.6781 | 12.6097 | 13.5453 | 15.678 | 12.6096 | 13.811 | 15.9881 | 12.8597
FN | 3AT2_Atherton No 2 66 kV | Power Factor | 0.99716 | 0.99894 | 0.9951 | 0.99722 | 0.99885 | 0.99519 | 0.9973 | 0.99878 | 0.99528 | 0.99729 | 0.99877 | 0.99528 | 0.99794 | 0.99901 | 0.99619
FN | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 3AT2_Atherton No 2 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
FN | 3AT2_Atherton No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0392 | 1.0385 | 1.0376 | 1.0387 | 1.0392 | 1.0372 | 1.0378 | 1.0507 | 1.0366 | 1.038 | 1.051 | 1.0368 | 1.0349 | 1.0476 | 1.0344
FN | 3CHI_Chillagoe 66 kV | % of Rated A | 2.467% | 2.194% | 2.495% | 2.466% | 2.193% | 2.494% | 2.465% | 2.185% | 2.493% | 2.466% | 2.186% | 2.493% | 2.463% | 2.199% | 2.491%
FN | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1
FN | 3CHI_Chillagoe 66 kV | Loading (A) | 12.8538 | 12.7053 | 12.9969 | 12.8504 | 12.6984 | 12.9941 | 12.8447 | 12.6486 | 12.9894 | 12.8464 | 12.6557 | 12.9907 | 12.8299 | 12.7328 | 12.9768
FN | 3CHI_Chillagoe 66 kV | Loading (MVA) | 1.5324 | 1.5147 | 1.5647 | 1.5316 | 1.513 | 1.5641 | 1.5302 | 1.5018 | 1.5629 | 1.5306 | 1.5035 | 1.5633 | 1.5268 | 1.5204 | 1.56
FN | 3CHI_Chillagoe 66 kV | Loading (MW) | 0.25378 | 0.44608 | 0.24869 | 0.25378 | 0.44608 | 0.24869 | 0.25378 | 0.45921 | 0.24869 | 0.25378 | 0.45921 | 0.24869 | 0.25378 | 0.42536 | 0.24868
FN | 3CHI_Chillagoe 66 kV | Power Factor | 0.16562 | 0.29451 | 0.15894 | 0.1657 | 0.29483 | 0.159 | 0.16584 | 0.30577 | 0.15911 | 0.1658 | 0.30543 | 0.15908 | 0.16621 | 0.27976 | 0.15941
FN | 3CHI_Chillagoe 66 kV | Rating (A) | 521 | 579 | 521 | 521 | 579 | 521 | 521 | 579 | 521 | 521 | 579 | 521 | 521 | 579 | 521
FN | 3CHI_Chillagoe 66 kV | Time | 06:00:00 | 19:00:00 | 02:30:00 | 06:00:00 | 19:00:00 | 02:30:00 | 06:00:00 | 17:30:00 | 02:30:00 | 06:00:00 | 17:30:00 | 02:30:00 | 06:00:00 | 19:30:00 | 02:30:00
FN | 3CHI_Chillagoe 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0428 | 1.0429 | 1.0531 | 1.0426 | 1.0423 | 1.0529 | 1.0421 | 1.0387 | 1.0526 | 1.0423 | 1.0392 | 1.0527 | 1.041 | 1.0446 | 1.0516
FN | 3COO_Cooktown 66 kV | % of Rated A | 17.86% | 18.77% | 14.02% | 17.52% | 18.43% | 13.76% | 17.54% | 18.44% | 13.59% | 17.54% | 18.42% | 13.59% | 17.6% | 18.5% | 13.62%
FN | 3COO_Cooktown 66 kV | Limiting Line Name | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1
FN | 3COO_Cooktown 66 kV | Loading (A) | 44.2816 | 46.562 | 34.7712 | 43.4434 | 45.7007 | 34.1137 | 43.5072 | 45.7212 | 33.7077 | 43.4915 | 45.6907 | 33.6983 | 43.6402 | 45.8753 | 33.7827
FN | 3COO_Cooktown 66 kV | Loading (MVA) | 5.0797 | 5.3354 | 3.9823 | 4.9832 | 5.2341 | 3.9068 | 4.9833 | 5.2341 | 3.9068 | 4.9833 | 5.2341 | 3.9068 | 4.9835 | 5.2344 | 3.9069
FN | 3COO_Cooktown 66 kV | Loading (MW) | 4.9827 | 5.2321 | 3.911 | 4.8886 | 5.1333 | 3.8371 | 4.8886 | 5.1333 | 3.8372 | 4.8886 | 5.1333 | 3.8372 | 4.8887 | 5.1333 | 3.8372
FN | 3COO_Cooktown 66 kV | Power Factor | 0.98041 | 0.98015 | 0.98144 | 0.9805 | 0.98024 | 0.98151 | 0.98048 | 0.98024 | 0.98151 | 0.98049 | 0.98024 | 0.98151 | 0.98046 | 0.9802 | 0.98149
FN | 3COO_Cooktown 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
FN | 3COO_Cooktown 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
FN | 3COO_Cooktown 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0035 | 1.0024 | 1.0019 | 1.0034 | 1.0019 | 1.0018 | 1.002 | 1.0014 | 1.0139 | 1.0023 | 1.0021 | 1.0142 | 0.99895 | 0.99812 | 1.0117
FN | 3DIM_Dimbulah 66 kV | % of Rated A | 24.59% | 20.92% | 29.88% | 24.59% | 20.93% | 29.89% | 24.6% | 20.96% | 29.91% | 24.6% | 20.96% | 29.91% | 24.62% | 21.03% | 29.97%
FN | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1
FN | 3DIM_Dimbulah 66 kV | Loading (A) | 53.5998 | 56.2752 | 75.5987 | 53.6084 | 56.3092 | 75.6282 | 53.6279 | 56.3915 | 75.6779 | 53.6212 | 56.3833 | 75.6651 | 53.6811 | 56.5579 | 75.8236
FN | 3DIM_Dimbulah 66 kV | Loading (MVA) | 6.3955 | 6.6938 | 8.904 | 6.3956 | 6.6941 | 8.9043 | 6.3958 | 6.6949 | 8.905 | 6.3958 | 6.6949 | 8.9048 | 6.3964 | 6.6965 | 8.9071
FN | 3DIM_Dimbulah 66 kV | Loading (MW) | 6.323 | 6.6422 | 8.6103 | 6.323 | 6.6423 | 8.6103 | 6.323 | 6.6422 | 8.6104 | 6.323 | 6.6422 | 8.6103 | 6.323 | 6.6424 | 8.6107
FN | 3DIM_Dimbulah 66 kV | Power Factor | 0.9883 | 0.99203 | 0.96671 | 0.98828 | 0.99198 | 0.96667 | 0.98825 | 0.99186 | 0.96661 | 0.98826 | 0.99187 | 0.96662 | 0.98817 | 0.99165 | 0.96642
FN | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253
FN | 3DIM_Dimbulah 66 kV | Time | 13:30:00 | 17:00:00 | 22:30:00 | 13:30:00 | 17:00:00 | 22:30:00 | 13:30:00 | 17:00:00 | 22:30:00 | 13:30:00 | 17:00:00 | 22:30:00 | 13:30:00 | 17:00:00 | 22:30:00
FN | 3DIM_Dimbulah 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0436 | 1.0402 | 1.0298 | 1.0434 | 1.0396 | 1.0294 | 1.0431 | 1.0382 | 1.0288 | 1.0432 | 1.0384 | 1.029 | 1.0422 | 1.0354 | 1.0271
FN | 3EVE_Evelyn 66 kV | % of Rated A | 15.79% | 13.86% | 11.48% | 15.8% | 13.68% | 11.48% | 15.81% | 13.69% | 11.49% | 15.81% | 13.69% | 11.49% | 15.87% | 13.74% | 11.52%
FN | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN | 3EVE_Evelyn 66 kV | Loading (A) | 26.6873 | 33.4089 | 26.9758 | 26.702 | 32.9625 | 26.9874 | 26.7272 | 33 | 27.0041 | 26.7217 | 32.9907 | 26.9996 | 26.8156 | 33.1177 | 27.0748
FN | 3EVE_Evelyn 66 kV | Loading (MVA) | 3.1205 | 3.8888 | 3.1528 | 3.1205 | 3.8883 | 3.1528 | 3.1205 | 3.8883 | 3.1528 | 3.1205 | 3.8883 | 3.1528 | 3.1206 | 3.8885 | 3.1528
FN | 3EVE_Evelyn 66 kV | Loading (MW) | 3.1205 | 3.8868 | 3.1527 | 3.1205 | 3.8866 | 3.1527 | 3.1205 | 3.8866 | 3.1528 | 3.1205 | 3.8866 | 3.1528 | 3.1205 | 3.8867 | 3.1528
FN | 3EVE_Evelyn 66 kV | Power Factor | 0.99998 | 0.99948 | 0.99999 | 0.99998 | 0.99956 | 0.99999 | 0.99998 | 0.99955 | 0.99999 | 0.99998 | 0.99956 | 0.99999 | 0.99997 | 0.99953 | 0.99998
FN | 3EVE_Evelyn 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 3EVE_Evelyn 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
FN | 3EVE_Evelyn 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0229 | 1.0182 | 1.0224 | 1.0223 | 1.0319 | 1.0219 | 1.0213 | 1.0307 | 1.0213 | 1.0215 | 1.031 | 1.0215 | 1.018 | 1.0271 | 1.0187
FN | 3HLA_Helenvale 66 kV | % of Rated A | 13.12% | 13.17% | 10.85% | 12.9% | 12.96% | 10.68% | 12.92% | 12.96% | 10.55% | 12.92% | 12.95% | 10.54% | 12.96% | 13.01% | 10.57%
FN | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1
FN | 3HLA_Helenvale 66 kV | Loading (A) | 49.593 | 52.5359 | 40.1542 | 48.7797 | 51.7014 | 39.503 | 48.8502 | 51.7244 | 39.0247 | 48.8328 | 51.6902 | 39.0136 | 48.9975 | 51.8971 | 39.1126
FN | 3HLA_Helenvale 66 kV | Loading (MVA) | 5.8278 | 6.177 | 4.6296 | 5.7292 | 6.0728 | 4.5536 | 5.7296 | 6.073 | 4.5519 | 5.7295 | 6.0727 | 4.5518 | 5.7305 | 6.0743 | 4.5523
FN | 3HLA_Helenvale 66 kV | Loading (MW) | 5.8261 | 6.172 | 4.6087 | 5.7281 | 6.0689 | 4.534 | 5.7284 | 6.069 | 4.5335 | 5.7283 | 6.0689 | 4.5335 | 5.7291 | 6.0699 | 4.5336
FN | 3HLA_Helenvale 66 kV | Power Factor | 0.99947 | 0.99886 | 0.99526 | 0.9996 | 0.99904 | 0.99546 | 0.99958 | 0.99903 | 0.99574 | 0.99958 | 0.99904 | 0.99575 | 0.99953 | 0.99895 | 0.99568
FN | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370
FN | 3HLA_Helenvale 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
FN | 3HLA_Helenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0271 | 1.0276 | 1.0086 | 1.0265 | 1.0266 | 1.0084 | 1.0251 | 1.0262 | 1.0203 | 1.0254 | 1.0268 | 1.0206 | 1.0222 | 1.023 | 1.0181
FN | 3MO1_Mossman No 1 66 kV | % of Rated A | 65.28% | 64.61% | 51.78% | 65.53% | 64.1% | 51.97% | 65.8% | 64.41% | 52.17% | 65.56% | 64.16% | 51.99% | 67.09% | 65.76% | 53.16%
FN | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN | 3MO1_Mossman No 1 66 kV | Loading (A) | 86.1656 | 107.8951 | 82.3297 | 86.499 | 107.0493 | 82.6367 | 86.8591 | 107.5652 | 82.9555 | 86.5446 | 107.154 | 82.6615 | 88.5631 | 109.8139 | 84.5175
FN | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 10.1949 | 12.7349 | 9.73 | 10.229 | 12.804 | 9.7623 | 10.2623 | 12.8477 | 9.7942 | 10.2275 | 12.802 | 9.7614 | 10.4329 | 13.0732 | 9.9557
FN | 3MO1_Mossman No 1 66 kV | Loading (MW) | 9.6745 | 12.3899 | 9.1745 | 9.7128 | 12.4346 | 9.2109 | 9.7513 | 12.4839 | 9.2473 | 9.713 | 12.435 | 9.211 | 9.9433 | 12.7292 | 9.4292
FN | 3MO1_Mossman No 1 66 kV | Power Factor | 0.94894 | 0.97287 | 0.94291 | 0.94952 | 0.97111 | 0.94351 | 0.95019 | 0.97164 | 0.94415 | 0.94968 | 0.97129 | 0.94361 | 0.95306 | 0.97364 | 0.94711
FN | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN | 3MO1_Mossman No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
FN | 3MO1_Mossman No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0348 | 1.0321 | 1.0336 | 1.0342 | 1.0459 | 1.0332 | 1.0333 | 1.0445 | 1.0326 | 1.0335 | 1.0448 | 1.0328 | 1.0302 | 1.041 | 1.0302
FN | 3MO2_Mossman No 2 66 kV | % of Rated A | 56.31% | 49.35% | 39.11% | 56.52% | 49% | 39.24% | 56.73% | 49.22% | 39.38% | 56.54% | 49.04% | 39.25% | 57.77% | 50.2% | 40.07%
FN | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1)
FN | 3MO2_Mossman No 2 66 kV | Loading (A) | 95.1675 | 117.9466 | 91.1228 | 95.5104 | 117.1011 | 91.4378 | 95.8793 | 117.6352 | 91.7643 | 95.5548 | 117.207 | 91.4616 | 97.6321 | 119.9726 | 93.3674
FN | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 11.3087 | 14.0159 | 10.8108 | 11.344 | 14.0977 | 10.8441 | 11.3781 | 14.1432 | 10.8769 | 11.3418 | 14.0948 | 10.8427 | 11.5544 | 14.3808 | 11.0435
FN | 3MO2_Mossman No 2 66 kV | Loading (MW) | 10.7457 | 13.6932 | 10.1943 | 10.7866 | 13.7456 | 10.2331 | 10.8275 | 13.7981 | 10.2719 | 10.7866 | 13.7456 | 10.2331 | 11.0321 | 14.0603 | 10.4659
FN | 3MO2_Mossman No 2 66 kV | Power Factor | 0.95022 | 0.97696 | 0.94298 | 0.95087 | 0.97501 | 0.94366 | 0.95161 | 0.97558 | 0.94438 | 0.95105 | 0.97521 | 0.94377 | 0.9548 | 0.9777 | 0.94769
FN | 3MO2_Mossman No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
FN | 3MO2_Mossman No 2 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
FN | 3MO2_Mossman No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0394 | 1.0394 | 1.0378 | 1.0389 | 1.053 | 1.0374 | 1.038 | 1.0516 | 1.0368 | 1.0383 | 1.0519 | 1.037 | 1.0352 | 1.0485 | 1.0346
FN | 3MTG_Mt Garnet 66 kV | % of Rated A | 14.56% | 7.883% | 6.336% | 14.56% | 7.888% | 6.338% | 14.57% | 7.901% | 6.34% | 14.57% | 7.9% | 6.339% | 14.58% | 7.927% | 6.351%
FN | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1
FN | 3MTG_Mt Garnet 66 kV | Loading (A) | 24.6001 | 18.9972 | 14.889 | 24.6076 | 19.0096 | 14.8933 | 24.6219 | 19.0418 | 14.8995 | 24.6183 | 19.0391 | 14.8978 | 24.636 | 19.1037 | 14.9257
FN | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 2.8407 | 2.2198 | 1.748 | 2.8407 | 2.2198 | 1.7477 | 2.8408 | 2.2199 | 1.7474 | 2.8408 | 2.2199 | 1.7475 | 2.8408 | 2.22 | 1.7459
FN | 3MTG_Mt Garnet 66 kV | Loading (MW) | 2.7334 | 2.1529 | 1.6716 | 2.7334 | 2.1529 | 1.6716 | 2.7334 | 2.153 | 1.6716 | 2.7334 | 2.153 | 1.6716 | 2.7334 | 2.153 | 1.6717
FN | 3MTG_Mt Garnet 66 kV | Power Factor | 0.96085 | 0.96886 | 0.95629 | 0.96085 | 0.96884 | 0.95643 | 0.96084 | 0.96882 | 0.95663 | 0.96084 | 0.96882 | 0.95657 | 0.96083 | 0.96876 | 0.95746
FN | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 3MTG_Mt Garnet 66 kV | Time | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00 | 15:00:00 | 17:00:00 | 22:00:00
FN | 3MTG_Mt Garnet 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0102 | 1.0222 | 1.026 | 1.0099 | 1.0215 | 1.0256 | 1.0093 | 1.0198 | 1.0249 | 1.0094 | 1.02 | 1.0251 | 1.0087 | 1.0166 | 1.0223
FN | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 9.198% | 8.214% | 7.107% | 9.202% | 8.107% | 7.11% | 9.211% | 8.115% | 7.114% | 9.209% | 8.113% | 7.113% | 9.24% | 8.144% | 7.132%
FN | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 15.5439 | 19.7946 | 16.7018 | 15.552 | 19.5367 | 16.7088 | 15.5661 | 19.5583 | 16.7187 | 15.563 | 19.5529 | 16.716 | 15.6152 | 19.6261 | 16.7609
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 1.8175 | 2.3041 | 1.952 | 1.8175 | 2.3046 | 1.952 | 1.8174 | 2.3045 | 1.9519 | 1.8174 | 2.3045 | 1.9519 | 1.8172 | 2.3044 | 1.9518
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 1.8076 | 2.3003 | 1.9442 | 1.8076 | 2.3002 | 1.9442 | 1.8076 | 2.3002 | 1.9442 | 1.8076 | 2.3002 | 1.9442 | 1.8076 | 2.3002 | 1.9442
FN | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.99453 | 0.99838 | 0.99599 | 0.99456 | 0.9981 | 0.99601 | 0.9946 | 0.99812 | 0.99603 | 0.99459 | 0.99812 | 0.99602 | 0.99474 | 0.9982 | 0.99612
FN | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 3RA1_Ravenshoe No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
FN | 3RA1_Ravenshoe No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0229 | 1.0182 | 1.0224 | 1.0223 | 1.0319 | 1.0219 | 1.0213 | 1.0307 | 1.0213 | 1.0215 | 1.031 | 1.0215 | 1.018 | 1.0271 | 1.0187
FN | 7200_Craiglie No 2 132 kV | % of Rated A | 16.85% | 16.67% | 15.08% | 16.97% | 16.81% | 15.17% | 17.17% | 17.01% | 15.33% | 17.09% | 16.92% | 15.27% | 17.36% | 17.2% | 15.47%
FN | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN | 7200_Craiglie No 2 132 kV | Loading (A) | 76.1509 | 79.3684 | 64.3943 | 76.688 | 80.0134 | 64.7942 | 77.5912 | 80.9867 | 65.4771 | 77.244 | 80.5624 | 65.2156 | 78.4525 | 81.889 | 66.0572
FN | 7200_Craiglie No 2 132 kV | Loading (MVA) | 18.1063 | 18.9174 | 15.4737 | 18.2258 | 19.0554 | 15.5645 | 18.4253 | 19.2893 | 15.7203 | 18.3462 | 19.1966 | 15.6599 | 18.5833 | 19.4508 | 15.8296
FN | 7200_Craiglie No 2 132 kV | Loading (MW) | 16.8567 | 17.7753 | 13.5221 | 16.9886 | 17.9295 | 13.6294 | 17.2227 | 18.188 | 13.8149 | 17.132 | 18.0848 | 13.7399 | 17.4293 | 18.3967 | 13.9737
FN | 7200_Craiglie No 2 132 kV | Power Factor | 0.93099 | 0.93962 | 0.87387 | 0.93212 | 0.94092 | 0.87568 | 0.93473 | 0.94291 | 0.87879 | 0.93382 | 0.94208 | 0.8774 | 0.9379 | 0.94581 | 0.88276
FN | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 7200_Craiglie No 2 132 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
FN | 7200_Craiglie No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0399 | 1.0424 | 1.051 | 1.0394 | 1.0415 | 1.0507 | 1.0385 | 1.0416 | 1.0501 | 1.0387 | 1.042 | 1.0503 | 1.0359 | 1.0387 | 1.0481
FN | 7201_Craiglie No 1 132 kV | % of Rated A | 16.76% | 16.59% | 15.01% | 16.88% | 16.73% | 15.11% | 17.08% | 16.93% | 15.27% | 17% | 16.84% | 15.21% | 17.27% | 17.12% | 15.4%
FN | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
FN | 7201_Craiglie No 1 132 kV | Loading (A) | 75.7677 | 78.9805 | 64.1088 | 76.3045 | 79.6251 | 64.5085 | 77.2049 | 80.5956 | 65.1895 | 76.858 | 80.1722 | 64.9283 | 78.0559 | 81.4875 | 65.762
FN | 7201_Craiglie No 1 132 kV | Loading (MVA) | 18.0152 | 18.825 | 15.4051 | 18.1346 | 18.9629 | 15.4958 | 18.3336 | 19.1962 | 15.6513 | 18.2545 | 19.1037 | 15.5909 | 18.4893 | 19.3554 | 15.7588
FN | 7201_Craiglie No 1 132 kV | Loading (MW) | 16.7571 | 17.675 | 13.4444 | 16.8891 | 17.8293 | 13.5518 | 17.1228 | 18.0874 | 13.737 | 17.032 | 17.9842 | 13.662 | 17.3271 | 18.2938 | 13.894
FN | 7201_Craiglie No 1 132 kV | Power Factor | 0.93017 | 0.93891 | 0.87272 | 0.93132 | 0.94022 | 0.87455 | 0.93396 | 0.94224 | 0.87769 | 0.93303 | 0.9414 | 0.87628 | 0.93714 | 0.94515 | 0.88166
FN | 7201_Craiglie No 1 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 7201_Craiglie No 1 132 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
FN | 7201_Craiglie No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.04 | 1.0425 | 1.051 | 1.0395 | 1.0416 | 1.0507 | 1.0386 | 1.0418 | 1.0501 | 1.0388 | 1.0422 | 1.0503 | 1.036 | 1.0389 | 1.0481
FN | 7285_4LAK (Lakeland) 132kV | % of Rated A | 8.74% | 8.403% | 8.683% | 8.9% | 8.581% | 8.799% | 9.099% | 8.803% | 8.965% | 9.049% | 8.747% | 8.93% | 9.095% | 8.8% | 8.956%
FN | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN | 7285_4LAK (Lakeland) 132kV | Loading (A) | 44.398 | 45.7115 | 41.6804 | 45.2118 | 46.6806 | 42.2356 | 46.2241 | 47.8862 | 43.0308 | 45.969 | 47.5857 | 42.863 | 46.2011 | 47.8736 | 42.9903
FN | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 10.5296 | 10.8608 | 10.0174 | 10.7169 | 11.0807 | 10.1467 | 10.9458 | 11.3662 | 10.3312 | 10.8881 | 11.3006 | 10.293 | 10.9105 | 11.3293 | 10.3005
FN | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 7.4831 | 8.0492 | 5.9959 | 7.7418 | 8.3512 | 6.2075 | 8.1005 | 8.7582 | 6.4948 | 8.0108 | 8.6562 | 6.4226 | 8.1014 | 8.7593 | 6.4952
FN | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.71067 | 0.74112 | 0.59855 | 0.7224 | 0.75367 | 0.61178 | 0.74006 | 0.77055 | 0.62866 | 0.73574 | 0.766 | 0.62398 | 0.74254 | 0.77316 | 0.63057
FN | 7285_4LAK (Lakeland) 132kV | Rating (A) | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480
FN | 7285_4LAK (Lakeland) 132kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
FN | 7285_4LAK (Lakeland) 132kV | Min Voltage at Constrained Conductor (pu) | 1.0373 | 1.0392 | 1.0512 | 1.0368 | 1.0382 | 1.0508 | 1.0357 | 1.0382 | 1.0501 | 1.036 | 1.0387 | 1.0503 | 1.0329 | 1.0351 | 1.048
FN | MOSS_7496 | % of Rated A | 18.27% | 19.96% | 17.39% | 18.28% | 19.97% | 17.39% | 18.35% | 20.02% | 17.45% | 18.25% | 19.91% | 17.36% | 18.62% | 20.31% | 17.68%
FN | MOSS_7496 | Limiting Line Name | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a
FN | MOSS_7496 | Loading (A) | 69.2309 | 73.8355 | 55.9836 | 69.2671 | 73.904 | 56.0055 | 69.5465 | 74.0735 | 56.1993 | 69.1769 | 73.6781 | 55.8915 | 70.5833 | 75.1476 | 56.923
FN | MOSS_7496 | Loading (MVA) | 16.413 | 17.5366 | 13.4497 | 16.4129 | 17.5365 | 13.4495 | 16.4626 | 17.5758 | 13.4876 | 16.3791 | 17.4909 | 13.4164 | 16.6625 | 17.7776 | 13.6334
FN | MOSS_7496 | Loading (MW) | 16.408 | 17.5335 | 13.4233 | 16.4079 | 17.5335 | 13.4232 | 16.458 | 17.5728 | 13.462 | 16.3744 | 17.4879 | 13.3903 | 16.6591 | 17.7755 | 13.6096
FN | MOSS_7496 | Power Factor | 0.99969 | 0.99982 | 0.99803 | 0.9997 | 0.99983 | 0.99804 | 0.99972 | 0.99983 | 0.9981 | 0.99971 | 0.99983 | 0.99806 | 0.9998 | 0.99988 | 0.99825
FN | MOSS_7496 | Rating (A) | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322
FN | MOSS_7496 | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
FN | MOSS_7496 | Min Voltage at Constrained Conductor (pu) | 1.0366 | 1.0385 | 1.0505 | 1.036 | 1.0375 | 1.0501 | 1.035 | 1.0374 | 1.0494 | 1.0353 | 1.038 | 1.0496 | 1.0322 | 1.0343 | 1.0473
MK | 231_Carmila 33 kV | % of Rated A | 25.46% | 36.64% | 31.15% | 25.46% | 36.64% | 31.15% | 25.48% | 36.68% | 31.18% | 25.48% | 36.68% | 31.18% | 25.48% | 36.68% | 31.18%
MK | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1
MK | 231_Carmila 33 kV | Loading (A) | 38.7061 | 55.6878 | 47.3487 | 38.7061 | 55.6878 | 47.3487 | 38.737 | 55.7514 | 47.3893 | 38.737 | 55.7514 | 47.3893 | 38.737 | 55.7514 | 47.3893
MK | 231_Carmila 33 kV | Loading (MVA) | 2.1967 | 3.1283 | 2.7033 | 2.1967 | 3.1283 | 2.7033 | 2.1968 | 3.1287 | 2.7035 | 2.1968 | 3.1287 | 2.7035 | 2.1968 | 3.1287 | 2.7035
MK | 231_Carmila 33 kV | Loading (MW) | 2.1307 | 3.0316 | 2.6246 | 2.1307 | 3.0316 | 2.6246 | 2.1308 | 3.0319 | 2.6247 | 2.1308 | 3.0319 | 2.6247 | 2.1308 | 3.0319 | 2.6247
MK | 231_Carmila 33 kV | Power Factor | 0.96986 | 0.96901 | 0.97081 | 0.96986 | 0.96901 | 0.97081 | 0.96982 | 0.96896 | 0.97077 | 0.96982 | 0.96896 | 0.97077 | 0.96982 | 0.96896 | 0.97077
MK | 231_Carmila 33 kV | Rating (A) | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152
MK | 231_Carmila 33 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
MK | 231_Carmila 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99258 | 0.98282 | 0.99886 | 0.99258 | 0.98282 | 0.99886 | 0.99184 | 0.98181 | 0.99809 | 0.99184 | 0.98181 | 0.99809 | 0.99184 | 0.98181 | 0.99809
MK | 3045_Sarina No 1 33 kV | % of Rated A | 36.64% | 44.68% | 36.5% | 36.64% | 44.68% | 36.5% | 36.67% | 44.73% | 36.53% | 25.72% | 31.37% | 30.1% | 25.86% | 31.73% | 30.43%
MK | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1 | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1 | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1 | TR_LINE 12173_1 | TR_LINE 113451_1 | TR_LINE 11547_1 | TR_LINE 12173_1 | TR_LINE 113451_1 | TR_LINE 11547_1
MK | 3045_Sarina No 1 33 kV | Loading (A) | 138.5163 | 279.2583 | 228.1334 | 138.5163 | 279.2583 | 228.1334 | 138.6178 | 279.5494 | 228.3086 | 76.8968 | 127.9991 | 91.8112 | 77.3248 | 129.4592 | 92.8075
MK | 3045_Sarina No 1 33 kV | Loading (MVA) | 8.0355 | 16.7809 | 13.7339 | 8.0355 | 16.7809 | 13.7339 | 8.0357 | 16.7838 | 13.735 | 4.6032 | 7.7203 | 5.485 | 4.6265 | 7.8069 | 5.5382
MK | 3045_Sarina No 1 33 kV | Loading (MW) | 7.434 | 16.5958 | 13.6914 | 7.434 | 16.5958 | 13.6914 | 7.434 | 16.5969 | 13.6919 | 3.3748 | 7.5313 | 4.805 | 3.4335 | 7.6333 | 4.8893
MK | 3045_Sarina No 1 33 kV | Power Factor | 0.92515 | 0.98889 | 0.99686 | 0.92515 | 0.98889 | 0.99686 | 0.92512 | 0.98879 | 0.99681 | 0.73301 | 0.97494 | 0.87587 | 0.74201 | 0.9772 | 0.88269
MK | 3045_Sarina No 1 33 kV | Rating (A) | 378 | 625 | 625 | 378 | 625 | 625 | 378 | 625 | 625 | 299 | 408 | 305 | 299 | 408 | 305
MK | 3045_Sarina No 1 33 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
MK | 3045_Sarina No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0148 | 1.0513 | 1.0532 | 1.0148 | 1.0513 | 1.0532 | 1.0141 | 1.0504 | 1.0525 | 1.0473 | 1.0538 | 1.0452 | 1.0468 | 1.0535 | 1.044
MK | 3046_Rosella 33 kV | % of Rated A | 10.1% | 12.48% | 10.53% | 10.1% | 12.48% | 10.53% | 21.03% | 26.15% | 21.95% | 21.22% | 26.01% | 21.87% | 21.95% | 26.92% | 22.61%
MK | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1
MK | 3046_Rosella 33 kV | Loading (A) | 41.2952 | 51.0627 | 43.06 | 41.2952 | 51.0627 | 43.06 | 86.0174 | 106.9579 | 89.7932 | 86.7863 | 106.3895 | 89.4458 | 89.7729 | 110.1035 | 92.4643
MK | 3046_Rosella 33 kV | Loading (MVA) | 2.465 | 3.0346 | 2.5684 | 2.465 | 3.0346 | 2.5684 | 5.0776 | 6.2664 | 5.2936 | 5.0795 | 6.2694 | 5.2959 | 5.2501 | 6.4815 | 5.4704
MK | 3046_Rosella 33 kV | Loading (MW) | 2.3832 | 2.9282 | 2.4823 | 2.3832 | 2.9282 | 2.4823 | 4.8649 | 5.98 | 5.0677 | 4.8652 | 5.9804 | 5.068 | 5.0254 | 6.1776 | 5.2344
MK | 3046_Rosella 33 kV | Power Factor | 0.96673 | 0.96484 | 0.96639 | 0.96673 | 0.96484 | 0.96639 | 0.95804 | 0.95424 | 0.95726 | 0.95774 | 0.95385 | 0.9569 | 0.95712 | 0.95304 | 0.95679
MK | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409
MK | 3046_Rosella 33 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
MK | 3046_Rosella 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0443 | 1.0397 | 1.0435 | 1.0443 | 1.0397 | 1.0435 | 1.0328 | 1.025 | 1.0314 | 1.024 | 1.031 | 1.0359 | 1.0232 | 1.0299 | 1.0351
MK | 3047_Sarina No 2 33 kV | % of Rated A | 39.18% | 44.48% | 34.79% | 39.18% | 44.48% | 34.79% | 39.21% | 44.52% | 34.82% | 0.1917% | 0.1938% | 0.1939% | 0.1917% | 0.1938% | 0.1939%
MK | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_CABLE 6963_1 | TR_CABLE 6963_1 | TR_CABLE 6963_1 | TR_CABLE 6963_1 | TR_CABLE 6963_1 | TR_CABLE 6963_1
MK | 3047_Sarina No 2 33 kV | Loading (A) | 148.893 | 185.9096 | 146.1034 | 148.893 | 185.9096 | 146.1034 | 149.0092 | 186.107 | 146.2244 | 1.3231 | 1.3374 | 1.3376 | 1.323 | 1.3373 | 1.3376
MK | 3047_Sarina No 2 33 kV | Loading (MVA) | 8.688 | 10.7306 | 8.53 | 8.688 | 10.7306 | 8.53 | 8.6887 | 10.7317 | 8.5308 | 0.079096 | 0.080825 | 0.08084 | 0.079091 | 0.080812 | 0.080842
MK | 3047_Sarina No 2 33 kV | Loading (MW) | 8.2939 | 10.1936 | 8.1741 | 8.2939 | 10.1936 | 8.1741 | 8.2941 | 10.1941 | 8.1744 | 0.00049908 | 0.00050999 | 0.00051009 | 0.00049906 | 0.00050992 | 0.0005101
MK | 3047_Sarina No 2 33 kV | Power Factor | 0.95464 | 0.94996 | 0.95827 | 0.95464 | 0.94996 | 0.95827 | 0.95459 | 0.9499 | 0.95822 | 4.983e-05 | 4.9831e-05 | 4.9813e-05 | 4.9811e-05 | 4.9844e-05 | 4.9831e-05
MK | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 690 | 690 | 690 | 690 | 690 | 690
MK | 3047_Sarina No 2 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 11:30:00 | 17:00:00 | 00:00:00 | 11:30:00 | 17:00:00 | 00:30:00
MK | 3047_Sarina No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0199 | 1.0086 | 1.0205 | 1.0199 | 1.0086 | 1.0205 | 1.0192 | 1.0077 | 1.0198 | 1.0459 | 1.0573 | 1.0574 | 1.0459 | 1.0572 | 1.0574
MK | 3053_Mt Bassett 33 kV | % of Rated A | 31.49% | 26.2% | 20.44% | 31.45% | 26.18% | 20.43% | 31.38% | 26.11% | 20.39% | 31.77% | 26.06% | 20.36% | 32.13% | 26.75% | 20.87%
MK | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK | 3053_Mt Bassett 33 kV | Loading (A) | 73.9984 | 85.1428 | 66.0335 | 73.918 | 85.0709 | 65.9805 | 73.75 | 84.8552 | 65.8452 | 74.6542 | 84.7045 | 65.7573 | 75.5052 | 86.9404 | 67.4073
MK | 3053_Mt Bassett 33 kV | Loading (MVA) | 4.4366 | 5.0567 | 3.9529 | 4.4321 | 5.0524 | 3.9498 | 4.4286 | 5.0489 | 3.9472 | 4.4277 | 5.0468 | 3.9458 | 4.5279 | 5.1636 | 4.0365
MK | 3053_Mt Bassett 33 kV | Loading (MW) | 4.3165 | 4.9145 | 3.8614 | 4.3125 | 4.9107 | 3.8586 | 4.3095 | 4.9078 | 3.8564 | 4.307 | 4.9062 | 3.8552 | 4.4046 | 5.0171 | 3.9423
MK | 3053_Mt Bassett 33 kV | Power Factor | 0.97293 | 0.97188 | 0.97686 | 0.97301 | 0.97195 | 0.97691 | 0.97313 | 0.97207 | 0.977 | 0.97273 | 0.97215 | 0.97704 | 0.97276 | 0.97163 | 0.97666
MK | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323
MK | 3053_Mt Bassett 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 3053_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0458 | 1.0353 | 1.0447 | 1.0459 | 1.0353 | 1.0447 | 1.0475 | 1.0373 | 1.0462 | 1.0345 | 1.0387 | 1.0472 | 1.046 | 1.0353 | 1.045
MK | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.255% | 1.646% | 1.703% | 2.255% | 1.646% | 1.704% | 2.257% | 1.649% | 1.704% | 2.26% | 1.651% | 1.703% | 2.255% | 1.645% | 1.702%
MK | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1
MK | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.8778 | 3.7031 | 3.7817 | 3.8783 | 3.7031 | 3.7818 | 3.8819 | 3.7099 | 3.783 | 3.8868 | 3.7138 | 3.7814 | 3.8784 | 3.7012 | 3.778
MK | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.23078 | 0.21397 | 0.22315 | 0.23084 | 0.21398 | 0.22316 | 0.23127 | 0.21475 | 0.2233 | 0.23186 | 0.2152 | 0.22312 | 0.23085 | 0.21375 | 0.22271
MK | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0042403 | 0.0039772 | 0.0041479 | 0.0042414 | 0.0039773 | 0.004148 | 0.0042492 | 0.0039918 | 0.0041507 | 0.00426 | 0.0040002 | 0.0041473 | 0.0042415 | 0.0039732 | 0.0041397
MK | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588
MK | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222
MK | 340_MK3-1 Farleigh 33 kV | Time | 11:00:00 | 21:30:00 | 01:30:00 | 11:00:00 | 21:30:00 | 01:30:00 | 11:00:00 | 21:30:00 | 01:00:00 | 11:00:00 | 21:30:00 | 05:30:00 | 11:00:00 | 21:30:00 | 01:00:00
MK | 340_MK3-1 Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0412 | 1.0109 | 1.0324 | 1.0414 | 1.0109 | 1.0324 | 1.0423 | 1.0128 | 1.0327 | 1.0436 | 1.0138 | 1.0323 | 1.0414 | 1.0104 | 1.0313
MK | 341_Tennyson St No 2 33 kV | % of Rated A | 60.85% | 62.02% | 45.15% | 60.5% | 61.68% | 44.92% | 60.14% | 61.3% | 44.67% | 60.76% | 61.06% | 44.53% | 61.27% | 62.5% | 45.49%
MK | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 253_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 253_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 253_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 253_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 253_1
MK | 341_Tennyson St No 2 33 kV | Loading (A) | 212.9759 | 217.082 | 158.0338 | 211.7429 | 215.883 | 157.2063 | 210.4783 | 214.5655 | 156.3417 | 212.6697 | 213.7252 | 155.84 | 214.4581 | 218.7367 | 159.2208
MK | 341_Tennyson St No 2 33 kV | Loading (MVA) | 12.8163 | 12.9714 | 9.514 | 12.7437 | 12.9006 | 9.4642 | 12.6867 | 12.8448 | 9.4253 | 12.6609 | 12.8122 | 9.4041 | 12.9095 | 13.0736 | 9.5898
MK | 341_Tennyson St No 2 33 kV | Loading (MW) | 12.8052 | 12.9585 | 9.4958 | 12.7334 | 12.8886 | 9.4452 | 12.6774 | 12.8339 | 9.4049 | 12.649 | 12.8019 | 9.3833 | 12.8977 | 13.0599 | 9.5725
MK | 341_Tennyson St No 2 33 kV | Power Factor | 0.99693 | 0.99678 | 0.9981 | 0.99703 | 0.99687 | 0.99799 | 0.99714 | 0.99699 | 0.99784 | 0.99682 | 0.99708 | 0.99778 | 0.99687 | 0.9967 | 0.9982
MK | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
MK | 341_Tennyson St No 2 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
MK | 341_Tennyson St No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0453 | 1.0525 | 1.0528 | 1.0453 | 1.0525 | 1.0544 | 1.0472 | 1.054 | 1.0415 | 1.0486 | 1.055 | 1.053 | 1.0456 | 1.053
MK | 342_South Mackay 33 kV | % of Rated A | 90.8% | 53.67% | 50.09% | 90.14% | 53.36% | 49.81% | 84.84% | 48.1% | 45.62% | 86.19% | 48.81% | 46.35% | 85.51% | 48.41% | 45.88%
MK | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1
MK | 342_South Mackay 33 kV | Loading (A) | 424.9443 | 340.8206 | 318.0402 | 421.8663 | 338.8262 | 316.2803 | 397.0475 | 305.4469 | 289.6623 | 403.3597 | 309.9142 | 294.3269 | 400.1885 | 307.4117 | 291.316
MK | 342_South Mackay 33 kV | Loading (MVA) | 25.6343 | 20.4908 | 19.2075 | 25.4528 | 20.3743 | 19.1039 | 23.9843 | 18.4462 | 17.556 | 24.0805 | 18.7603 | 17.8714 | 24.1556 | 18.5377 | 17.6445
MK | 342_South Mackay 33 kV | Loading (MW) | 24.624 | 18.5101 | 16.8588 | 24.4176 | 18.3689 | 16.7287 | 22.6898 | 15.7335 | 14.5024 | 22.5251 | 15.6102 | 14.3889 | 22.8961 | 15.8748 | 14.6326
MK | 342_South Mackay 33 kV | Power Factor | 0.96046 | 0.90334 | 0.87772 | 0.9592 | 0.90157 | 0.87567 | 0.94589 | 0.85294 | 0.82607 | 0.93525 | 0.83209 | 0.80513 | 0.94772 | 0.85636 | 0.8293
MK | 342_South Mackay 33 kV | Rating (A) | 468 | 635 | 635 | 468 | 635 | 635 | 468 | 635 | 635 | 468 | 635 | 635 | 468 | 635 | 635
MK | 342_South Mackay 33 kV | Time | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00
MK | 342_South Mackay 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0553 | 1.0518 | 1.0566 | 1.0555 | 1.052 | 1.0567 | 1.0568 | 1.0565 | 1.0604 | 1.0444 | 1.0591 | 1.0623 | 1.056 | 1.055 | 1.0597
MK | 343_Pleystowe 33 kV | % of Rated A | 44.63% | 62.26% | 41.86% | 44.63% | 62.26% | 41.86% | 44.22% | 61.66% | 41.47% | 44.82% | 61.58% | 41.43% | 45.33% | 63.27% | 42.48%
MK | 343_Pleystowe 33 kV | Limiting Line Name | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1
MK | 343_Pleystowe 33 kV | Loading (A) | 98.1839 | 136.972 | 92.0867 | 98.1758 | 136.9723 | 92.0858 | 97.2921 | 135.6508 | 91.2435 | 98.597 | 135.4709 | 91.148 | 99.7317 | 139.1905 | 93.4502
MK | 343_Pleystowe 33 kV | Loading (MVA) | 5.7837 | 7.9114 | 5.421 | 5.7837 | 7.9114 | 5.421 | 5.7415 | 7.8526 | 5.3803 | 5.7439 | 7.8534 | 5.3801 | 5.8743 | 8.0356 | 5.5017
MK | 343_Pleystowe 33 kV | Loading (MW) | 5.7578 | 7.8549 | 5.3997 | 5.7578 | 7.8549 | 5.3997 | 5.7161 | 7.7972 | 5.3594 | 5.7174 | 7.7975 | 5.3593 | 5.8469 | 7.9758 | 5.4791
MK | 343_Pleystowe 33 kV | Power Factor | 0.99547 | 0.99279 | 0.99601 | 0.99547 | 0.99279 | 0.99601 | 0.99552 | 0.99286 | 0.99606 | 0.99533 | 0.99281 | 0.99607 | 0.99527 | 0.9925 | 0.99584
MK | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
MK | 343_Pleystowe 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 343_Pleystowe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0306 | 1.0105 | 1.0299 | 1.0307 | 1.0105 | 1.0299 | 1.0325 | 1.0128 | 1.0316 | 1.0192 | 1.0142 | 1.0327 | 1.0305 | 1.01 | 1.03
MK | 344_West Mackay 2 33 kV | % of Rated A | 25.41% | 26.38% | 19.65% | 25.41% | 26.38% | 19.65% | 25.38% | 26.34% | 19.62% | 25.56% | 26.16% | 19.5% | 25.8% | 26.79% | 19.94%
MK | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK | 344_West Mackay 2 33 kV | Loading (A) | 158.8123 | 164.8957 | 122.7838 | 158.7999 | 164.8924 | 122.7827 | 158.6212 | 164.5993 | 122.6085 | 159.7361 | 163.5174 | 121.8521 | 161.2353 | 167.4217 | 124.6355
MK | 344_West Mackay 2 33 kV | Loading (MVA) | 9.5808 | 9.8785 | 7.3907 | 9.5808 | 9.8785 | 7.3907 | 9.5838 | 9.878 | 7.3905 | 9.5339 | 9.8262 | 7.352 | 9.7303 | 10.0328 | 7.5056
MK | 344_West Mackay 2 33 kV | Loading (MW) | 9.4181 | 9.7058 | 7.2813 | 9.4181 | 9.7058 | 7.2813 | 9.4187 | 9.7057 | 7.2812 | 9.3703 | 9.6556 | 7.2438 | 9.5634 | 9.8556 | 7.3936
MK | 344_West Mackay 2 33 kV | Power Factor | 0.98275 | 0.98225 | 0.98494 | 0.98275 | 0.98225 | 0.98494 | 0.98251 | 0.98229 | 0.98497 | 0.98257 | 0.98238 | 0.98502 | 0.98259 | 0.98207 | 0.98482
MK | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625
MK | 344_West Mackay 2 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
MK | 344_West Mackay 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0555 | 1.0481 | 1.0531 | 1.0555 | 1.0481 | 1.0531 | 1.0571 | 1.0499 | 1.0546 | 1.0442 | 1.0513 | 1.0556 | 1.0558 | 1.0484 | 1.0536
MK | 346_Ritchies Rd 33 kV | % of Rated A | 33.35% | 33.66% | 22.71% | 33.34% | 33.66% | 22.71% | 33.04% | 33.34% | 22.5% | 33.49% | 33.29% | 22.48% | 33.87% | 34.21% | 23.04%
MK | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1
MK | 346_Ritchies Rd 33 kV | Loading (A) | 73.3618 | 102.3275 | 68.8065 | 73.3557 | 102.3277 | 68.8058 | 72.6959 | 101.3413 | 68.1769 | 73.6703 | 101.2076 | 68.1056 | 74.5186 | 103.9852 | 69.8256
MK | 346_Ritchies Rd 33 kV | Loading (MVA) | 4.3222 | 5.9118 | 4.0512 | 4.3222 | 5.9118 | 4.0512 | 4.2907 | 5.868 | 4.0208 | 4.2925 | 5.8686 | 4.0206 | 4.39 | 6.0047 | 4.1115
MK | 346_Ritchies Rd 33 kV | Loading (MW) | 4.2982 | 5.8644 | 4.0308 | 4.2982 | 5.8644 | 4.0308 | 4.267 | 5.8212 | 4.0007 | 4.2681 | 5.8215 | 4.0006 | 4.3647 | 5.9547 | 4.0901
MK | 346_Ritchies Rd 33 kV | Power Factor | 0.99444 | 0.99198 | 0.99496 | 0.99444 | 0.99198 | 0.99496 | 0.99448 | 0.99204 | 0.995 | 0.99431 | 0.99198 | 0.99501 | 0.99424 | 0.99168 | 0.99479
MK | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 346_Ritchies Rd 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 346_Ritchies Rd 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0307 | 1.0107 | 1.0301 | 1.0308 | 1.0107 | 1.0301 | 1.0326 | 1.013 | 1.0318 | 1.0193 | 1.0144 | 1.0328 | 1.0306 | 1.0102 | 1.0301
MK | 347_Mt Bassett 33 kV | % of Rated A | 44.14% | 53.11% | 41.71% | 44.17% | 53.14% | 41.73% | 44.12% | 53.06% | 41.68% | 44.7% | 52.99% | 41.65% | 45.26% | 54.45% | 42.74%
MK | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK | 347_Mt Bassett 33 kV | Loading (A) | 112.5669 | 135.4357 | 106.3529 | 112.627 | 135.5026 | 106.4013 | 112.5097 | 135.2963 | 106.2855 | 113.9953 | 135.1337 | 106.1993 | 115.412 | 138.8454 | 108.9751
MK | 347_Mt Bassett 33 kV | Loading (MVA) | 6.7669 | 8.0704 | 6.3846 | 6.7711 | 8.0746 | 6.3876 | 6.774 | 8.0771 | 6.3896 | 6.7794 | 8.0784 | 6.3907 | 6.9399 | 8.2747 | 6.5447
MK | 347_Mt Bassett 33 kV | Loading (MW) | 6.7058 | 7.9801 | 6.3209 | 6.7098 | 7.9839 | 6.3237 | 6.7126 | 7.9864 | 6.3257 | 6.7169 | 7.9877 | 6.3268 | 6.8758 | 8.1798 | 6.4782
MK | 347_Mt Bassett 33 kV | Power Factor | 0.99089 | 0.98871 | 0.98993 | 0.99085 | 0.98868 | 0.9899 | 0.99083 | 0.98868 | 0.98989 | 0.99069 | 0.98869 | 0.9899 | 0.99066 | 0.98844 | 0.98974
MK | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
MK | 347_Mt Bassett 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 347_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0517 | 1.0425 | 1.0503 | 1.0518 | 1.0425 | 1.0503 | 1.0534 | 1.0445 | 1.0518 | 1.0405 | 1.0459 | 1.0528 | 1.052 | 1.0427 | 1.0507
MK | 348_Farleigh 33 kV | % of Rated A | 35.51% | 36.5% | 23.88% | 35.51% | 36.5% | 23.88% | 35.44% | 36.41% | 23.84% | 35.93% | 36.37% | 23.81% | 36.9% | 37.97% | 24.81%
MK | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1
MK | 348_Farleigh 33 kV | Loading (A) | 68.8899 | 94.8987 | 61.6071 | 68.884 | 94.8989 | 61.6065 | 68.7581 | 94.666 | 61.4993 | 69.7113 | 94.5602 | 61.433 | 71.5861 | 98.7132 | 63.9972
MK | 348_Farleigh 33 kV | Loading (MVA) | 4.0233 | 5.4133 | 3.5992 | 4.0233 | 5.4133 | 3.5992 | 4.023 | 5.4125 | 3.5989 | 4.0254 | 5.4142 | 3.5988 | 4.1788 | 5.6249 | 3.7379
MK | 348_Farleigh 33 kV | Loading (MW) | 4.0052 | 5.3667 | 3.5868 | 4.0052 | 5.3667 | 3.5868 | 4.005 | 5.3663 | 3.5866 | 4.0063 | 5.367 | 3.5866 | 4.1582 | 5.573 | 3.7236
MK | 348_Farleigh 33 kV | Power Factor | 0.9955 | 0.9914 | 0.99655 | 0.9955 | 0.9914 | 0.99655 | 0.99554 | 0.99147 | 0.99658 | 0.99524 | 0.99129 | 0.9966 | 0.99507 | 0.99077 | 0.99617
MK | 348_Farleigh 33 kV | Rating (A) | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258
MK | 348_Farleigh 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 348_Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0205 | 0.99616 | 1.021 | 1.0206 | 0.99616 | 1.021 | 1.0224 | 0.99847 | 1.0227 | 1.009 | 0.99992 | 1.0238 | 1.02 | 0.99503 | 1.0207
MK | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 44.38% | 41.6% | 29.22% | 44.38% | 41.61% | 29.23% | 44.36% | 41.59% | 29.21% | 44.36% | 41.56% | 29.2% | 45.34% | 42.57% | 29.85%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 97.6318 | 126.4621 | 88.5445 | 97.6433 | 126.4965 | 88.5574 | 97.5972 | 126.4388 | 88.5214 | 97.5864 | 126.35 | 88.4795 | 99.7504 | 129.4238 | 90.4445
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 11.7236 | 14.9307 | 10.6611 | 11.7237 | 14.9311 | 10.6612 | 11.7233 | 14.9305 | 10.6612 | 11.7249 | 14.9296 | 10.6608 | 11.9651 | 15.2468 | 10.8786
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 11.5324 | 14.582 | 10.5119 | 11.5324 | 14.5821 | 10.5119 | 11.5323 | 14.5819 | 10.5119 | 11.5326 | 14.5817 | 10.5119 | 11.7645 | 14.8818 | 10.7216
MK | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.98368 | 0.97664 | 0.986 | 0.98368 | 0.97663 | 0.98599 | 0.98371 | 0.97666 | 0.986 | 0.9836 | 0.9767 | 0.98603 | 0.98323 | 0.97606 | 0.98557
MK | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 349_Pioneer Valley - Pinnacle 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 349_Pioneer Valley - Pinnacle 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0504 | 1.0327 | 1.0532 | 1.0503 | 1.0325 | 1.0531 | 1.0507 | 1.0329 | 1.0535 | 1.051 | 1.0336 | 1.054 | 1.0493 | 1.0305 | 1.0521
MK | 351_Alligator Creek 33 kV | % of Rated A | 17.52% | 21.72% | 18.35% | 17.52% | 21.72% | 18.34% | 0.189% | 0.1364% | 0.1374% | 0.1884% | 0.1367% | 0.1375% | 0.1887% | 0.1367% | 0.1373%
MK | 351_Alligator Creek 33 kV | Limiting Line Name | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_LINE 66244_3 | TR_LINE 66244_3 | TR_LINE 66244_3 | TR_LINE 66244_3 | TR_LINE 66244_3 | TR_LINE 66244_3 | TR_LINE 66244_3 | TR_LINE 66244_3 | TR_LINE 66244_3
MK | 351_Alligator Creek 33 kV | Loading (A) | 41.0059 | 50.8203 | 42.9289 | 40.9972 | 50.8147 | 42.9241 | 0.48193 | 0.48139 | 0.48373 | 0.48051 | 0.48246 | 0.48387 | 0.48129 | 0.48247 | 0.48342
MK | 351_Alligator Creek 33 kV | Loading (MVA) | 2.4646 | 3.0343 | 2.5601 | 2.4646 | 3.0342 | 2.5601 | 0.029185 | 0.02912 | 0.029403 | 0.029013 | 0.029248 | 0.02942 | 0.029107 | 0.02925 | 0.029365
MK | 351_Alligator Creek 33 kV | Loading (MW) | 2.3832 | 2.9281 | 2.4744 | 2.3832 | 2.9281 | 2.4744 | 0.0054972 | 0.0054849 | 0.0055385 | 0.0054646 | 0.0055091 | 0.0055415 | 0.0054825 | 0.0055094 | 0.0055311
MK | 351_Alligator Creek 33 kV | Power Factor | 0.96684 | 0.96493 | 0.96642 | 0.96684 | 0.96493 | 0.96642 | 0.18836 | 0.18836 | 0.18837 | 0.18835 | 0.18836 | 0.18836 | 0.18836 | 0.18836 | 0.18836
MK | 351_Alligator Creek 33 kV | Rating (A) | 234 | 234 | 234 | 234 | 234 | 234 | 255 | 353 | 352 | 255 | 353 | 352 | 255 | 353 | 352
MK | 351_Alligator Creek 33 kV | Time | 16:30:00 | 19:00:00 | 22:30:00 | 16:30:00 | 19:00:00 | 22:30:00 | 16:30:00 | 19:30:00 | 01:00:00 | 14:30:00 | 19:30:00 | 00:30:00 | 16:30:00 | 20:00:00 | 01:00:00
MK | 351_Alligator Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0516 | 1.0446 | 1.0434 | 1.0518 | 1.0447 | 1.0435 | 1.0595 | 1.0583 | 1.0634 | 1.0564 | 1.0606 | 1.0638 | 1.0581 | 1.0607 | 1.0628
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 15.08% | 12.53% | 12.15% | 15.08% | 12.54% | 12.15% | 15.08% | 12.53% | 12.15% | 15.07% | 12.52% | 12.14% | 15.11% | 12.57% | 12.17%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 13.8763 | 14.9124 | 13.7324 | 13.8781 | 14.917 | 13.7347 | 13.8707 | 14.9093 | 13.7279 | 13.8665 | 14.8975 | 13.7205 | 13.8988 | 14.9588 | 13.7535
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 1.6372 | 1.7238 | 1.6261 | 1.6373 | 1.7239 | 1.6261 | 1.6371 | 1.7237 | 1.626 | 1.6371 | 1.7235 | 1.6259 | 1.6376 | 1.7246 | 1.6265
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 1.4964 | 1.5741 | 1.4866 | 1.4964 | 1.5741 | 1.4866 | 1.4964 | 1.5741 | 1.4866 | 1.4964 | 1.574 | 1.4865 | 1.4964 | 1.5741 | 1.4866
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.91394 | 0.91311 | 0.91418 | 0.91392 | 0.91308 | 0.91416 | 0.91399 | 0.91313 | 0.91422 | 0.91402 | 0.91323 | 0.91428 | 0.91374 | 0.91275 | 0.91399
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0321 | 1.0112 | 1.0358 | 1.032 | 1.0109 | 1.0357 | 1.0325 | 1.0114 | 1.0361 | 1.0328 | 1.0121 | 1.0366 | 1.0307 | 1.0085 | 1.0345
MK | 364_West Mackay No 1 33 kV | % of Rated A | 54.78% | 40.13% | 29.95% | 54.77% | 40.13% | 29.95% | 54.71% | 40.06% | 29.91% | 55.1% | 39.8% | 29.73% | 55.61% | 40.75% | 30.41%
MK | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK | 364_West Mackay No 1 33 kV | Loading (A) | 158.8587 | 164.9464 | 122.8109 | 158.8463 | 164.9431 | 122.8098 | 158.6676 | 164.6496 | 122.6354 | 159.7837 | 163.567 | 121.8787 | 161.2832 | 167.474 | 124.6635
MK | 364_West Mackay No 1 33 kV | Loading (MVA) | 9.5813 | 9.8791 | 7.391 | 9.5813 | 9.8791 | 7.391 | 9.5844 | 9.8786 | 7.3908 | 9.5345 | 9.8267 | 7.3523 | 9.7308 | 10.0334 | 7.5059
MK | 364_West Mackay No 1 33 kV | Loading (MW) | 9.4159 | 9.7035 | 7.2797 | 9.4159 | 9.7035 | 7.2797 | 9.4166 | 9.7034 | 7.2796 | 9.3681 | 9.6534 | 7.2421 | 9.5612 | 9.8533 | 7.3919
MK | 364_West Mackay No 1 33 kV | Power Factor | 0.98274 | 0.98223 | 0.98493 | 0.98274 | 0.98223 | 0.98493 | 0.98249 | 0.98227 | 0.98496 | 0.98255 | 0.98236 | 0.98501 | 0.98257 | 0.98205 | 0.98481
MK | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410
MK | 364_West Mackay No 1 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
MK | 364_West Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0552 | 1.0478 | 1.0529 | 1.0552 | 1.0478 | 1.0529 | 1.0568 | 1.0496 | 1.0543 | 1.0439 | 1.051 | 1.0554 | 1.0555 | 1.0481 | 1.0534
MK | 365_Tennyson St No 1 33 kV | % of Rated A | 8.039% | 8.193% | 5.963% | 7.992% | 8.148% | 5.932% | 7.945% | 8.098% | 5.899% | 8.027% | 8.067% | 5.88% | 8.094% | 8.255% | 6.008%
MK | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1
MK | 365_Tennyson St No 1 33 kV | Loading (A) | 53.4567 | 54.481 | 39.6559 | 53.1497 | 54.1824 | 39.4459 | 52.8354 | 53.8548 | 39.2259 | 53.3767 | 53.6461 | 39.099 | 53.8267 | 54.8939 | 39.9558
MK | 365_Tennyson St No 1 33 kV | Loading (MVA) | 3.2165 | 3.2551 | 2.3827 | 3.1983 | 3.2373 | 2.3702 | 3.1841 | 3.2234 | 2.3603 | 3.1774 | 3.2153 | 2.3549 | 3.2398 | 3.2806 | 2.4018
MK | 365_Tennyson St No 1 33 kV | Loading (MW) | 2.7508 | 2.7794 | 2.1234 | 2.7375 | 2.7665 | 2.1138 | 2.7281 | 2.7575 | 2.1071 | 2.7146 | 2.7525 | 2.103 | 2.769 | 2.7993 | 2.1389
MK | 365_Tennyson St No 1 33 kV | Power Factor | 0.85517 | 0.85384 | 0.89112 | 0.85588 | 0.85451 | 0.89181 | 0.85675 | 0.85542 | 0.89268 | 0.85431 | 0.85602 | 0.89298 | 0.85464 | 0.85324 | 0.8905
MK | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665
MK | 365_Tennyson St No 1 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
MK | 365_Tennyson St No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0453 | 1.0512 | 1.0528 | 1.0453 | 1.0512 | 1.0544 | 1.0472 | 1.0527 | 1.0415 | 1.0486 | 1.0537 | 1.053 | 1.0456 | 1.0517
MK | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.06525% | 0.04706% | 0.04724% | 0.06525% | 0.04705% | 0.04724% | 0.06528% | 0.04707% | 0.04725% | 0.06531% | 0.04709% | 0.04727% | 0.06525% | 0.04702% | 0.0472%
MK | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16443 | 0.16422 | 0.1644 | 0.16443 | 0.1642 | 0.16438 | 0.1645 | 0.16427 | 0.16444 | 0.16458 | 0.16435 | 0.16452 | 0.16442 | 0.16411 | 0.16426
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.019941 | 0.01989 | 0.019933 | 0.019941 | 0.019885 | 0.019928 | 0.019957 | 0.019903 | 0.019944 | 0.019977 | 0.01992 | 0.019961 | 0.019939 | 0.019863 | 0.019899
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.1175e-08 | 8.0969e-08 | 8.1111e-08 | 8.1218e-08 | 8.0978e-08 | 8.1161e-08 | 8.1274e-08 | 8.0992e-08 | 8.115e-08 | 8.1307e-08 | 8.111e-08 | 8.1228e-08 | 8.1165e-08 | 8.0908e-08 | 8.1091e-08
MK | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.0709e-06 | 4.0708e-06 | 4.0691e-06 | 4.0729e-06 | 4.0723e-06 | 4.0727e-06 | 4.0724e-06 | 4.0694e-06 | 4.0689e-06 | 4.0701e-06 | 4.0717e-06 | 4.0693e-06 | 4.0707e-06 | 4.0732e-06 | 4.0751e-06
MK | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348
MK | 367_Pioneer Valley - Greenmount 66 kV | Time | 14:00:00 | 21:30:00 | 22:00:00 | 14:00:00 | 21:30:00 | 22:00:00 | 14:00:00 | 21:30:00 | 22:00:00 | 14:30:00 | 21:30:00 | 22:00:00 | 14:00:00 | 21:30:00 | 22:00:00
MK | 367_Pioneer Valley - Greenmount 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0608 | 1.0595 | 1.0607 | 1.0609 | 1.0594 | 1.0605 | 1.0613 | 1.0598 | 1.0609 | 1.0618 | 1.0603 | 1.0614 | 1.0608 | 1.0588 | 1.0597
MK | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 13.43% | 12.8% | 9.544% | 13.43% | 12.8% | 9.545% | 13.42% | 12.8% | 9.542% | 13.42% | 12.79% | 9.537% | 13.76% | 13.13% | 9.782%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 26.1845 | 35.5841 | 25.7694 | 26.1873 | 35.5929 | 25.7728 | 26.1759 | 35.5781 | 25.7625 | 26.1693 | 35.5552 | 25.7512 | 26.8373 | 36.5128 | 26.4112
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 3.1579 | 4.2253 | 3.1138 | 3.1579 | 4.2253 | 3.1138 | 3.1579 | 4.2253 | 3.1137 | 3.1579 | 4.2252 | 3.1137 | 3.2334 | 4.3267 | 3.1883
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 3.1227 | 4.1725 | 3.0793 | 3.1227 | 4.1725 | 3.0793 | 3.1227 | 4.1725 | 3.0793 | 3.1227 | 4.1725 | 3.0792 | 3.1971 | 4.272 | 3.1527
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.98885 | 0.9875 | 0.98892 | 0.98885 | 0.9875 | 0.98892 | 0.98886 | 0.9875 | 0.98892 | 0.98886 | 0.98751 | 0.98892 | 0.98876 | 0.98736 | 0.98883
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.055 | 1.0387 | 1.057 | 1.0549 | 1.0385 | 1.0569 | 1.0553 | 1.0389 | 1.0573 | 1.0556 | 1.0395 | 1.0577 | 1.054 | 1.0366 | 1.056
MK | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 60.52% | 61.37% | 44.29% | 60.31% | 61.17% | 44.16% | 60.17% | 61.03% | 44.06% | 60.58% | 60.66% | 43.85% | 61.16% | 62.05% | 44.74%
MK | 387_Mackay-Alfred Street 1 33 kV | Limiting Line Name | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1
MK | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 260.8354 | 264.5205 | 190.9009 | 259.9405 | 263.6547 | 190.317 | 259.3365 | 263.032 | 189.9198 | 261.0996 | 261.4236 | 188.9783 | 263.6139 | 267.4326 | 192.8155
MK | 387_Mackay-Alfred Street 1 33 kV | Loading (MVA) | 15.7388 | 15.9004 | 11.4926 | 15.6859 | 15.849 | 11.4576 | 15.6721 | 15.8375 | 11.4496 | 15.587 | 15.7613 | 11.4038 | 15.9119 | 16.0813 | 11.6132
MK | 387_Mackay-Alfred Street 1 33 kV | Loading (MW) | 15.6686 | 15.8383 | 11.1648 | 15.614 | 15.7854 | 11.1263 | 15.5981 | 15.7718 | 11.1137 | 15.5241 | 15.6915 | 11.0612 | 15.8468 | 16.0242 | 11.295
MK | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 0.99554 | 0.9961 | 0.97147 | 0.99541 | 0.99598 | 0.97109 | 0.99528 | 0.99586 | 0.97066 | 0.99596 | 0.99557 | 0.96995 | 0.99591 | 0.99645 | 0.9726
MK | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431
MK | 387_Mackay-Alfred Street 1 33 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
MK | 387_Mackay-Alfred Street 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0537 | 1.0497 | 1.0521 | 1.0538 | 1.0497 | 1.0521 | 1.0553 | 1.0514 | 1.0535 | 1.0425 | 1.0528 | 1.0546 | 1.054 | 1.05 | 1.0525
MK | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 24.3% | 25.84% | 20.1% | 24.02% | 25.57% | 19.9% | 23.66% | 25.21% | 19.65% | 24.04% | 25.28% | 19.71% | 24.17% | 25.78% | 20.07%
MK | 395_Tennyson Street-Alfred Street 33 kV | Limiting Line Name | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1
MK | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 163.2709 | 173.6297 | 135.0456 | 161.4149 | 171.8342 | 133.7615 | 158.9969 | 169.4068 | 132.0786 | 161.5747 | 169.8715 | 132.478 | 162.4479 | 173.2126 | 134.8482
MK | 395_Tennyson Street-Alfred Street 33 kV | Loading (MVA) | 9.824 | 10.357 | 8.1142 | 9.7133 | 10.2501 | 8.0372 | 9.5818 | 10.1236 | 7.9473 | 9.6182 | 10.1651 | 7.9791 | 9.7776 | 10.3337 | 8.1059
MK | 395_Tennyson Street-Alfred Street 33 kV | Loading (MW) | 9.2964 | 9.8346 | 7.5603 | 9.1892 | 9.7312 | 7.4847 | 9.0612 | 9.6077 | 7.395 | 9.1082 | 9.6449 | 7.4217 | 9.2582 | 9.8183 | 7.5568
MK | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 0.94488 | 0.94814 | 0.93033 | 0.94463 | 0.94795 | 0.92984 | 0.94426 | 0.94762 | 0.9291 | 0.94556 | 0.9474 | 0.92872 | 0.94547 | 0.9487 | 0.93084
MK | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672
MK | 395_Tennyson Street-Alfred Street 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
MK | 395_Tennyson Street-Alfred Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0436 | 1.0512 | 1.0528 | 1.0436 | 1.0512 | 1.0544 | 1.0455 | 1.0527 | 1.0415 | 1.0469 | 1.0537 | 1.053 | 1.0438 | 1.0517
MK | 422_North Mackay No 1 33 kV | % of Rated A | 68.73% | 88.96% | 66.05% | 69.09% | 89.48% | 66.4% | 70.11% | 90.85% | 67.38% | 70.78% | 91.72% | 68.01% | 73.69% | 95.84% | 70.85%
MK | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2
MK | 422_North Mackay No 1 33 kV | Loading (A) | 252.2455 | 364.7497 | 264.2129 | 253.5735 | 366.8486 | 265.6149 | 257.2861 | 372.4876 | 269.5232 | 259.7537 | 376.035 | 272.0585 | 270.4444 | 392.9407 | 283.4028
MK | 422_North Mackay No 1 33 kV | Loading (MVA) | 14.8643 | 21.139 | 15.5287 | 14.9356 | 21.241 | 15.6032 | 15.1492 | 21.5464 | 15.8264 | 15.2917 | 21.7498 | 15.9752 | 15.8599 | 22.5615 | 16.5716
MK | 422_North Mackay No 1 33 kV | Loading (MW) | 14.8437 | 21.0815 | 15.5061 | 14.9147 | 21.1824 | 15.5802 | 15.1273 | 21.485 | 15.8024 | 15.2691 | 21.6866 | 15.9505 | 15.8356 | 22.4924 | 16.5435
MK | 422_North Mackay No 1 33 kV | Power Factor | 0.99861 | 0.99728 | 0.99854 | 0.9986 | 0.99724 | 0.99853 | 0.99856 | 0.99715 | 0.99848 | 0.99853 | 0.9971 | 0.99845 | 0.99847 | 0.99694 | 0.99831
MK | 422_North Mackay No 1 33 kV | Rating (A) | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400
MK | 422_North Mackay No 1 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 422_North Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0308 | 1.0137 | 1.0281 | 1.0304 | 1.0128 | 1.0276 | 1.03 | 1.0118 | 1.0272 | 1.0298 | 1.0117 | 1.0272 | 1.0259 | 1.0043 | 1.0229
MK | 423_North Mackay No 2 33 kV | % of Rated A | 29.89% | 39.42% | 30.05% | 30.08% | 39.7% | 30.24% | 30.35% | 40.09% | 30.51% | 30.44% | 40.21% | 30.6% | 31.32% | 41.54% | 31.49%
MK | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1
MK | 423_North Mackay No 2 33 kV | Loading (A) | 182.938 | 241.2703 | 183.9088 | 184.089 | 242.9697 | 185.0721 | 185.7425 | 245.3677 | 186.7427 | 186.2827 | 246.0671 | 187.2614 | 191.6602 | 254.2059 | 192.6994
MK | 423_North Mackay No 2 33 kV | Loading (MVA) | 10.9373 | 14.4212 | 10.9835 | 11.0031 | 14.5149 | 11.0497 | 11.1037 | 14.6572 | 11.1509 | 11.1376 | 14.7058 | 11.1855 | 11.432 | 15.1251 | 11.4815
MK | 423_North Mackay No 2 33 kV | Loading (MW) | 10.2888 | 14.0539 | 10.3438 | 10.3625 | 14.1546 | 10.4178 | 10.473 | 14.3057 | 10.5289 | 10.5098 | 14.356 | 10.5659 | 10.8414 | 14.8098 | 10.8993
MK | 423_North Mackay No 2 33 kV | Power Factor | 0.94071 | 0.97453 | 0.94175 | 0.94178 | 0.97518 | 0.94282 | 0.94319 | 0.97602 | 0.94422 | 0.94363 | 0.97622 | 0.9446 | 0.94834 | 0.97916 | 0.94929
MK | 423_North Mackay No 2 33 kV | Rating (A) | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
MK | 423_North Mackay No 2 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | 423_North Mackay No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.046 | 1.0457 | 1.0449 | 1.0457 | 1.0452 | 1.0445 | 1.0459 | 1.0451 | 1.0447 | 1.046 | 1.0456 | 1.045 | 1.0435 | 1.0409 | 1.0424
MK | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 43.79% | 44.4% | 32.05% | 43.64% | 44.26% | 31.95% | 43.53% | 44.15% | 31.89% | 43.83% | 43.88% | 31.73% | 44.25% | 44.89% | 32.37%
MK | 430_Mackay-Alfred Street 2 33 kV | Limiting Line Name | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1
MK | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 253.5161 | 257.0959 | 185.5864 | 252.6467 | 256.2547 | 185.0193 | 252.0601 | 255.65 | 184.6338 | 253.7715 | 254.0877 | 183.7196 | 256.2154 | 259.9249 | 187.4459
MK | 430_Mackay-Alfred Street 2 33 kV | Loading (MVA) | 15.2971 | 15.4541 | 11.1727 | 15.2458 | 15.4042 | 11.1386 | 15.2324 | 15.393 | 11.1309 | 15.1496 | 15.319 | 11.0865 | 15.4653 | 15.6299 | 11.2898
MK | 430_Mackay-Alfred Street 2 33 kV | Loading (MW) | 15.2275 | 15.3925 | 10.8506 | 15.1744 | 15.3411 | 10.8132 | 15.159 | 15.3279 | 10.801 | 15.0871 | 15.2498 | 10.7499 | 15.4007 | 15.5732 | 10.9771
MK | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 0.99545 | 0.99601 | 0.97117 | 0.99532 | 0.9959 | 0.97078 | 0.99519 | 0.99577 | 0.97036 | 0.99588 | 0.99548 | 0.96964 | 0.99582 | 0.99637 | 0.9723
MK | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579
MK | 430_Mackay-Alfred Street 2 33 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
MK | 430_Mackay-Alfred Street 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0555 | 1.0515 | 1.0532 | 1.0556 | 1.0516 | 1.0532 | 1.0571 | 1.0533 | 1.0547 | 1.0443 | 1.0547 | 1.0557 | 1.0559 | 1.0519 | 1.0537
MK | PV 6/4_Glenella No 2 66 kV | % of Rated A | 25.25% | 31.4% | 24.16% | 25.41% | 31.61% | 24.31% | 25.68% | 31.96% | 24.55% | 25.79% | 32.09% | 24.65% | 26.66% | 33.28% | 25.45%
MK | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105536_1 | TR_LINE 105543_1 | TR_LINE 105598_1 | TR_LINE 105536_1 | TR_LINE 105543_1 | TR_LINE 105446_1 | TR_LINE 105536_1 | TR_LINE 105543_1 | TR_LINE 105074_1 | TR_LINE 105536_1 | TR_LINE 105543_1 | TR_LINE 105525_3 | TR_LINE 105536_1 | TR_LINE 105543_1 | TR_LINE 105543_1
MK | PV 6/4_Glenella No 2 66 kV | Loading (A) | 204.2829 | 285.1249 | 215.2917 | 205.6012 | 287.0387 | 216.5891 | 207.7413 | 290.1807 | 218.7538 | 208.6218 | 291.413 | 219.6424 | 215.7088 | 302.178 | 226.778
MK | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 24.7234 | 33.4577 | 25.9083 | 24.8803 | 33.6668 | 26.0426 | 25.1501 | 34.0369 | 26.2805 | 25.2629 | 34.1978 | 26.3868 | 26.0834 | 35.329 | 27.1597
MK | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 24.6977 | 33.4319 | 25.9083 | 24.8569 | 33.6384 | 26.0426 | 25.1302 | 34.0035 | 26.2805 | 25.2445 | 34.1622 | 26.3868 | 26.0744 | 35.2783 | 27.1591
MK | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.99896 | 0.99923 | 1 | 0.99906 | 0.99915 | 1 | 0.99921 | 0.99902 | 1 | 0.99927 | 0.99896 | 1 | 0.99966 | 0.99856 | 0.99998
MK | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | PV 6/4_Glenella No 2 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
MK | PV 6/4_Glenella No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0587 | 1.0264 | 1.0525 | 1.0586 | 1.026 | 1.0515 | 1.059 | 1.026 | 1.0509 | 1.0593 | 1.0265 | 1.0508 | 1.0578 | 1.0227 | 1.0476
MK | PV 6/5_Glenella No 1 66 kV | % of Rated A | 24.97% | 31.33% | 24.46% | 25.13% | 31.53% | 24.6% | 25.39% | 31.87% | 24.84% | 25.5% | 32.01% | 24.94% | 26.36% | 33.17% | 25.73%
MK | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105119_4
MK | PV 6/5_Glenella No 1 66 kV | Loading (A) | 201.9932 | 284.4342 | 217.9104 | 203.2925 | 286.3239 | 219.1956 | 205.4013 | 289.4234 | 221.3357 | 206.2688 | 290.6376 | 222.2126 | 213.2543 | 301.2249 | 229.2834
MK | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 24.4463 | 33.4298 | 26.1616 | 24.601 | 33.6375 | 26.3095 | 24.8668 | 34.0047 | 26.5722 | 24.978 | 34.1643 | 26.687 | 25.7866 | 35.2739 | 27.4757
MK | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 24.424 | 33.3829 | 26.1584 | 24.5808 | 33.5869 | 26.3057 | 24.8498 | 33.9477 | 26.5673 | 24.9624 | 34.1044 | 26.6816 | 25.7794 | 35.1885 | 27.4648
MK | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.99908 | 0.9986 | 0.99988 | 0.99918 | 0.9985 | 0.99986 | 0.99931 | 0.99832 | 0.99982 | 0.99937 | 0.99825 | 0.9998 | 0.99972 | 0.99758 | 0.9996
MK | PV 6/5_Glenella No 1 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | PV 6/5_Glenella No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
MK | PV 6/5_Glenella No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0587 | 1.0279 | 1.05 | 1.0586 | 1.0274 | 1.0498 | 1.059 | 1.0275 | 1.05 | 1.0593 | 1.028 | 1.0504 | 1.0577 | 1.0241 | 1.0481
MK | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 14.77% | 13.64% | 12.41% | 14.87% | 13.74% | 12.49% | 14.87% | 13.74% | 12.49% | 14.87% | 13.73% | 12.49% | 15.11% | 13.95% | 12.68%
MK | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1
MK | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 57.0279 | 53.0679 | 41.9424 | 57.4144 | 53.4332 | 42.2065 | 57.4148 | 53.4336 | 42.2065 | 57.4109 | 53.4284 | 42.2033 | 58.3062 | 54.2604 | 42.8529
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 6.8335 | 6.3573 | 5.0534 | 6.8353 | 6.3589 | 5.0525 | 6.8353 | 6.3589 | 5.0525 | 6.8353 | 6.3589 | 5.0525 | 6.9396 | 6.4557 | 5.129
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 6.4875 | 6.0425 | 4.8173 | 6.4878 | 6.0427 | 4.8172 | 6.4878 | 6.0427 | 4.8172 | 6.4878 | 6.0427 | 4.8172 | 6.585 | 6.1332 | 4.8893
MK | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.94936 | 0.95046 | 0.95328 | 0.94915 | 0.95026 | 0.95342 | 0.94915 | 0.95026 | 0.95342 | 0.94915 | 0.95026 | 0.95342 | 0.94889 | 0.95002 | 0.95324
MK | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
MK | 6328_Broadlea - Moorvale 66 kV | Time | 15:30:00 | 17:00:00 | 22:00:00 | 15:30:00 | 17:00:00 | 22:00:00 | 15:30:00 | 17:00:00 | 22:00:00 | 15:30:00 | 17:00:00 | 22:00:00 | 15:30:00 | 17:00:00 | 22:00:00
MK | 6328_Broadlea - Moorvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0482 | 1.0479 | 1.054 | 1.0414 | 1.041 | 1.0472 | 1.0414 | 1.041 | 1.0472 | 1.0415 | 1.0411 | 1.0473 | 1.0411 | 1.0408 | 1.047
MK | 6329_Broadlea - Coppabella 66 kV | % of Rated A | 26.98% | 23.49% | 28.13% | 27.16% | 23.66% | 28.01% | 27.16% | 23.66% | 28.01% | 27.15% | 23.66% | 28.01% | 27.16% | 23.66% | 28.02%
MK | 6329_Broadlea - Coppabella 66 kV | Limiting Line Name | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1
MK | 6329_Broadlea - Coppabella 66 kV | Loading (A) | 91.1774 | 91.3771 | 95.0878 | 91.7887 | 92.0383 | 94.6883 | 91.7885 | 92.0386 | 94.6883 | 91.7836 | 92.0304 | 94.6837 | 91.798 | 92.0514 | 94.6979
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MVA) | 10.8227 | 10.8859 | 11.217 | 10.826 | 10.8921 | 11.2433 | 10.826 | 10.8921 | 11.2433 | 10.8259 | 10.892 | 11.2432 | 10.8261 | 10.8922 | 11.2433
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MW) | 10.3983 | 10.4632 | 10.7661 | 10.4 | 10.4658 | 10.7969 | 10.4 | 10.4658 | 10.7969 | 10.4 | 10.4658 | 10.7968 | 10.4001 | 10.4659 | 10.7969
MK | 6329_Broadlea - Coppabella 66 kV | Power Factor | 0.95768 | 0.95807 | 0.9573 | 0.95772 | 0.95794 | 0.95767 | 0.95772 | 0.95794 | 0.95767 | 0.95773 | 0.95794 | 0.95768 | 0.95772 | 0.95793 | 0.95767
MK | 6329_Broadlea - Coppabella 66 kV | Rating (A) | 338 | 389 | 338 | 338 | 389 | 338 | 338 | 389 | 338 | 338 | 389 | 338 | 338 | 389 | 338
MK | 6329_Broadlea - Coppabella 66 kV | Time | 07:00:00 | 21:00:00 | 02:30:00 | 07:00:00 | 21:00:00 | 02:00:00 | 07:00:00 | 21:00:00 | 02:00:00 | 07:00:00 | 21:00:00 | 02:00:00 | 07:00:00 | 21:00:00 | 02:00:00
MK | 6329_Broadlea - Coppabella 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0279 | 1.0317 | 1.0202 | 1.021 | 1.0245 | 1.0272 | 1.021 | 1.0245 | 1.0272 | 1.0211 | 1.0246 | 1.0273 | 1.0209 | 1.0243 | 1.0271
MK | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 40.61% | 38.88% | 43.95% | 44.36% | 42.34% | 48.05% | 44.36% | 42.34% | 48.05% | 44.36% | 42.34% | 48.05% | 44.41% | 42.4% | 48.11%
MK | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 286.2949 | 285.7704 | 286.5782 | 289.2126 | 311.2206 | 313.3066 | 289.212 | 311.2213 | 313.3059 | 289.1984 | 311.1949 | 313.2928 | 289.567 | 311.6422 | 313.6494
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 65.8521 | 65.8002 | 66.0616 | 66.8091 | 71.3527 | 71.8987 | 66.8091 | 71.3527 | 71.8987 | 66.8089 | 71.3523 | 71.8985 | 66.8859 | 71.4422 | 71.9724
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 60.296 | 60.1565 | 60.391 | 61.0107 | 64.7488 | 65.2189 | 61.0107 | 64.7488 | 65.2189 | 61.0107 | 64.7487 | 65.2189 | 61.08 | 64.8288 | 65.2853
MK | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.91563 | 0.91423 | 0.91416 | 0.91321 | 0.90745 | 0.90709 | 0.91321 | 0.90745 | 0.90709 | 0.91321 | 0.90745 | 0.9071 | 0.9132 | 0.90743 | 0.90709
MK | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 735 | 652 | 652 | 735 | 652 | 652 | 735 | 652 | 652 | 735 | 652 | 652 | 735 | 652
MK | 7366_Moranbah - Broadlea 132 kV | Time | 15:00:00 | 21:00:00 | 05:00:00 | 07:30:00 | 21:00:00 | 05:00:00 | 07:30:00 | 21:00:00 | 05:00:00 | 07:30:00 | 21:00:00 | 05:00:00 | 07:30:00 | 21:00:00 | 05:00:00
MK | 7366_Moranbah - Broadlea 132 kV | Min Voltage at Constrained Conductor (pu) | 1.006 | 1.007 | 1.0082 | 1.0103 | 1.0027 | 1.0037 | 1.0103 | 1.0027 | 1.0037 | 1.0104 | 1.0028 | 1.0037 | 1.0102 | 1.0026 | 1.0036
MK | 232_Newlands-Glenden 66 kV | % of Rated A | 10.91% | 7.896% | 5.676% | 10.91% | 7.902% | 5.679% | 10.91% | 7.902% | 5.679% | 10.91% | 7.901% | 5.679% | 10.91% | 7.902% | 5.679%
MK | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1
MK | 232_Newlands-Glenden 66 kV | Loading (A) | 12.6499 | 12.6334 | 8.8539 | 12.6594 | 12.6431 | 8.8598 | 12.6595 | 12.6432 | 8.8598 | 12.6585 | 12.6418 | 8.8592 | 12.6598 | 12.6434 | 8.8599
MK | 232_Newlands-Glenden 66 kV | Loading (MVA) | 1.512 | 1.5101 | 1.0618 | 1.512 | 1.5101 | 1.0617 | 1.512 | 1.5101 | 1.0617 | 1.512 | 1.5101 | 1.0617 | 1.512 | 1.5101 | 1.0617
MK | 232_Newlands-Glenden 66 kV | Loading (MW) | 1.5026 | 1.5007 | 1.0401 | 1.5026 | 1.5007 | 1.0401 | 1.5026 | 1.5007 | 1.0401 | 1.5026 | 1.5007 | 1.0401 | 1.5026 | 1.5007 | 1.0401
MK | 232_Newlands-Glenden 66 kV | Power Factor | 0.99379 | 0.99376 | 0.97956 | 0.99383 | 0.9938 | 0.97964 | 0.99383 | 0.9938 | 0.97964 | 0.99382 | 0.99379 | 0.97963 | 0.99383 | 0.9938 | 0.97964
MK | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
MK | 232_Newlands-Glenden 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
MK | 232_Newlands-Glenden 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0456 | 1.0456 | 1.0491 | 1.0448 | 1.0448 | 1.0483 | 1.0448 | 1.0448 | 1.0483 | 1.0449 | 1.0449 | 1.0484 | 1.0448 | 1.0448 | 1.0483
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 40.4% | 38.38% | 40.62% | 40.44% | 38.41% | 40.65% | 40.44% | 38.41% | 40.65% | 40.44% | 38.41% | 40.65% | 40.44% | 38.41% | 40.65%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 75.9598 | 78.677 | 75.1462 | 76.0273 | 78.7474 | 75.2099 | 76.0279 | 78.748 | 75.21 | 76.0207 | 78.7381 | 75.2054 | 76.0302 | 78.7498 | 75.2105
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 9.0392 | 9.3555 | 8.9722 | 9.0402 | 9.3565 | 8.9731 | 9.0402 | 9.3565 | 8.9731 | 9.0401 | 9.3564 | 8.9731 | 9.0402 | 9.3566 | 8.9731
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 7.9012 | 8.1607 | 7.8426 | 7.9013 | 8.1608 | 7.8427 | 7.9013 | 8.1608 | 7.8427 | 7.9013 | 8.1608 | 7.8427 | 7.9013 | 8.1608 | 7.8427
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.87131 | 0.86963 | 0.87124 | 0.87122 | 0.86955 | 0.87116 | 0.87122 | 0.86955 | 0.87116 | 0.87123 | 0.86956 | 0.87117 | 0.87122 | 0.86954 | 0.87116
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 16:30:00 | 18:30:00 | 00:30:00 | 16:30:00 | 18:30:00 | 00:30:00 | 16:30:00 | 18:30:00 | 00:30:00 | 16:30:00 | 18:30:00 | 00:30:00 | 16:30:00 | 18:30:00 | 00:30:00
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0388 | 1.0377 | 1.0424 | 1.038 | 1.0368 | 1.0416 | 1.038 | 1.0368 | 1.0416 | 1.0381 | 1.0369 | 1.0417 | 1.0379 | 1.0368 | 1.0416
NQ | 2021_Collinsville PS-Collinsville 33 kV | % of Rated A | 23.43% | 19.71% | 18.36% | 23.43% | 19.71% | 18.36% | 23.35% | 19.66% | 18.32% | 23.27% | 19.6% | 18.27% | 23.43% | 19.72% | 18.36%
NQ | 2021_Collinsville PS-Collinsville 33 kV | Limiting Line Name | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1 | TR_CABLE 4176_1
NQ | 2021_Collinsville PS-Collinsville 33 kV | Loading (A) | 162.3778 | 136.6199 | 127.2677 | 162.3779 | 136.6203 | 127.2678 | 161.8095 | 136.2173 | 126.9568 | 161.2406 | 135.8108 | 126.6455 | 162.3797 | 136.6255 | 127.2687
NQ | 2021_Collinsville PS-Collinsville 33 kV | Loading (MVA) | 9.4919 | 7.9906 | 7.4628 | 9.4919 | 7.9906 | 7.4627 | 9.4592 | 7.967 | 7.4447 | 9.4265 | 7.9441 | 7.4267 | 9.4918 | 7.9896 | 7.4625
NQ | 2021_Collinsville PS-Collinsville 33 kV | Loading (MW) | 6.4983 | 5.1117 | 4.723 | 6.4983 | 5.1117 | 4.723 | 6.4702 | 5.0913 | 4.7072 | 6.4421 | 5.071 | 4.6915 | 6.4983 | 5.1116 | 4.723
NQ | 2021_Collinsville PS-Collinsville 33 kV | Power Factor | 0.68442 | 0.63952 | 0.63268 | 0.68442 | 0.63952 | 0.63269 | 0.68382 | 0.63886 | 0.6321 | 0.68321 | 0.63814 | 0.63151 | 0.68443 | 0.6396 | 0.63271
NQ | 2021_Collinsville PS-Collinsville 33 kV | Rating (A) | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693
NQ | 2021_Collinsville PS-Collinsville 33 kV | Time | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00
NQ | 2021_Collinsville PS-Collinsville 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0227 | 1.0233 | 1.0259 | 1.0227 | 1.0233 | 1.0259 | 1.0228 | 1.0233 | 1.0259 | 1.0228 | 1.0234 | 1.026 | 1.0227 | 1.0231 | 1.0259
NQ | 2031 Collinsville-PS-Collinsville 33 kV | % of Rated A | 30.37% | 23.34% | 21.43% | 30.37% | 23.34% | 21.43% | 30.22% | 23.24% | 21.36% | 30.07% | 23.14% | 21.28% | 30.37% | 23.35% | 21.43%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Limiting Line Name | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Loading (A) | 210.457 | 161.7512 | 148.5068 | 210.4572 | 161.7534 | 148.5075 | 209.4221 | 161.0586 | 148.0001 | 208.3857 | 160.3446 | 147.4916 | 210.464 | 161.7816 | 148.5135
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MVA) | 12.3024 | 9.4611 | 8.7093 | 12.3024 | 9.4611 | 8.7093 | 12.2426 | 9.4206 | 8.6797 | 12.1828 | 9.3801 | 8.6502 | 12.3025 | 9.4612 | 8.7093
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MW) | 12.1599 | 9.4563 | 8.6966 | 12.1599 | 9.4563 | 8.6966 | 12.1051 | 9.4166 | 8.6659 | 12.0503 | 9.3769 | 8.6351 | 12.1599 | 9.4564 | 8.6967
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Power Factor | 0.98813 | 0.99929 | 0.99854 | 0.98813 | 0.99929 | 0.99855 | 0.98849 | 0.99939 | 0.9984 | 0.98884 | 0.99948 | 0.99825 | 0.98813 | 0.99929 | 0.99855
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Rating (A) | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Time | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00 | 14:30:00 | 17:00:00 | 23:00:00
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0227 | 1.0233 | 1.0259 | 1.0227 | 1.0233 | 1.0259 | 1.0228 | 1.0233 | 1.0259 | 1.0228 | 1.0234 | 1.026 | 1.0227 | 1.0231 | 1.0259
NQ | 6321_Lucinda 66 kV | % of Rated A | 22.72% | 25.87% | 24.17% | 22.44% | 25.49% | 23.79% | 22.44% | 25.49% | 23.79% | 22.43% | 25.48% | 23.78% | 22.74% | 25.9% | 24.19%
NQ | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2
NQ | 6321_Lucinda 66 kV | Loading (A) | 45.2192 | 57.696 | 49.2974 | 44.6534 | 56.8412 | 48.53 | 44.6469 | 56.8351 | 48.5232 | 44.633 | 56.8306 | 48.511 | 45.252 | 57.7541 | 49.3528
NQ | 6321_Lucinda 66 kV | Loading (MVA) | 5.3589 | 6.7871 | 5.772 | 5.2884 | 6.6832 | 5.678 | 5.2884 | 6.6831 | 5.678 | 5.2883 | 6.685 | 5.6779 | 5.3582 | 6.7875 | 5.7724
NQ | 6321_Lucinda 66 kV | Loading (MW) | 5.072 | 6.3716 | 5.4314 | 5.0081 | 6.2789 | 5.347 | 5.0081 | 6.2789 | 5.347 | 5.0081 | 6.2793 | 5.347 | 5.0719 | 6.3717 | 5.4314
NQ | 6321_Lucinda 66 kV | Power Factor | 0.94624 | 0.93857 | 0.94073 | 0.94677 | 0.93929 | 0.94146 | 0.94677 | 0.93929 | 0.94147 | 0.94679 | 0.93908 | 0.94148 | 0.94634 | 0.93852 | 0.94068
NQ | 6321_Lucinda 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 6321_Lucinda 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | 6321_Lucinda 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0367 | 1.029 | 1.0242 | 1.036 | 1.0285 | 1.0235 | 1.0362 | 1.0286 | 1.0236 | 1.0365 | 1.0289 | 1.0239 | 1.0358 | 1.028 | 1.0232
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 22.8% | 18.01% | 19.19% | 22.75% | 18% | 19.16% | 22.75% | 18% | 19.17% | 22.76% | 18.01% | 19.17% | 22.75% | 17.99% | 19.16%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 15.7287 | 15.6672 | 15.7334 | 15.7 | 15.6562 | 15.7144 | 15.7005 | 15.6578 | 15.7161 | 15.7025 | 15.6653 | 15.7191 | 15.6986 | 15.6542 | 15.7138
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 1.9019 | 1.8764 | 1.9049 | 1.895 | 1.8737 | 1.9004 | 1.8951 | 1.8741 | 1.9009 | 1.8956 | 1.8759 | 1.9016 | 1.8947 | 1.8732 | 1.9003
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 0.24184 | 0.60437 | 0.28528 | 0.24181 | 0.60436 | 0.28764 | 0.24181 | 0.60437 | 0.28764 | 0.24181 | 0.60437 | 0.28765 | 0.2418 | 0.60436 | 0.28764
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.12716 | 0.32209 | 0.14976 | 0.1276 | 0.32256 | 0.15136 | 0.12759 | 0.32249 | 0.15132 | 0.12756 | 0.32217 | 0.15127 | 0.12762 | 0.32264 | 0.15137
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 09:30:00 | 17:30:00 | 03:30:00 | 09:30:00 | 17:30:00 | 02:30:00 | 09:30:00 | 17:30:00 | 02:30:00 | 09:30:00 | 17:30:00 | 02:30:00 | 09:30:00 | 17:30:00 | 02:30:00
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0578 | 1.0477 | 1.0591 | 1.0559 | 1.0469 | 1.0579 | 1.0559 | 1.047 | 1.058 | 1.056 | 1.0475 | 1.0582 | 1.0558 | 1.0467 | 1.0579
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 12.54% | 10.66% | 7.17% | 12% | 10.2% | 6.863% | 12% | 10.2% | 6.862% | 11.99% | 10.2% | 6.86% | 12% | 10.2% | 6.863%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 16.8018 | 19.3014 | 12.5472 | 16.0771 | 18.4667 | 12.0098 | 16.0748 | 18.465 | 12.0083 | 16.0702 | 18.4581 | 12.0055 | 16.0778 | 18.4695 | 12.0109
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 2.0118 | 2.3043 | 1.4938 | 1.9237 | 2.2033 | 1.4287 | 1.9236 | 2.2033 | 1.4287 | 1.9236 | 2.2033 | 1.4287 | 1.9237 | 2.2033 | 1.4287
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 2.0101 | 2.301 | 1.4938 | 1.9224 | 2.2005 | 1.4287 | 1.9224 | 2.2005 | 1.4287 | 1.9224 | 2.2005 | 1.4287 | 1.9224 | 2.2005 | 1.4287
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.99905 | 0.99839 | 0.9999 | 0.99922 | 0.99861 | 0.99996 | 0.99922 | 0.99861 | 0.99996 | 0.99922 | 0.99861 | 0.99996 | 0.99922 | 0.99861 | 0.99996
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0474 | 1.0444 | 1.0414 | 1.0467 | 1.0437 | 1.0406 | 1.0468 | 1.0438 | 1.0407 | 1.0471 | 1.0442 | 1.0409 | 1.0466 | 1.0435 | 1.0405
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 46.07% | 52.87% | 46.09% | 45.9% | 52.51% | 45.73% | 45.89% | 52.5% | 45.72% | 45.89% | 52.48% | 45.71% | 46.17% | 52.91% | 46.14%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 93.9892 | 117.906 | 94.0144 | 93.6344 | 117.0864 | 93.28 | 93.6216 | 117.0681 | 93.2671 | 93.61 | 117.0309 | 93.2439 | 94.1854 | 117.9992 | 94.1187
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 11.1232 | 13.7486 | 11.092 | 11.0598 | 13.6458 | 10.9959 | 11.0598 | 13.6457 | 10.9958 | 11.0597 | 13.6455 | 10.9957 | 11.1243 | 13.7492 | 11.0928
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 9.2758 | 11.6736 | 9.606 | 9.2174 | 11.5827 | 9.5206 | 9.2174 | 11.5827 | 9.5206 | 9.2174 | 11.5827 | 9.5205 | 9.2759 | 11.6738 | 9.6061
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.83389 | 0.84907 | 0.866 | 0.83339 | 0.8488 | 0.8658 | 0.83339 | 0.8488 | 0.86581 | 0.8334 | 0.84881 | 0.86582 | 0.83381 | 0.84904 | 0.86596
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 204 | 223 | 204 | 204 | 223 | 204 | 204 | 223 | 204 | 204 | 223 | 204 | 204 | 223 | 204
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 08:30:00 | 21:00:00 | 22:00:00 | 08:30:00 | 21:00:00 | 22:00:00 | 08:30:00 | 21:00:00 | 22:00:00 | 08:30:00 | 21:00:00 | 22:00:00 | 08:30:00 | 21:00:00 | 22:00:00
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0352 | 1.02 | 1.032 | 1.0332 | 1.0194 | 1.0311 | 1.0333 | 1.0196 | 1.0313 | 1.0335 | 1.0199 | 1.0315 | 1.0331 | 1.0192 | 1.0309
NQ | 118_Cannonvale No 2 66 kV | % of Rated A | 92.43% | 95.02% | 72.23% | 92.44% | 95.03% | 72.24% | 92.44% | 95.11% | 72.25% | 92.49% | 94.85% | 72.08% | 93.38% | 96.15% | 72.94%
NQ | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1
NQ | 118_Cannonvale No 2 66 kV | Loading (A) | 178.3931 | 183.3842 | 139.4024 | 178.4056 | 183.4146 | 139.428 | 178.4131 | 183.5681 | 139.4365 | 178.5132 | 183.0679 | 139.1138 | 180.2295 | 185.5701 | 140.7765
NQ | 118_Cannonvale No 2 66 kV | Loading (MVA) | 20.7026 | 21.1274 | 16.2657 | 20.7023 | 21.1278 | 16.267 | 20.7023 | 21.1287 | 16.2668 | 20.6568 | 21.0769 | 16.2311 | 20.8934 | 21.337 | 16.4128
NQ | 118_Cannonvale No 2 66 kV | Loading (MW) | 20.6864 | 21.1205 | 16.085 | 20.6859 | 21.1208 | 16.086 | 20.686 | 21.1221 | 16.086 | 20.6417 | 21.0695 | 16.0474 | 20.8805 | 21.3326 | 16.2422
NQ | 118_Cannonvale No 2 66 kV | Power Factor | 0.99922 | 0.99967 | 0.98889 | 0.99921 | 0.99967 | 0.98887 | 0.99921 | 0.99969 | 0.98888 | 0.99927 | 0.99965 | 0.98869 | 0.99938 | 0.9998 | 0.9896
NQ | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
NQ | 118_Cannonvale No 2 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | 118_Cannonvale No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0151 | 1.0077 | 1.0206 | 1.015 | 1.0076 | 1.0205 | 1.015 | 1.0068 | 1.0205 | 1.0122 | 1.0071 | 1.0206 | 1.014 | 1.0057 | 1.0198
NQ | 119_Cannonvale No 1 66 kV | % of Rated A | 98.03% | 72.63% | 56.55% | 98.04% | 72.64% | 56.56% | 98.04% | 72.7% | 56.56% | 98.09% | 72.5% | 56.43% | 99.07% | 73.51% | 57.12%
NQ | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQ | 119_Cannonvale No 1 66 kV | Loading (A) | 181.3577 | 188.1106 | 142.4973 | 181.3703 | 188.1416 | 142.5236 | 181.3779 | 188.3003 | 142.5324 | 181.4691 | 187.776 | 142.1934 | 183.2762 | 190.3982 | 143.9394
NQ | 119_Cannonvale No 1 66 kV | Loading (MVA) | 20.9129 | 21.5357 | 16.562 | 20.9126 | 21.5361 | 16.5632 | 20.9126 | 21.5368 | 16.5631 | 20.8646 | 21.4833 | 16.5259 | 21.1095 | 21.7516 | 16.7149
NQ | 119_Cannonvale No 1 66 kV | Loading (MW) | 20.8713 | 21.5142 | 16.3381 | 20.8707 | 21.5144 | 16.339 | 20.8708 | 21.5158 | 16.3391 | 20.8248 | 21.461 | 16.2988 | 21.0732 | 21.7349 | 16.502
NQ | 119_Cannonvale No 1 66 kV | Power Factor | 0.99791 | 0.99892 | 0.98631 | 0.99789 | 0.99892 | 0.98629 | 0.9979 | 0.99895 | 0.9863 | 0.99799 | 0.99888 | 0.98609 | 0.99818 | 0.99916 | 0.98709
NQ | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252
NQ | 119_Cannonvale No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | 119_Cannonvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0074 | 1.0001 | 1.0159 | 1.0073 | 0.99993 | 1.0158 | 1.0073 | 0.99911 | 1.0157 | 1.0045 | 0.99942 | 1.0158 | 1.0062 | 0.99793 | 1.015
NQ | 120_Prosperpine - Calen 66 kV | % of Rated A | 22.57% | 28.47% | 22.8% | 22.92% | 29.01% | 23.22% | 22.92% | 29.04% | 23.22% | 22.98% | 29.03% | 23.22% | 23.42% | 29.59% | 23.62%
NQ | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1
NQ | 120_Prosperpine - Calen 66 kV | Loading (A) | 29.7957 | 50.3937 | 38.7588 | 30.2541 | 51.3407 | 39.4771 | 30.2552 | 51.3991 | 39.4799 | 30.3349 | 51.3838 | 39.4751 | 30.9084 | 52.3664 | 40.1468
NQ | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 3.4578 | 5.7073 | 4.5224 | 3.5107 | 5.811 | 4.6058 | 3.5107 | 5.8113 | 4.6058 | 3.5102 | 5.8112 | 4.6058 | 3.5831 | 5.9122 | 4.6806
NQ | 120_Prosperpine - Calen 66 kV | Loading (MW) | 3.4259 | 5.6972 | 4.518 | 3.4811 | 5.7995 | 4.6023 | 3.4811 | 5.7997 | 4.6024 | 3.4815 | 5.7996 | 4.6023 | 3.5552 | 5.9002 | 4.6776
NQ | 120_Prosperpine - Calen 66 kV | Power Factor | 0.99076 | 0.99821 | 0.99902 | 0.99157 | 0.998 | 0.99926 | 0.99158 | 0.99798 | 0.99926 | 0.99181 | 0.99799 | 0.99926 | 0.99221 | 0.99795 | 0.99935
NQ | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
NQ | 120_Prosperpine - Calen 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | 120_Prosperpine - Calen 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0152 | 0.99064 | 1.0207 | 1.0151 | 0.99004 | 1.0206 | 1.015 | 0.98896 | 1.0205 | 1.0122 | 0.98924 | 1.0206 | 1.0141 | 0.98754 | 1.0198
NQ | 426_Mt Rooper 66 kV | % of Rated A | 49.96% | 43.72% | 31.74% | 49.96% | 43.72% | 31.75% | 49.97% | 43.73% | 31.75% | 49.95% | 43.71% | 31.74% | 49.99% | 43.8% | 31.78%
NQ | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1
NQ | 426_Mt Rooper 66 kV | Loading (A) | 124.4017 | 122.403 | 88.8755 | 124.4114 | 122.4208 | 88.8875 | 124.4211 | 122.4383 | 88.8942 | 124.3859 | 122.3857 | 88.8741 | 124.481 | 122.6471 | 88.9913
NQ | 426_Mt Rooper 66 kV | Loading (MVA) | 14.0058 | 13.6141 | 10.1189 | 14.0059 | 13.6142 | 10.119 | 14.0059 | 13.6143 | 10.119 | 14.0057 | 13.614 | 10.1189 | 14.0063 | 13.6154 | 10.1191
NQ | 426_Mt Rooper 66 kV | Loading (MW) | 13.7788 | 13.3277 | 9.9462 | 13.7788 | 13.3278 | 9.9463 | 13.7788 | 13.3278 | 9.9463 | 13.7788 | 13.3277 | 9.9462 | 13.779 | 13.3282 | 9.9464
NQ | 426_Mt Rooper 66 kV | Power Factor | 0.98379 | 0.97853 | 0.98237 | 0.98379 | 0.97852 | 0.98237 | 0.98379 | 0.97852 | 0.98237 | 0.9838 | 0.97853 | 0.98237 | 0.98377 | 0.97847 | 0.98237
NQ | 426_Mt Rooper 66 kV | Rating (A) | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280
NQ | 426_Mt Rooper 66 kV | Time | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00
NQ | 426_Mt Rooper 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98485 | 0.97295 | 0.99597 | 0.98477 | 0.97282 | 0.99584 | 0.9847 | 0.97269 | 0.99577 | 0.98496 | 0.97308 | 0.99598 | 0.98426 | 0.97111 | 0.99469
NQ | CANN_JUPO (Ex119&118) | % of Rated A | 63.05% | 63.5% | 47.05% | 63.35% | 63.82% | 47.3% | 63.35% | 63.83% | 47.3% | 63.55% | 63.8% | 47.29% | 64.05% | 64.56% | 47.84%
NQ | CANN_JUPO (Ex119&118) | Limiting Line Name | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1
NQ | CANN_JUPO (Ex119&118) | Loading (A) | 176.5277 | 177.7891 | 131.7369 | 177.372 | 178.6892 | 132.4305 | 177.3805 | 178.7145 | 132.4404 | 177.9349 | 178.6386 | 132.4108 | 179.3263 | 180.7573 | 133.9398
NQ | CANN_JUPO (Ex119&118) | Loading (MVA) | 19.8414 | 19.8994 | 15.0645 | 19.9344 | 19.9977 | 15.142 | 19.9345 | 19.9978 | 15.1421 | 19.9377 | 19.9974 | 15.1419 | 20.1221 | 20.1947 | 15.2974
NQ | CANN_JUPO (Ex119&118) | Loading (MW) | 19.6314 | 19.6906 | 14.9742 | 19.7232 | 19.7876 | 15.0509 | 19.7232 | 19.7876 | 15.0509 | 19.7245 | 19.7875 | 15.0508 | 19.9075 | 19.9818 | 15.2044
NQ | CANN_JUPO (Ex119&118) | Power Factor | 0.98841 | 0.98851 | 0.99283 | 0.9884 | 0.98849 | 0.99281 | 0.9884 | 0.98849 | 0.99281 | 0.98831 | 0.9885 | 0.99282 | 0.98834 | 0.98847 | 0.99276
NQ | CANN_JUPO (Ex119&118) | Rating (A) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
NQ | CANN_JUPO (Ex119&118) | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
NQ | CANN_JUPO (Ex119&118) | Min Voltage at Constrained Conductor (pu) | 0.98323 | 0.97911 | 1.0003 | 0.98314 | 0.97899 | 1.0002 | 0.98309 | 0.97886 | 1.0001 | 0.98019 | 0.97925 | 1.0004 | 0.98158 | 0.97732 | 0.99909
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 65.45% | 67.79% | 60.82% | 65.25% | 67.59% | 60.67% | 65.26% | 67.66% | 60.67% | 64.67% | 67.33% | 60.42% | 65.77% | 68.24% | 61.09%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 127.6237 | 147.7917 | 121.0396 | 127.2469 | 147.3523 | 120.7281 | 127.2558 | 147.509 | 120.7333 | 126.1069 | 146.7707 | 120.2285 | 128.2425 | 148.7581 | 121.5677
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 15.0614 | 17.2968 | 14.1832 | 15.0174 | 17.2449 | 14.147 | 15.0185 | 17.2465 | 14.1472 | 14.7636 | 17.1643 | 14.0894 | 15.1258 | 17.3811 | 14.2395
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 14.8002 | 17.158 | 13.7555 | 14.7535 | 17.1041 | 13.7162 | 14.7557 | 17.108 | 13.7177 | 14.3809 | 17.0219 | 13.6544 | 14.8719 | 17.2496 | 13.8198
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.98265 | 0.99197 | 0.96983 | 0.98242 | 0.99183 | 0.96954 | 0.98249 | 0.99196 | 0.96963 | 0.97407 | 0.9917 | 0.96912 | 0.98321 | 0.99243 | 0.97051
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0323 | 1.0237 | 1.025 | 1.0323 | 1.0237 | 1.025 | 1.0323 | 1.0227 | 1.025 | 1.0241 | 1.0229 | 1.0251 | 1.0317 | 1.022 | 1.0246
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 13.41% | 9.416% | 5.02% | 13.51% | 9.499% | 5.058% | 13.54% | 9.519% | 5.069% | 10.56% | 9.509% | 5.064% | 13.78% | 9.702% | 5.139%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 25.8813 | 25.8009 | 13.403 | 26.0785 | 26.0265 | 13.5052 | 26.1276 | 26.0833 | 13.5353 | 20.3722 | 26.056 | 13.5218 | 26.6034 | 26.5834 | 13.7203
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 3.0036 | 2.9851 | 1.5643 | 3.0262 | 3.0108 | 1.5761 | 3.0318 | 3.017 | 1.5795 | 2.3574 | 3.0146 | 1.5781 | 3.0841 | 3.072 | 1.6005
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 2.2938 | 2.2203 | 0.74647 | 2.3216 | 2.2522 | 0.76766 | 2.3235 | 2.2549 | 0.76615 | 2.0356 | 2.2571 | 0.76826 | 2.373 | 2.3075 | 0.79287
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.76368 | 0.74379 | 0.4772 | 0.76716 | 0.74802 | 0.48707 | 0.76637 | 0.74737 | 0.48505 | 0.86348 | 0.74871 | 0.48684 | 0.76943 | 0.75115 | 0.4954
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 16:30:00 | 17:00:00 | 03:00:00 | 16:30:00 | 17:00:00 | 03:00:00 | 16:30:00 | 17:00:00 | 03:00:00 | 16:30:00 | 17:00:00 | 03:00:00 | 16:30:00 | 17:00:00 | 03:00:00
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0152 | 1.0121 | 1.0209 | 1.0151 | 1.012 | 1.0209 | 1.0151 | 1.0118 | 1.0208 | 1.0123 | 1.0121 | 1.0209 | 1.0141 | 1.0109 | 1.0204
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 62.75% | 41.61% | 65% | 62.75% | 41.61% | 65% | 62.75% | 41.61% | 65% | 62.75% | 41.61% | 65% | 62.4% | 41.63% | 65.02%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 128.0094 | 92.7866 | 132.5998 | 128.0122 | 92.7914 | 132.604 | 128.0164 | 92.7972 | 132.6086 | 128.0047 | 92.7832 | 132.5967 | 127.3003 | 92.8277 | 132.6352
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 14.6374 | 10.6737 | 15.1624 | 14.6375 | 10.6737 | 15.1624 | 14.6375 | 10.6737 | 15.1625 | 14.6374 | 10.6737 | 15.1624 | 14.6355 | 10.6738 | 15.1625
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 14.1644 | 10.3385 | 14.6709 | 14.1644 | 10.3385 | 14.671 | 14.1644 | 10.3385 | 14.671 | 14.1644 | 10.3385 | 14.6709 | 14.163 | 10.3385 | 14.671
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.96768 | 0.968 | 0.96758 | 0.96768 | 0.968 | 0.96758 | 0.96768 | 0.968 | 0.96758 | 0.96768 | 0.968 | 0.96758 | 0.96771 | 0.968 | 0.96758
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 204 | 223 | 204 | 204 | 223 | 204 | 204 | 223 | 204 | 204 | 223 | 204 | 204 | 223 | 204
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 06:30:00 | 21:30:00 | 04:00:00 | 06:30:00 | 21:30:00 | 04:00:00 | 06:30:00 | 21:30:00 | 04:00:00 | 06:30:00 | 21:30:00 | 04:00:00 | 06:30:00 | 21:30:00 | 04:00:00
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99071 | 1.0002 | 0.99028 | 0.99069 | 1.0002 | 0.99025 | 0.99066 | 1.0001 | 0.99022 | 0.99075 | 1.0003 | 0.99031 | 0.99623 | 0.99978 | 0.99002
NQ | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 16.92% | 15.56% | 11.82% | 17.06% | 15.68% | 11.92% | 17.19% | 15.82% | 12.01% | 17.24% | 15.82% | 12.01% | 17.61% | 16.22% | 12.31%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 29.9458 | 36.7098 | 26.7207 | 30.1876 | 37.0112 | 26.9368 | 30.428 | 37.3448 | 27.152 | 30.5133 | 37.3345 | 27.1488 | 31.1755 | 38.2686 | 27.8098
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 3.475 | 4.2302 | 3.1177 | 3.5028 | 4.264 | 3.1426 | 3.5306 | 4.2979 | 3.1674 | 3.5307 | 4.2979 | 3.1674 | 3.6139 | 4.3996 | 3.2421
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 3.4077 | 4.1423 | 3.0589 | 3.4348 | 4.1752 | 3.0832 | 3.4618 | 4.2081 | 3.1074 | 3.4618 | 4.2081 | 3.1074 | 3.543 | 4.3067 | 3.1803
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.98061 | 0.97922 | 0.98113 | 0.98056 | 0.97916 | 0.98109 | 0.98051 | 0.97908 | 0.98105 | 0.98048 | 0.97908 | 0.98105 | 0.98036 | 0.97888 | 0.98091
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0151 | 1.008 | 1.0207 | 1.015 | 1.0078 | 1.0205 | 1.015 | 1.0068 | 1.0205 | 1.0122 | 1.007 | 1.0206 | 1.014 | 1.0057 | 1.0198
NQ | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 33.89% | 31.17% | 23.68% | 34.17% | 31.43% | 23.87% | 34.44% | 31.72% | 24.07% | 34.54% | 31.71% | 24.06% | 35.29% | 32.5% | 24.65%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 59.992 | 73.572 | 53.5226 | 60.4772 | 74.1774 | 53.9563 | 60.9597 | 74.8476 | 54.388 | 61.1311 | 74.8269 | 54.3816 | 62.4601 | 76.7032 | 55.6978
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 6.9615 | 8.4776 | 6.2447 | 7.0172 | 8.5456 | 6.2946 | 7.0729 | 8.6138 | 6.3445 | 7.0733 | 8.6138 | 6.3445 | 7.2402 | 8.818 | 6.4932
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 6.8269 | 8.3019 | 6.1271 | 6.8812 | 8.368 | 6.1758 | 6.9355 | 8.434 | 6.2246 | 6.9355 | 8.434 | 6.2246 | 7.0984 | 8.6323 | 6.3704
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.98064 | 0.97926 | 0.98116 | 0.9806 | 0.9792 | 0.98112 | 0.98055 | 0.97912 | 0.98108 | 0.98052 | 0.97913 | 0.98108 | 0.9804 | 0.97893 | 0.98108
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0151 | 1.008 | 1.0206 | 1.015 | 1.0078 | 1.0205 | 1.015 | 1.0067 | 1.0204 | 1.0122 | 1.007 | 1.0206 | 1.014 | 1.0056 | 1.0198
NQ | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 25.66% | 23.04% | 23.83% | 25.66% | 23.04% | 23.83% | 25.79% | 23.15% | 23.94% | 25.79% | 23.15% | 23.94% | 25.85% | 23.21% | 23.97%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 219.3921 | 214.2498 | 207.7701 | 219.3921 | 214.2498 | 207.7701 | 220.4892 | 215.3054 | 208.7786 | 220.4861 | 215.3013 | 208.7768 | 220.9794 | 215.8924 | 209.0465
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 83.7611 | 82.0104 | 79.7592 | 83.7611 | 82.0104 | 79.7592 | 83.8003 | 82.0472 | 79.7939 | 83.8001 | 82.047 | 79.7938 | 83.9696 | 82.2502 | 79.8883
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 81.4859 | 79.9927 | 77.648 | 81.4859 | 79.9927 | 77.648 | 81.4881 | 79.9976 | 77.652 | 81.4881 | 79.9976 | 77.652 | 81.6513 | 80.1924 | 77.7444
NQ | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.9716 | 0.97419 | 0.97236 | 0.9716 | 0.97419 | 0.97236 | 0.97116 | 0.9738 | 0.97198 | 0.97116 | 0.9738 | 0.97198 | 0.97114 | 0.97376 | 0.97198
NQ | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872
NQ | 7018_Mica Creek C - Chumvale 220 kV | Time | 14:30:00 | 17:00:00 | 03:00:00 | 14:30:00 | 17:00:00 | 03:00:00 | 14:30:00 | 17:00:00 | 03:00:00 | 14:30:00 | 17:00:00 | 03:00:00 | 14:30:00 | 17:00:00 | 03:00:00
NQ | 7018_Mica Creek C - Chumvale 220 kV | Min Voltage at Constrained Conductor (pu) | 1.0019 | 1.0045 | 1.0074 | 1.0019 | 1.0045 | 1.0074 | 0.99741 | 1.0001 | 1.003 | 0.99742 | 1.0001 | 1.003 | 0.99721 | 0.99981 | 1.0029
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 41.8% | 39.91% | 28.13% | 41.8% | 39.91% | 28.13% | 42% | 40.1% | 28.26% | 42% | 40.09% | 28.26% | 43.05% | 41.1% | 28.96%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 68.1351 | 72.6303 | 48.3765 | 68.1351 | 72.6303 | 48.3765 | 68.4572 | 72.9731 | 48.6036 | 68.456 | 72.9717 | 48.603 | 70.1727 | 74.802 | 49.8042
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 7.7255 | 8.2697 | 5.5411 | 7.7255 | 8.2697 | 5.5411 | 7.7264 | 8.27 | 5.5415 | 7.7264 | 8.27 | 5.5415 | 7.9154 | 8.472 | 5.6763
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 7.6506 | 8.1904 | 5.5008 | 7.6506 | 8.1904 | 5.5008 | 7.6509 | 8.1906 | 5.501 | 7.6509 | 8.1906 | 5.501 | 7.8365 | 8.389 | 5.634
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.99023 | 0.99035 | 0.9926 | 0.99023 | 0.99035 | 0.9926 | 0.99016 | 0.99034 | 0.99255 | 0.99016 | 0.99034 | 0.99255 | 0.98996 | 0.99014 | 0.99242
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99135 | 0.99545 | 1.0017 | 0.99135 | 0.99545 | 1.0017 | 0.98679 | 0.99081 | 0.99708 | 0.98681 | 0.99083 | 0.9971 | 0.9862 | 0.99017 | 0.9967
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 14.4% | 8.764% | 8.479% | 14.4% | 8.764% | 8.479% | 14.34% | 8.729% | 8.445% | 14.34% | 8.729% | 8.445% | 14.34% | 8.728% | 8.444%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 11.9512 | 11.9192 | 11.9552 | 11.9512 | 11.9192 | 11.9552 | 11.9035 | 11.8712 | 11.9075 | 11.9038 | 11.8717 | 11.9078 | 11.9023 | 11.8695 | 11.9065
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 1.4355 | 1.4281 | 1.4365 | 1.4355 | 1.4281 | 1.4365 | 1.4245 | 1.417 | 1.4254 | 1.4245 | 1.4171 | 1.4255 | 1.4242 | 1.4166 | 1.4252
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.092929 | 0.092889 | 0.092934 | 0.092929 | 0.092889 | 0.092934 | 0.092869 | 0.092828 | 0.092874 | 0.092869 | 0.092829 | 0.092874 | 0.092867 | 0.092826 | 0.092873
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.064736 | 0.065044 | 0.064697 | 0.064736 | 0.065044 | 0.064697 | 0.065196 | 0.06551 | 0.065156 | 0.065193 | 0.065505 | 0.065154 | 0.065207 | 0.065527 | 0.065167
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 09:00:00 | 21:30:00 | 05:30:00 | 09:00:00 | 21:30:00 | 05:30:00 | 09:00:00 | 21:30:00 | 05:30:00 | 09:00:00 | 21:30:00 | 05:30:00 | 09:00:00 | 21:30:00 | 05:30:00
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0507 | 1.0481 | 1.0511 | 1.0507 | 1.0481 | 1.0511 | 1.0468 | 1.0442 | 1.0472 | 1.0468 | 1.0442 | 1.0472 | 1.0467 | 1.044 | 1.0471
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 18.91% | 16.88% | 13.15% | 18.91% | 16.88% | 13.15% | 18.98% | 16.95% | 13.2% | 18.88% | 16.86% | 13.13% | 19.28% | 17.21% | 13.41%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 72.6141 | 82.9015 | 60.7647 | 72.6141 | 82.9015 | 60.7647 | 72.8872 | 83.2151 | 60.9937 | 72.5074 | 82.7808 | 60.6759 | 74.0302 | 84.5221 | 61.9489
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 17.0168 | 19.4376 | 14.2795 | 17.0168 | 19.4376 | 14.2795 | 17.0173 | 19.4383 | 14.2802 | 16.929 | 19.3374 | 14.2059 | 17.2823 | 19.7413 | 14.5029
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 16.9193 | 19.3174 | 14.2404 | 16.9193 | 19.3174 | 14.2404 | 16.9194 | 19.3176 | 14.2405 | 16.8319 | 19.2177 | 14.1668 | 17.1821 | 19.6175 | 14.4617
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.99427 | 0.99381 | 0.99723 | 0.99427 | 0.99381 | 0.99723 | 0.99425 | 0.99379 | 0.9972 | 0.99426 | 0.99381 | 0.99722 | 0.99419 | 0.99373 | 0.99713
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.025 | 1.0255 | 1.0278 | 1.025 | 1.0255 | 1.0278 | 1.0212 | 1.0217 | 1.024 | 1.0212 | 1.0217 | 1.024 | 1.0211 | 1.0216 | 1.024
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 26.03% | 24.01% | 18.16% | 26.03% | 24.01% | 18.16% | 26.12% | 24.1% | 18.23% | 25.99% | 23.98% | 18.13% | 26.53% | 24.48% | 18.51%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 72.6138 | 82.8432 | 61.0095 | 72.6138 | 82.8432 | 61.0095 | 72.8864 | 83.1566 | 61.2363 | 72.5088 | 82.7245 | 60.9212 | 74.0226 | 84.4569 | 62.1834
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 17.0198 | 19.4278 | 14.3376 | 17.0198 | 19.4278 | 14.3376 | 17.0203 | 19.4285 | 14.3375 | 16.9325 | 19.328 | 14.2639 | 17.2838 | 19.73 | 14.5584
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 17.0145 | 19.4126 | 14.3365 | 17.0145 | 19.4126 | 14.3365 | 17.0145 | 19.4127 | 14.3366 | 16.927 | 19.3127 | 14.2629 | 17.2772 | 19.7126 | 14.5578
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.99968 | 0.99921 | 0.99993 | 0.99968 | 0.99921 | 0.99993 | 0.99966 | 0.99918 | 0.99994 | 0.99967 | 0.9992 | 0.99993 | 0.99961 | 0.99911 | 0.99996
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0252 | 1.0257 | 1.0277 | 1.0252 | 1.0257 | 1.0277 | 1.0214 | 1.0219 | 1.0239 | 1.0214 | 1.0219 | 1.0239 | 1.0213 | 1.0218 | 1.0238
NQ | MICC-MICB No 1 132 kV | % of Rated A | 47.56% | 34.04% | 33.01% | 47.56% | 34.04% | 33.01% | 47.75% | 34.18% | 33.13% | 47.75% | 34.17% | 33.13% | 47.83% | 34.24% | 33.16%
NQ | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ | MICC-MICB No 1 132 kV | Loading (A) | 248.2774 | 244.7718 | 237.6393 | 248.2774 | 244.7718 | 237.6393 | 249.2625 | 245.7186 | 238.5271 | 249.2592 | 245.715 | 238.5257 | 249.6706 | 246.1671 | 238.7358
NQ | MICC-MICB No 1 132 kV | Loading (MVA) | 58.2478 | 57.4469 | 55.8641 | 58.2478 | 57.4469 | 55.8641 | 58.2618 | 57.4557 | 55.8665 | 58.2617 | 57.4556 | 55.8665 | 58.3528 | 57.5556 | 55.9134
NQ | MICC-MICB No 1 132 kV | Loading (MW) | 58.2426 | 57.4468 | 55.8561 | 58.2426 | 57.4468 | 55.8561 | 58.2501 | 57.4551 | 55.8636 | 58.25 | 57.4551 | 55.8635 | 58.3398 | 57.5548 | 55.9107
NQ | MICC-MICB No 1 132 kV | Power Factor | 0.99991 | 1 | 0.99986 | 0.99991 | 1 | 0.99986 | 0.9998 | 0.99999 | 0.99995 | 0.9998 | 0.99999 | 0.99995 | 0.99978 | 0.99999 | 0.99995
NQ | MICC-MICB No 1 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | MICC-MICB No 1 132 kV | Time | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00
NQ | MICC-MICB No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0261 | 1.0265 | 1.0282 | 1.0261 | 1.0265 | 1.0282 | 1.0223 | 1.0227 | 1.0244 | 1.0223 | 1.0227 | 1.0244 | 1.0222 | 1.0226 | 1.0244
NQ | MICC-MICB No 2 132 kV | % of Rated A | 47.73% | 34.16% | 33.12% | 47.73% | 34.16% | 33.12% | 47.92% | 34.29% | 33.24% | 47.92% | 34.29% | 33.24% | 48% | 34.36% | 33.27%
NQ | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ | MICC-MICB No 2 132 kV | Loading (A) | 249.1436 | 245.6258 | 238.4683 | 249.1436 | 245.6258 | 238.4683 | 250.1321 | 246.5758 | 239.3593 | 250.1288 | 246.5723 | 239.3578 | 250.5417 | 247.0259 | 239.5687
NQ | MICC-MICB No 2 132 kV | Loading (MVA) | 58.451 | 57.6474 | 56.059 | 58.451 | 57.6474 | 56.059 | 58.4651 | 57.6561 | 56.0614 | 58.465 | 57.6561 | 56.0614 | 58.5564 | 57.7564 | 56.1085
NQ | MICC-MICB No 2 132 kV | Loading (MW) | 58.4458 | 57.6472 | 56.051 | 58.4458 | 57.6472 | 56.051 | 58.4533 | 57.6556 | 56.0584 | 58.4533 | 57.6556 | 56.0584 | 58.5434 | 57.7556 | 56.1058
NQ | MICC-MICB No 2 132 kV | Power Factor | 0.99991 | 1 | 0.99986 | 0.99991 | 1 | 0.99986 | 0.9998 | 0.99999 | 0.99995 | 0.9998 | 0.99999 | 0.99995 | 0.99978 | 0.99999 | 0.99995
NQ | MICC-MICB No 2 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | MICC-MICB No 2 132 kV | Time | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00 | 15:30:00 | 17:00:00 | 03:00:00
NQ | MICC-MICB No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0261 | 1.0265 | 1.0282 | 1.0261 | 1.0265 | 1.0282 | 1.0223 | 1.0227 | 1.0244 | 1.0223 | 1.0227 | 1.0244 | 1.0222 | 1.0226 | 1.0244
NQ | 6127_Bohle-Black River 1 66 kV | % of Rated A | 17.6% | 24.01% | 17.9% | 18% | 24.57% | 18.2% | 18.42% | 25.18% | 18.63% | 18.71% | 25.59% | 18.93% | 19.44% | 26.63% | 19.66%
NQ | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ | 6127_Bohle-Black River 1 66 kV | Loading (A) | 128.327 | 187.9905 | 127.1209 | 131.2007 | 192.3497 | 129.2348 | 134.2923 | 197.1388 | 132.2746 | 136.3848 | 200.3881 | 134.3678 | 141.6947 | 208.5498 | 139.5907
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 15.2402 | 22.114 | 15.1418 | 15.4144 | 22.3757 | 15.3145 | 15.7635 | 22.8957 | 15.6632 | 16.0053 | 23.2616 | 15.9068 | 16.5993 | 24.1502 | 16.5021
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 15.187 | 21.9219 | 15.0897 | 15.3576 | 22.1746 | 15.2607 | 15.7015 | 22.677 | 15.6044 | 15.9394 | 23.0296 | 15.8442 | 16.5232 | 23.8862 | 16.4297
NQ | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.99651 | 0.99132 | 0.99656 | 0.99632 | 0.99101 | 0.99649 | 0.99606 | 0.99045 | 0.99624 | 0.99588 | 0.99003 | 0.99606 | 0.99541 | 0.98907 | 0.99561
NQ | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 6127_Bohle-Black River 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | 6127_Bohle-Black River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0389 | 1.029 | 1.042 | 1.0277 | 1.0176 | 1.0366 | 1.0268 | 1.016 | 1.0359 | 1.0266 | 1.0155 | 1.0356 | 1.0248 | 1.013 | 1.0341
NQ | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 17.8% | 24.28% | 18.1% | 18.2% | 24.84% | 18.4% | 18.63% | 25.46% | 18.84% | 18.92% | 25.88% | 19.13% | 19.65% | 26.93% | 19.88%
NQ | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 129.7486 | 190.074 | 128.5291 | 132.6542 | 194.4816 | 130.6664 | 135.78 | 199.3239 | 133.74 | 137.8958 | 202.6092 | 135.8564 | 143.2646 | 210.8615 | 141.1373
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 15.4091 | 22.3595 | 15.3097 | 15.5853 | 22.6242 | 15.4843 | 15.9384 | 23.15 | 15.8369 | 16.1829 | 23.52 | 16.0832 | 16.7834 | 24.4185 | 16.6851
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 15.3617 | 22.18 | 15.2633 | 15.5346 | 22.4359 | 15.4363 | 15.8826 | 22.9448 | 15.7842 | 16.1235 | 23.3019 | 16.027 | 16.7144 | 24.1695 | 16.6196
NQ | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.99692 | 0.99197 | 0.99697 | 0.99674 | 0.99168 | 0.9969 | 0.9965 | 0.99113 | 0.99667 | 0.99633 | 0.99073 | 0.9965 | 0.99589 | 0.9898 | 0.99607
NQ | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 6266_Bohle-Black River No 2 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | 6266_Bohle-Black River No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0389 | 1.029 | 1.0419 | 1.0277 | 1.0176 | 1.0366 | 1.0268 | 1.0159 | 1.0358 | 1.0266 | 1.0154 | 1.0356 | 1.0248 | 1.0129 | 1.0341
NQ | 6299_Townsville Port 66 kV | % of Rated A | 33.98% | 32.52% | 26.59% | 35.1% | 33.56% | 27.76% | 35.38% | 33.85% | 27.96% | 35.33% | 33.86% | 27.96% | 36.2% | 34.74% | 28.67%
NQ | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96490_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1
NQ | 6299_Townsville Port 66 kV | Loading (A) | 371.0987 | 391.9036 | 294.3249 | 383.2869 | 404.354 | 307.2688 | 386.308 | 407.9218 | 309.5667 | 385.7914 | 407.9549 | 309.5407 | 395.3415 | 418.6151 | 317.3836
NQ | 6299_Townsville Port 66 kV | Loading (MVA) | 44.8009 | 47.2364 | 35.4666 | 45.8931 | 48.3384 | 37.005 | 46.2378 | 48.7283 | 37.2724 | 46.1782 | 48.733 | 37.2694 | 47.2829 | 49.9599 | 38.1909
NQ | 6299_Townsville Port 66 kV | Loading (MW) | 44.7472 | 47.1593 | 35.2689 | 45.3137 | 47.7152 | 36.6898 | 45.6293 | 48.0902 | 36.9392 | 45.5749 | 48.0959 | 36.9385 | 46.6411 | 49.2748 | 37.8358
NQ | 6299_Townsville Port 66 kV | Power Factor | 0.9988 | 0.99837 | 0.99442 | 0.98737 | 0.98711 | 0.99148 | 0.98684 | 0.98691 | 0.99106 | 0.98694 | 0.98693 | 0.99112 | 0.98643 | 0.98629 | 0.9907
NQ | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
NQ | 6299_Townsville Port 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | 6299_Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 1.056 | 1.0543 | 1.0541 | 1.0473 | 1.0457 | 1.0534 | 1.0469 | 1.0449 | 1.0532 | 1.047 | 1.0449 | 1.0532 | 1.0461 | 1.0439 | 1.0526
NQ | 6312_Merinda - Home Hill 66 kV | % of Rated A | 5.904% | 5.374% | 5.294% | 5.903% | 5.373% | 5.294% | 5.91% | 5.392% | 5.294% | 5.909% | 5.39% | 5.294% | 5.904% | 5.385% | 5.294%
NQ | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1
NQ | 6312_Merinda - Home Hill 66 kV | Loading (A) | 14.5236 | 14.6698 | 13.8702 | 14.5224 | 14.6681 | 13.8703 | 14.5384 | 14.7202 | 13.8696 | 14.5363 | 14.7152 | 13.8697 | 14.5249 | 14.7008 | 13.8701
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 1.6777 | 1.6758 | 1.6145 | 1.6779 | 1.676 | 1.6148 | 1.6754 | 1.6685 | 1.6107 | 1.6758 | 1.6692 | 1.6112 | 1.6775 | 1.6712 | 1.6138
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 1.5405 | 1.5379 | 1.3122 | 1.5405 | 1.5379 | 1.3122 | 1.5405 | 1.538 | 1.3122 | 1.5405 | 1.538 | 1.3122 | 1.5405 | 1.538 | 1.3122
NQ | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.91822 | 0.91775 | 0.81273 | 0.91812 | 0.91761 | 0.81262 | 0.91948 | 0.92178 | 0.81468 | 0.9193 | 0.9214 | 0.81445 | 0.91833 | 0.92027 | 0.81311
NQ | 6312_Merinda - Home Hill 66 kV | Rating (A) | 246 | 273 | 262 | 246 | 273 | 262 | 246 | 273 | 262 | 246 | 273 | 262 | 246 | 273 | 262
NQ | 6312_Merinda - Home Hill 66 kV | Time | 16:30:00 | 19:00:00 | 23:00:00 | 16:30:00 | 19:00:00 | 23:00:00 | 16:30:00 | 19:00:00 | 23:00:00 | 16:30:00 | 19:00:00 | 23:00:00 | 16:30:00 | 19:00:00 | 23:00:00
NQ | 6312_Merinda - Home Hill 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0091 | 0.99785 | 1.0183 | 1.0093 | 0.99811 | 1.0184 | 1.0067 | 0.99009 | 1.0159 | 1.007 | 0.99083 | 1.0162 | 1.0089 | 0.99301 | 1.0178
NQ | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 57.42% | 60.72% | 47.51% | 59.93% | 63.74% | 47.92% | 59.34% | 63.34% | 47.27% | 59.13% | 63.27% | 47.15% | 60.64% | 65.03% | 48.44%
NQ | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 98272_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 98272_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 98272_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 98272_1 | TR_LINE 31738_1
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 186.6309 | 201.5771 | 139.2074 | 194.7777 | 211.6332 | 140.4096 | 192.8545 | 210.2859 | 138.5084 | 192.1787 | 210.0582 | 138.1571 | 197.0824 | 215.9061 | 141.9304
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 22.3984 | 24.1336 | 16.7232 | 23.2417 | 25.1606 | 16.8267 | 23.0038 | 24.9805 | 16.5947 | 22.9217 | 24.9515 | 16.5512 | 23.4873 | 25.6203 | 16.9925
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 21.8308 | 23.6953 | 16.2448 | 23.2405 | 25.16 | 16.7462 | 23.0036 | 24.9793 | 16.5269 | 22.9214 | 24.9503 | 16.4815 | 23.4873 | 25.6173 | 16.9296
NQ | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.97464 | 0.98182 | 0.97138 | 0.99995 | 0.99997 | 0.99521 | 0.99999 | 0.99995 | 0.99591 | 0.99999 | 0.99995 | 0.99579 | 1 | 0.99988 | 0.99629
NQ | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293
NQ | 6325_Oonoonba-Stuart 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | 6325_Oonoonba-Stuart 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0498 | 1.0472 | 1.0508 | 1.0437 | 1.0391 | 1.0483 | 1.0433 | 1.0382 | 1.048 | 1.0433 | 1.0382 | 1.0479 | 1.0424 | 1.0371 | 1.0473
NQ | 6382 JACR-HUGH 66kV | % of Rated A | 80.45% | 94.15% | 51.12% | 78.24% | 92.77% | 50.55% | 82.12% | 96.54% | 51.03% | 81.38% | 95.43% | 50.71% | 82.64% | 97.11% | 51.32%
NQ | 6382 JACR-HUGH 66kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ | 6382 JACR-HUGH 66kV | Loading (A) | 114.2352 | 133.6872 | 72.5871 | 111.1036 | 131.7381 | 71.7782 | 116.6095 | 137.0932 | 72.4579 | 115.5652 | 135.5099 | 72.0127 | 117.349 | 137.8992 | 72.8707
NQ | 6382 JACR-HUGH 66kV | Loading (MVA) | 13.2438 | 15.3731 | 8.5571 | 12.7837 | 15.2242 | 8.4752 | 13.4189 | 15.5504 | 8.4502 | 13.3492 | 15.469 | 8.4118 | 13.4874 | 15.6222 | 8.4945
NQ | 6382 JACR-HUGH 66kV | Loading (MW) | 12.9399 | 14.5919 | 8.4153 | 12.5579 | 14.4653 | 8.3227 | 13.0185 | 14.6241 | 8.3221 | 12.9636 | 14.5706 | 8.2753 | 13.0803 | 14.6873 | 8.3711
NQ | 6382 JACR-HUGH 66kV | Power Factor | 0.97705 | 0.94918 | 0.98344 | 0.98234 | 0.95015 | 0.98201 | 0.97016 | 0.94043 | 0.98485 | 0.97111 | 0.94192 | 0.98377 | 0.96982 | 0.94016 | 0.98548
NQ | 6382 JACR-HUGH 66kV | Rating (A) | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142
NQ | 6382 JACR-HUGH 66kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | 6382 JACR-HUGH 66kV | Min Voltage at Constrained Conductor (pu) | 0.99295 | 0.97857 | 1.0218 | 0.98611 | 0.98424 | 1.0237 | 0.98465 | 0.96349 | 1.0106 | 0.98882 | 0.97044 | 1.0124 | 0.98318 | 0.96198 | 1.01
NQ | 6383 CARI-CPRE 66kV | % of Rated A | 38.84% | 38.72% | 34.31% | 37.98% | 38.23% | 34.31% | 39.39% | 39.81% | 33.21% | 39.15% | 39.42% | 33.25% | 39.58% | 40.03% | 32.69%
NQ | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ | 6383 CARI-CPRE 66kV | Loading (A) | 121.1706 | 138.6323 | 112.8784 | 118.4831 | 136.8479 | 112.8712 | 122.8896 | 142.519 | 109.2719 | 122.1599 | 141.1217 | 109.3884 | 123.5042 | 143.3127 | 107.5339
NQ | 6383 CARI-CPRE 66kV | Loading (MVA) | 13.5333 | 15.0535 | 13.9336 | 13.2544 | 14.9141 | 13.9298 | 13.5078 | 15.1498 | 13.2845 | 13.4673 | 15.0753 | 13.3072 | 13.5643 | 15.2225 | 13.0816
NQ | 6383 CARI-CPRE 66kV | Loading (MW) | 13.2883 | 15.0505 | 4.6127 | 12.8885 | 14.9136 | 4.5469 | 13.3794 | 15.1082 | 4.8116 | 13.3205 | 15.0463 | 4.7798 | 13.4445 | 15.1762 | 5.1267
NQ | 6383 CARI-CPRE 66kV | Power Factor | 0.98189 | 0.9998 | 0.331 | 0.97238 | 0.99997 | 0.32637 | 0.99049 | 0.99725 | 0.36215 | 0.98909 | 0.99808 | 0.35914 | 0.99116 | 0.99696 | 0.39186
NQ | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 6383 CARI-CPRE 66kV | Time | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 05:30:00
NQ | 6383 CARI-CPRE 66kV | Min Voltage at Constrained Conductor (pu) | 0.97698 | 0.94981 | 1.0798 | 0.97856 | 0.95328 | 1.0796 | 0.96149 | 0.9298 | 1.0635 | 0.96433 | 0.9344 | 1.0642 | 0.9607 | 0.92909 | 1.0642
NQ | 7182 Ross - Milchester | % of Rated A | 52.23% | 48.25% | 42.68% | 52.16% | 48.21% | 42.64% | 58.93% | 54.4% | 47.28% | 58.76% | 54.17% | 47.2% | 59.16% | 54.61% | 47.44%
NQ | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 221851_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 221851_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 221851_1 | TR_LINE 76326_1
NQ | 7182 Ross - Milchester | Loading (A) | 162.9482 | 172.722 | 140.4296 | 162.7501 | 172.5907 | 140.272 | 183.8698 | 194.7689 | 155.5463 | 183.3159 | 193.9292 | 155.2725 | 184.5797 | 195.5097 | 156.0785
NQ | 7182 Ross - Milchester | Loading (MVA) | 38.296 | 40.2703 | 33.6851 | 38.2456 | 40.2446 | 33.6452 | 42.6981 | 44.259 | 36.9292 | 42.591 | 44.1134 | 36.8736 | 42.8506 | 44.4125 | 37.0493
NQ | 7182 Ross - Milchester | Loading (MW) | 38.0048 | 40.2454 | 31.0624 | 37.9487 | 40.2127 | 30.9883 | 42.6938 | 44.1489 | 35.6952 | 42.5829 | 44.0261 | 35.6091 | 42.8471 | 44.3006 | 35.8237
NQ | 7182 Ross - Milchester | Power Factor | 0.9924 | 0.99938 | 0.92214 | 0.99224 | 0.99921 | 0.92103 | 0.9999 | 0.99751 | 0.96658 | 0.99981 | 0.99802 | 0.96571 | 0.99992 | 0.99748 | 0.96692
NQ | 7182 Ross - Milchester | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 7182 Ross - Milchester | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | 7182 Ross - Milchester | Min Voltage at Constrained Conductor (pu) | 1.0209 | 1.0104 | 1.0482 | 1.0209 | 1.0107 | 1.0482 | 1.0053 | 0.99385 | 1.0345 | 1.006 | 0.99487 | 1.0348 | 1.005 | 0.99352 | 1.0343
NQ | 7460 CPRE-JACR 132kV | % of Rated A | 34.69% | 26.26% | 20.06% | 33.74% | 25.87% | 20.06% | 35.86% | 27.29% | 19.41% | 35.54% | 26.98% | 19.43% | 36.09% | 27.45% | 19.1%
NQ | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257 | TR_LINE 51339257 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257 | TR_LINE 51339257_1 | TR_LINE 51339257 | TR_LINE 51339257 | TR_LINE 51339257_1 | TR_LINE 51339257 | TR_LINE 51339257 | TR_LINE 51339257_1 | TR_LINE 51339257 | TR_LINE 51339257 | TR_LINE 51339257_1
NQ | 7460 CPRE-JACR 132kV | Loading (A) | 60.0142 | 72.9961 | 55.7571 | 58.3665 | 71.9304 | 55.7545 | 62.0403 | 75.8696 | 53.9694 | 61.4878 | 74.9935 | 54.0276 | 62.4332 | 76.3169 | 53.1048
NQ | 7460 CPRE-JACR 132kV | Loading (MVA) | 13.5046 | 15.5289 | 14.1306 | 13.2698 | 15.3763 | 14.1274 | 13.5282 | 15.7212 | 13.4653 | 13.4567 | 15.636 | 13.4888 | 13.5978 | 15.7946 | 13.2527
NQ | 7460 CPRE-JACR 132kV | Loading (MW) | 13.2368 | 14.9968 | 4.5596 | 12.8434 | 14.8602 | 4.4939 | 13.3287 | 15.055 | 4.7604 | 13.2697 | 14.9932 | 4.7285 | 13.3937 | 15.1228 | 5.0757
NQ | 7460 CPRE-JACR 132kV | Power Factor | 0.97331 | 0.94285 | 0.32268 | 0.96787 | 0.94398 | 0.3181 | 0.96581 | 0.93333 | 0.35353 | 0.96687 | 0.93502 | 0.35055 | 0.96542 | 0.933 | 0.38299
NQ | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
NQ | 7460 CPRE-JACR 132kV | Time | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 04:30:00 | 16:30:00 | 18:30:00 | 05:30:00
NQ | 7460 CPRE-JACR 132kV | Min Voltage at Constrained Conductor (pu) | 0.97248 | 0.93048 | 1.1085 | 0.9942 | 0.93499 | 1.1083 | 0.95375 | 0.90632 | 1.0913 | 0.95723 | 0.91194 | 1.092 | 0.95261 | 0.90522 | 1.0915
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 16.08% | 5.543% | 5.785% | 16.88% | 5.853% | 6.803% | 16.85% | 5.733% | 6.718% | 16.44% | 5.45% | 6.542% | 16.6% | 5.308% | 6.274%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 53.5463 | 21.6172 | 21.0009 | 56.2197 | 22.8285 | 24.6938 | 56.1085 | 22.3606 | 24.3867 | 54.7444 | 21.2545 | 23.7473 | 55.2909 | 20.7022 | 22.7731
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 6.4436 | 2.5808 | 2.53 | 6.7544 | 2.7025 | 2.9708 | 6.7404 | 2.6458 | 2.9334 | 6.5772 | 2.5149 | 2.8565 | 6.639 | 2.4465 | 2.7433
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 6.2418 | 1.0838 | 0.6832 | 6.078 | 1.1951 | 1.2971 | 6.0719 | 1.1176 | 1.267 | 5.9089 | 0.8935 | 1.1328 | 5.9737 | 0.85473 | 0.89477
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.96869 | 0.41994 | 0.27004 | 0.89981 | 0.44219 | 0.43659 | 0.90077 | 0.4224 | 0.43189 | 0.89833 | 0.35527 | 0.39654 | 0.89974 | 0.34934 | 0.32615
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 12:00:00 | 18:00:00 | 05:00:00 | 13:30:00 | 17:00:00 | 05:30:00 | 13:30:00 | 17:00:00 | 05:30:00 | 13:30:00 | 17:00:00 | 05:30:00 | 13:30:00 | 17:00:00 | 03:00:00
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0526 | 1.0443 | 1.0539 | 1.051 | 1.0356 | 1.0524 | 1.0509 | 1.0351 | 1.0522 | 1.051 | 1.0351 | 1.0522 | 1.0504 | 1.0338 | 1.0538
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 38.33% | 36.09% | 27.04% | 38.11% | 35.84% | 27.97% | 38.07% | 35.86% | 27.97% | 38.1% | 35.92% | 28.03% | 38.88% | 36.67% | 28.57%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 58723_1 | TR_LINE 58723_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 176.3343 | 186.2333 | 128.1888 | 175.3004 | 184.9599 | 132.5621 | 175.1009 | 185.018 | 132.5765 | 175.2791 | 185.3423 | 132.8752 | 178.8526 | 189.2014 | 135.4373
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 21.1291 | 22.2593 | 15.432 | 20.8124 | 21.9081 | 15.8692 | 20.7814 | 21.902 | 15.8669 | 20.8033 | 21.9402 | 15.9023 | 21.2051 | 22.3707 | 16.1963
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 21.0493 | 22.1656 | 15.3189 | 20.6681 | 21.7969 | 15.4883 | 20.6384 | 21.7919 | 15.4906 | 20.6606 | 21.8311 | 15.5288 | 21.0789 | 22.2698 | 15.8465
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.99623 | 0.99579 | 0.99265 | 0.993 | 0.99485 | 0.97594 | 0.99305 | 0.9949 | 0.97623 | 0.99307 | 0.99496 | 0.97645 | 0.99398 | 0.99542 | 0.97835
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.048 | 1.0454 | 1.0529 | 1.0383 | 1.0359 | 1.0471 | 1.038 | 1.0353 | 1.0468 | 1.038 | 1.0353 | 1.0468 | 1.0369 | 1.034 | 1.046
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 18.59% | 18.24% | 16.66% | 18.49% | 18.14% | 16.57% | 18.17% | 18.23% | 16.27% | 18.13% | 18.15% | 16.22% | 19.56% | 20.28% | 17.57%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 50.9258 | 53.9905 | 45.6391 | 50.6739 | 53.7029 | 45.414 | 49.7882 | 53.9616 | 44.5917 | 49.6636 | 53.7267 | 44.4452 | 53.5964 | 60.0297 | 48.1504
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 5.7755 | 6.0582 | 5.2079 | 5.7478 | 6.0276 | 5.1829 | 5.7066 | 6.0046 | 5.142 | 5.6938 | 5.9833 | 5.1264 | 6.1542 | 6.7037 | 5.5614
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 3.4128 | 3.3174 | 3.0972 | 3.389 | 3.2906 | 3.0756 | 3.3554 | 3.2342 | 3.0425 | 3.3194 | 3.1716 | 3.0023 | 3.3532 | 3.2109 | 3.0471
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.59044 | 0.54708 | 0.59431 | 0.58915 | 0.54542 | 0.59301 | 0.58753 | 0.53811 | 0.5913 | 0.58254 | 0.52957 | 0.58526 | 0.54438 | 0.47842 | 0.54746
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 274 | 296 | 274 | 274 | 296 | 274 | 274 | 296 | 274 | 274 | 296 | 274 | 274 | 296 | 274
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 07:00:00 | 19:30:00 | 05:30:00 | 07:00:00 | 19:30:00 | 05:30:00 | 07:00:00 | 19:30:00 | 05:30:00 | 07:00:00 | 19:30:00 | 05:30:00 | 07:00:00 | 19:30:00 | 05:30:00
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99209 | 0.98158 | 0.9982 | 0.99223 | 0.98184 | 0.99833 | 1.0026 | 0.97341 | 1.0087 | 1.0029 | 0.97419 | 1.009 | 1.0045 | 0.97689 | 1.0104
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 46.4% | 48.78% | 38.38% | 46.36% | 48.74% | 38.37% | 46.53% | 49.19% | 38.47% | 46.21% | 48.85% | 38.18% | 46.5% | 49% | 38.63%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 119.7097 | 143.8929 | 104.3982 | 119.6054 | 143.7975 | 104.3628 | 120.0566 | 145.1208 | 104.6503 | 119.2267 | 144.0988 | 103.8498 | 119.9791 | 144.547 | 105.0633
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 13.7149 | 16.2732 | 12.0368 | 13.7058 | 16.2663 | 12.0349 | 13.7215 | 16.2772 | 12.0406 | 13.6319 | 16.1752 | 11.9526 | 13.7504 | 16.2688 | 12.1105
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 13.4603 | 15.78 | 11.853 | 13.453 | 15.7752 | 11.8519 | 13.4659 | 15.7867 | 11.856 | 13.3745 | 15.6821 | 11.7666 | 13.6381 | 15.9756 | 12.0209
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.98144 | 0.96969 | 0.98473 | 0.98156 | 0.96981 | 0.9848 | 0.98137 | 0.96986 | 0.98466 | 0.98112 | 0.96952 | 0.98444 | 0.99183 | 0.98198 | 0.9926
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0021 | 0.98922 | 1.0085 | 1.0024 | 0.98947 | 1.0087 | 0.99974 | 0.9811 | 1.0064 | 1.0001 | 0.98186 | 1.0068 | 1.0025 | 0.98448 | 1.0083
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 29.37% | 36.59% | 28% | 29.7% | 37.01% | 28.15% | 30.08% | 37.51% | 28.5% | 30.08% | 37.53% | 28.5% | 30.81% | 38.49% | 29.2%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 55.5173 | 75.3769 | 52.0874 | 56.1381 | 76.2463 | 52.3611 | 56.8438 | 77.2672 | 53.0041 | 56.8579 | 77.3054 | 53.0185 | 58.2336 | 79.2931 | 54.316
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 6.5661 | 8.818 | 6.1805 | 6.5677 | 8.8198 | 6.1808 | 6.6439 | 8.9235 | 6.2518 | 6.6439 | 8.9236 | 6.2518 | 6.7919 | 9.1296 | 6.3951
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 6.5593 | 8.7899 | 6.1757 | 6.5601 | 8.791 | 6.1758 | 6.6357 | 8.8929 | 6.2463 | 6.6357 | 8.893 | 6.2463 | 6.7824 | 9.0958 | 6.3887
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.99895 | 0.99681 | 0.9992 | 0.99884 | 0.99672 | 0.99918 | 0.99876 | 0.99656 | 0.99912 | 0.99876 | 0.99655 | 0.99912 | 0.9986 | 0.99629 | 0.99898
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0345 | 1.0232 | 1.0378 | 1.0233 | 1.0117 | 1.0325 | 1.0223 | 1.0101 | 1.0317 | 1.022 | 1.0096 | 1.0314 | 1.0201 | 1.007 | 1.0298
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 7.863% | 8.914% | 7.131% | 7.983% | 9.06% | 7.196% | 8.028% | 9.116% | 7.235% | 8.028% | 9.116% | 7.235% | 8.25% | 9.379% | 7.426%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Limiting Line Name | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 62.4293 | 70.778 | 56.6199 | 63.3854 | 71.9353 | 57.1385 | 63.7433 | 72.3815 | 57.4447 | 63.7415 | 72.3846 | 57.4454 | 65.5034 | 74.466 | 58.9629
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MVA) | 7.5078 | 8.4928 | 6.8162 | 7.5254 | 8.5208 | 6.8401 | 7.5652 | 8.5669 | 6.875 | 7.5653 | 8.5669 | 6.875 | 7.7662 | 8.8022 | 7.0511
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MW) | 7.2026 | 8.265 | 6.4431 | 7.2452 | 8.3142 | 6.4816 | 7.2888 | 8.3643 | 6.5206 | 7.2888 | 8.3643 | 6.5206 | 7.507 | 8.615 | 6.7156
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 0.95934 | 0.97317 | 0.94526 | 0.96276 | 0.97575 | 0.94758 | 0.96346 | 0.97634 | 0.94845 | 0.96345 | 0.97635 | 0.94845 | 0.96663 | 0.97874 | 0.95242
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.052 | 1.0496 | 1.0531 | 1.0385 | 1.0361 | 1.0472 | 1.0382 | 1.0353 | 1.0469 | 1.0382 | 1.0353 | 1.0469 | 1.0371 | 1.034 | 1.0461
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 7.855% | 8.907% | 7.123% | 7.976% | 9.053% | 7.188% | 8.021% | 9.109% | 7.227% | 8.021% | 9.109% | 7.227% | 8.243% | 9.372% | 7.418%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Limiting Line Name | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 62.3693 | 70.7212 | 56.5566 | 63.3269 | 71.8799 | 57.076 | 63.6851 | 72.3262 | 57.3824 | 63.6832 | 72.3293 | 57.3832 | 65.4459 | 74.4112 | 58.9016
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MVA) | 7.5006 | 8.486 | 6.8086 | 7.5184 | 8.5142 | 6.8326 | 7.5583 | 8.5604 | 6.8676 | 7.5584 | 8.5603 | 6.8675 | 7.7594 | 8.7957 | 7.0438
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MW) | 7.1992 | 8.2612 | 6.4401 | 7.2418 | 8.3104 | 6.4786 | 7.2854 | 8.3605 | 6.5175 | 7.2854 | 8.3605 | 6.5175 | 7.5036 | 8.6111 | 6.7125
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 0.95982 | 0.9735 | 0.94588 | 0.96321 | 0.97606 | 0.94818 | 0.9639 | 0.97664 | 0.94903 | 0.96389 | 0.97665 | 0.94903 | 0.96703 | 0.97902 | 0.95297
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.052 | 1.0496 | 1.0531 | 1.0385 | 1.0361 | 1.0472 | 1.0382 | 1.0353 | 1.0469 | 1.0382 | 1.0353 | 1.0469 | 1.0371 | 1.034 | 1.0461
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 50.79% | 62.28% | 44.77% | 53.93% | 66.15% | 46.07% | 55.26% | 67.93% | 47.25% | 55.49% | 68.41% | 47.53% | 57.33% | 70.9% | 49.15%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 227.0224 | 278.3901 | 200.1243 | 241.0655 | 295.6702 | 205.942 | 247.0179 | 303.6252 | 211.2041 | 248.0599 | 305.7893 | 212.474 | 256.2429 | 316.9193 | 219.7102
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 27.2016 | 33.1828 | 24.0472 | 28.652 | 34.9538 | 24.6456 | 29.344 | 35.8571 | 25.265 | 29.4642 | 36.1037 | 25.4131 | 30.3993 | 37.3598 | 26.2541
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 27.175 | 33.016 | 23.9344 | 28.1384 | 34.1389 | 24.3275 | 28.8006 | 34.9834 | 24.9249 | 28.9149 | 35.2094 | 25.0671 | 29.8078 | 36.3838 | 25.8834
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.99875 | 0.99472 | 0.99502 | 0.98181 | 0.97643 | 0.98681 | 0.98122 | 0.97538 | 0.98626 | 0.98109 | 0.97497 | 0.9861 | 0.98028 | 0.97362 | 0.98561
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0481 | 1.0427 | 1.0511 | 1.0397 | 1.0341 | 1.0469 | 1.0392 | 1.0331 | 1.0464 | 1.039 | 1.0328 | 1.0463 | 1.0378 | 1.0312 | 1.0453
NQ | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 73.25% | 62.76% | 61.06% | 73.22% | 62.7% | 61% | 112.8% | 95.69% | 97.09% | 112.6% | 95.48% | 97% | 113.2% | 96.01% | 97.33%
NQ | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 188.9746 | 185.1285 | 166.0796 | 188.9112 | 184.9732 | 165.9181 | 291.0338 | 282.2928 | 264.0964 | 290.4262 | 281.6663 | 263.8342 | 291.9328 | 283.2293 | 264.7262
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 22.5438 | 22.0162 | 19.8393 | 22.5371 | 21.9939 | 19.8207 | 34.5976 | 33.2934 | 31.4482 | 34.5291 | 33.2326 | 31.4194 | 34.7334 | 33.4499 | 31.5412
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 22.5001 | 21.9642 | 19.7962 | 22.494 | 21.9376 | 19.7775 | 34.4605 | 33.1829 | 31.3343 | 34.399 | 33.1287 | 31.3087 | 34.5909 | 33.333 | 31.4248
NQ | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.99806 | 0.99763 | 0.99782 | 0.99808 | 0.99744 | 0.99781 | 0.99604 | 0.99668 | 0.99638 | 0.99623 | 0.99687 | 0.99648 | 0.9959 | 0.99651 | 0.99631
NQ | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | CHTO_Clare South - Charters Towers 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00
NQ | CHTO_Clare South - Charters Towers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0435 | 1.0403 | 1.0449 | 1.0435 | 1.0401 | 1.045 | 1.0169 | 1.0095 | 1.0209 | 1.0171 | 1.0101 | 1.021 | 1.0176 | 1.0108 | 1.0214
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 35.9% | 37.3% | 29.99% | 35.77% | 37.17% | 29.88% | 35.89% | 37.5% | 29.96% | 35.64% | 37.21% | 29.74% | 35.78% | 37.33% | 29.96%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 112.0219 | 135.3886 | 101.0674 | 111.607 | 134.9294 | 100.7063 | 111.9783 | 136.1231 | 100.9685 | 111.189 | 135.0894 | 100.2139 | 111.6317 | 135.5165 | 100.9595
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 12.9534 | 15.4779 | 11.7446 | 12.9079 | 15.4251 | 11.7046 | 12.9178 | 15.4343 | 11.709 | 12.8309 | 15.3287 | 11.6248 | 12.9055 | 15.4099 | 11.7249
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 12.5087 | 14.7935 | 11.3823 | 12.468 | 14.7465 | 11.3462 | 12.4746 | 14.753 | 11.3482 | 12.3903 | 14.6513 | 11.2665 | 12.5747 | 14.8653 | 11.4414
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.96565 | 0.95578 | 0.96907 | 0.9659 | 0.956 | 0.9693 | 0.96566 | 0.95586 | 0.96912 | 0.96563 | 0.95581 | 0.96911 | 0.97435 | 0.96466 | 0.97576
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0109 | 0.99919 | 1.016 | 1.0111 | 0.99918 | 1.0162 | 1.0085 | 0.99098 | 1.0139 | 1.0089 | 0.99175 | 1.0142 | 1.0107 | 0.99386 | 1.0154
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 63.52% | 54.31% | 41.56% | 63.29% | 54.12% | 41.41% | 63.5% | 54.6% | 41.52% | 63.05% | 54.19% | 41.21% | 63.32% | 54.37% | 41.53%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 107.3551 | 129.7932 | 96.8337 | 106.9569 | 129.3523 | 96.4874 | 107.314 | 130.5027 | 96.7394 | 106.5549 | 129.5083 | 96.0137 | 107.0135 | 129.9469 | 96.7571
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 12.5453 | 15.0427 | 11.3563 | 12.5004 | 14.9904 | 11.3171 | 12.5112 | 15.0041 | 11.322 | 12.4256 | 14.8991 | 11.2394 | 12.4985 | 14.9762 | 11.3383
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 12.2781 | 14.5848 | 11.1515 | 12.237 | 14.5372 | 11.1151 | 12.2449 | 14.5471 | 11.1181 | 12.1613 | 14.4455 | 11.0373 | 12.3161 | 14.6281 | 11.1904
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.97861 | 0.96956 | 0.98166 | 0.97882 | 0.96977 | 0.98184 | 0.97862 | 0.96954 | 0.98168 | 0.97862 | 0.96955 | 0.9817 | 0.98535 | 0.97676 | 0.98671
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0178 | 1.008 | 1.0222 | 1.018 | 1.0079 | 1.0223 | 1.0155 | 0.9998 | 1.0201 | 1.0157 | 1.0005 | 1.0203 | 1.0173 | 1.0023 | 1.0213
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 38.55% | 29.13% | 19.5% | 37.24% | 29.09% | 19.36% | 39.48% | 30.03% | 19.39% | 39.48% | 30.12% | 19.33% | 39.55% | 30.06% | 19.46%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 55.1226 | 61.7611 | 40.746 | 53.2498 | 61.6671 | 40.4685 | 56.46 | 63.6595 | 40.5265 | 56.4634 | 63.8583 | 40.3962 | 56.5634 | 63.7175 | 40.6735
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 6.1565 | 6.7211 | 4.8013 | 5.9569 | 6.7368 | 4.7743 | 6.206 | 6.8847 | 4.7261 | 6.2247 | 6.9352 | 4.717 | 6.2123 | 6.8872 | 4.742
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 4.2056 | 4.2014 | 3.8994 | 4.3719 | 4.0945 | 3.8507 | 3.9689 | 3.7839 | 3.8623 | 3.916 | 3.712 | 3.836 | 4.0089 | 3.8253 | 3.8879
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.68311 | 0.62511 | 0.81217 | 0.73391 | 0.60779 | 0.80655 | 0.63953 | 0.54961 | 0.81724 | 0.62911 | 0.53524 | 0.81323 | 0.64532 | 0.55543 | 0.81989
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97701 | 0.95196 | 1.0308 | 0.97859 | 0.95565 | 1.032 | 0.96153 | 0.94605 | 1.0201 | 0.96438 | 0.95003 | 1.0215 | 0.96075 | 0.94553 | 1.0199
NQ | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 43.63% | 40.2% | 41.7% | 43.63% | 40.21% | 41.7% | 43.75% | 40.52% | 41.42% | 43.74% | 40.5% | 41.42% | 44.18% | 40.89% | 42.26%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 85.0833 | 87.6358 | 82.9768 | 85.0793 | 87.6537 | 82.9767 | 85.3114 | 88.3364 | 82.4237 | 85.3019 | 88.292 | 82.4193 | 86.1603 | 89.1441 | 84.1046
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 10.0048 | 10.268 | 9.6867 | 10.0048 | 10.2682 | 9.6867 | 10.0079 | 10.2683 | 9.6013 | 10.0078 | 10.2677 | 9.6013 | 10.1147 | 10.3758 | 9.7974
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 8.3306 | 8.5436 | 8.0504 | 8.3306 | 8.5436 | 8.0504 | 8.3309 | 8.5439 | 7.9816 | 8.3309 | 8.5438 | 7.9816 | 8.4136 | 8.6277 | 8.1338
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.83262 | 0.83203 | 0.83104 | 0.83262 | 0.83201 | 0.83104 | 0.8324 | 0.83204 | 0.83126 | 0.83241 | 0.83208 | 0.83126 | 0.83179 | 0.83149 | 0.83016
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Time | 16:30:00 | 18:30:00 | 01:30:00 | 16:30:00 | 18:30:00 | 01:30:00 | 16:30:00 | 18:30:00 | 03:00:00 | 16:30:00 | 18:30:00 | 03:00:00 | 16:30:00 | 18:30:00 | 01:30:00
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0286 | 1.0249 | 1.0212 | 1.0286 | 1.0247 | 1.0212 | 1.0261 | 1.0168 | 1.019 | 1.0263 | 1.0172 | 1.019 | 1.0269 | 1.0181 | 1.019
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 41.91% | 41.05% | 38.08% | 41.5% | 40.66% | 38% | 41.33% | 40.7% | 37.46% | 41.21% | 40.46% | 37.46% | 41.36% | 40.73% | 37.48%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 77.1162 | 82.0946 | 68.5525 | 76.3633 | 81.3172 | 68.4032 | 76.0411 | 81.3918 | 67.4348 | 75.8296 | 80.9128 | 67.4352 | 76.0976 | 81.4636 | 67.4552
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 8.9397 | 9.4709 | 8.0351 | 8.8521 | 9.3883 | 8.0188 | 8.6852 | 9.2169 | 7.8156 | 8.6718 | 9.1809 | 7.8202 | 8.6877 | 9.2217 | 7.8164
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 7.7583 | 8.7884 | 5.2181 | 7.6344 | 8.6437 | 5.1479 | 7.5734 | 8.656 | 5.0242 | 7.5091 | 8.5637 | 4.9882 | 7.5861 | 8.6684 | 5.0283
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.86785 | 0.92794 | 0.64939 | 0.86244 | 0.92069 | 0.64194 | 0.87198 | 0.93914 | 0.64282 | 0.86593 | 0.93277 | 0.63782 | 0.8732 | 0.93999 | 0.64327
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0138 | 1.0087 | 1.0253 | 1.0138 | 1.0095 | 1.0255 | 0.99883 | 0.99009 | 1.0138 | 1.0001 | 0.99209 | 1.0144 | 0.99837 | 0.98974 | 1.0136
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 38.5% | 37.46% | 26.42% | 38.83% | 37.75% | 26.44% | 54.51% | 51.08% | 41.63% | 54.29% | 50.84% | 41.47% | 54.6% | 51.09% | 41.74%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 107.0426 | 116.5132 | 75.0293 | 107.9452 | 117.3914 | 75.1038 | 151.5273 | 158.844 | 118.2181 | 150.9399 | 158.1125 | 117.7619 | 151.7774 | 158.8962 | 118.531
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 12.4096 | 13.4856 | 8.7944 | 12.5139 | 13.5922 | 8.8045 | 17.3091 | 17.9899 | 13.7023 | 17.2633 | 17.9428 | 13.6574 | 17.3297 | 17.9894 | 13.7358
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 11.0493 | 11.7548 | 8.4848 | 11.1379 | 11.8477 | 8.4916 | 15.5107 | 15.7981 | 12.9486 | 15.4663 | 15.7579 | 12.9046 | 15.5565 | 15.837 | 12.9966
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.89037 | 0.87165 | 0.96477 | 0.89003 | 0.87165 | 0.96445 | 0.8961 | 0.87816 | 0.945 | 0.89591 | 0.87823 | 0.94488 | 0.89768 | 0.88035 | 0.94619
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0141 | 1.0124 | 1.0253 | 1.014 | 1.0128 | 1.0255 | 0.99915 | 0.9906 | 1.0138 | 1.0004 | 0.99258 | 1.0144 | 0.99869 | 0.99025 | 1.0136
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 41.79% | 38.23% | 28.83% | 42.38% | 38.73% | 28.06% | 42.08% | 38.43% | 27.8% | 41.48% | 37.85% | 27.34% | 42.05% | 38.36% | 27.66%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126334_1 | TR_LINE 126334_1 | TR_LINE 126322_1 | TR_LINE 126334_1 | TR_LINE 126334_1 | TR_LINE 126322_1 | TR_LINE 126334_1 | TR_LINE 126334_1 | TR_LINE 126322_1 | TR_LINE 126334_1 | TR_LINE 126334_1 | TR_LINE 126322_1
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 188.8855 | 181.9583 | 123.0948 | 191.571 | 184.338 | 119.8132 | 190.2175 | 182.9323 | 118.7205 | 187.5057 | 180.1858 | 116.744 | 190.0542 | 182.573 | 118.1206
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 22.6404 | 21.7769 | 14.8075 | 22.7446 | 21.8515 | 14.3513 | 22.5752 | 21.6737 | 14.2162 | 22.2528 | 21.3473 | 13.9784 | 22.5291 | 21.6037 | 14.1311
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 22.4485 | 21.5622 | 14.642 | 22.6869 | 21.8001 | 14.341 | 22.5209 | 21.6251 | 14.2041 | 22.2027 | 21.303 | 13.9641 | 22.4741 | 21.557 | 14.1186
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.99148 | 0.99009 | 0.98881 | 0.99746 | 0.99765 | 0.99929 | 0.9976 | 0.99776 | 0.99915 | 0.99775 | 0.99793 | 0.99897 | 0.99756 | 0.99784 | 0.99911
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0483 | 1.0468 | 1.0522 | 1.0383 | 1.0367 | 1.0476 | 1.0379 | 1.0362 | 1.0473 | 1.0379 | 1.0362 | 1.0473 | 1.0367 | 1.0349 | 1.0464
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 26.4% | 24.08% | 25.89% | 26.21% | 23.83% | 25.45% | 26.72% | 24.41% | 26% | 26.85% | 24.49% | 26.11% | 27.83% | 25.39% | 27.03%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 145.4401 | 140.1397 | 135.6866 | 144.424 | 138.6852 | 133.3538 | 147.2044 | 142.0819 | 136.2458 | 147.9212 | 142.5416 | 136.8195 | 153.3538 | 147.7929 | 141.6447
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 17.4085 | 16.7063 | 16.2495 | 17.1717 | 16.4197 | 15.9167 | 17.4972 | 16.8109 | 16.2559 | 17.5806 | 16.8626 | 16.3217 | 18.2053 | 17.4601 | 16.8801
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 15.8551 | 15.1101 | 14.5646 | 15.9541 | 15.1794 | 14.5806 | 16.3349 | 15.5857 | 14.9661 | 16.3995 | 15.6211 | 15.014 | 16.9756 | 16.1731 | 15.5242
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.91076 | 0.90446 | 0.89631 | 0.92909 | 0.92447 | 0.91606 | 0.93357 | 0.92712 | 0.92066 | 0.93282 | 0.92637 | 0.91988 | 0.93246 | 0.92629 | 0.91967
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00 | 16:00:00 | 17:00:00 | 22:00:00
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Min Voltage at Constrained Conductor (pu) | 1.047 | 1.0428 | 1.0476 | 1.04 | 1.0356 | 1.044 | 1.0397 | 1.035 | 1.0437 | 1.0396 | 1.0348 | 1.0435 | 1.0384 | 1.0334 | 1.0424
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 32.79% | 27.92% | 21.93% | 32.91% | 27.99% | 21.83% | 33.5% | 28.34% | 22.19% | 33.17% | 28.03% | 21.98% | 33.74% | 28.51% | 22.35%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 82.2967 | 107.5084 | 83.3315 | 82.6056 | 107.7789 | 82.9663 | 84.0906 | 109.1111 | 84.3121 | 83.2493 | 107.8997 | 83.5161 | 84.6786 | 109.7713 | 84.9155
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 9.8825 | 12.8546 | 10.0349 | 9.8491 | 12.7942 | 9.954 | 10.0219 | 12.942 | 10.1121 | 9.9206 | 12.7958 | 10.0154 | 10.0801 | 13.0006 | 10.1748
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 9.7699 | 12.6792 | 9.8921 | 9.7976 | 12.6883 | 9.8787 | 9.9765 | 12.8375 | 10.0447 | 9.8758 | 12.6944 | 9.9486 | 10.0341 | 12.8967 | 10.106
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.9886 | 0.98636 | 0.98577 | 0.99477 | 0.99172 | 0.99244 | 0.99547 | 0.99193 | 0.99334 | 0.99549 | 0.99207 | 0.99333 | 0.99544 | 0.99201 | 0.99323
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0505 | 1.0459 | 1.0534 | 1.043 | 1.0384 | 1.0495 | 1.0426 | 1.0376 | 1.0492 | 1.0424 | 1.0374 | 1.049 | 1.0413 | 1.036 | 1.0482
NQ | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 61.94% | 49.39% | 37.16% | 61.77% | 49.27% | 37.06% | 62.01% | 49.73% | 37.17% | 61.61% | 49.38% | 36.91% | 61.93% | 49.56% | 37.25%
NQ | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 130.0838 | 155.5781 | 115.1859 | 129.7273 | 155.2109 | 114.8913 | 130.2277 | 156.6513 | 115.2392 | 129.3755 | 155.541 | 114.4239 | 130.0521 | 156.1139 | 115.4683
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 14.9625 | 17.671 | 13.3341 | 14.9242 | 17.6286 | 13.302 | 14.9427 | 17.6444 | 13.312 | 14.85 | 17.5332 | 13.2218 | 14.9677 | 17.652 | 13.3659
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 14.3781 | 16.7877 | 12.8753 | 14.3448 | 16.7508 | 12.8471 | 14.3583 | 16.7661 | 12.8538 | 14.2683 | 16.6586 | 12.7662 | 14.5813 | 17.015 | 13.0427
NQ | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.96094 | 0.95001 | 0.9656 | 0.96118 | 0.95021 | 0.9658 | 0.96089 | 0.95022 | 0.96558 | 0.96083 | 0.95012 | 0.96554 | 0.97418 | 0.96392 | 0.97582
NQ | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | EAAY_Clare South - East Ayr 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | EAAY_Clare South - East Ayr 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0061 | 0.99343 | 1.0126 | 1.0062 | 0.9934 | 1.0127 | 1.0036 | 0.98514 | 1.0104 | 1.004 | 0.98592 | 1.0107 | 1.0067 | 0.98896 | 1.0125
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 37.74% | 51.31% | 38.26% | 38.15% | 51.9% | 39.64% | 39.47% | 53.59% | 40.89% | 40.19% | 54.51% | 41.58% | 41.82% | 56.71% | 43.18%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 207.9489 | 298.6115 | 200.4606 | 210.2026 | 302.072 | 207.6889 | 217.4836 | 311.9073 | 214.2644 | 221.4415 | 317.2387 | 217.8579 | 230.4195 | 330.0363 | 226.2766
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 24.7665 | 35.2973 | 23.9446 | 24.7693 | 35.3171 | 24.6822 | 25.607 | 36.4149 | 25.4474 | 26.0685 | 37.0238 | 25.869 | 27.0827 | 38.4364 | 26.8358
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 24.2893 | 34.5053 | 23.8257 | 24.7339 | 35.0868 | 24.6521 | 25.557 | 36.1459 | 25.4059 | 26.0122 | 36.7355 | 25.8223 | 27.007 | 38.0932 | 26.7764
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.98073 | 0.97756 | 0.99503 | 0.99857 | 0.99348 | 0.99878 | 0.99805 | 0.99261 | 0.99837 | 0.99784 | 0.99221 | 0.9982 | 0.9972 | 0.99107 | 0.99778
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0418 | 1.034 | 1.0449 | 1.0308 | 1.0227 | 1.0396 | 1.0299 | 1.0212 | 1.0389 | 1.0298 | 1.0209 | 1.0387 | 1.0281 | 1.0187 | 1.0374
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 49.83% | 48.45% | 40.66% | 41.38% | 40.57% | 36.04% | 41.62% | 40.91% | 36.31% | 41.54% | 40.74% | 36.23% | 42.19% | 41.38% | 36.75%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 171.9161 | 173.9319 | 130.1266 | 142.7662 | 145.6554 | 115.3239 | 143.5852 | 146.8811 | 116.1797 | 143.3221 | 146.2437 | 115.9402 | 145.5462 | 148.5395 | 117.6143
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 20.6334 | 20.8281 | 15.6806 | 16.9224 | 17.2245 | 13.7868 | 17.0135 | 17.3564 | 13.8857 | 16.983 | 17.2803 | 13.8568 | 17.2281 | 17.5292 | 14.0457
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 15.3176 | 15.7356 | 10.5004 | 14.2939 | 14.7434 | 11.6431 | 14.5118 | 15.0416 | 11.8622 | 14.4822 | 14.9849 | 11.8426 | 14.718 | 15.2105 | 12.0215
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.74237 | 0.7555 | 0.66955 | 0.84468 | 0.85596 | 0.84446 | 0.85295 | 0.86663 | 0.85423 | 0.85274 | 0.86717 | 0.8546 | 0.8543 | 0.86772 | 0.85584
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 16:30:00 | 17:30:00 | 01:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0493 | 1.0469 | 1.0538 | 1.0365 | 1.034 | 1.0455 | 1.0361 | 1.0332 | 1.0452 | 1.0361 | 1.0332 | 1.0452 | 1.035 | 1.0319 | 1.0444
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 40.7% | 26.77% | 18.75% | 44.57% | 29.58% | 20.52% | 46.31% | 30.74% | 21.29% | 46.05% | 30.57% | 21.18% | 46.83% | 31.1% | 21.54%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 68.781 | 63.9784 | 43.6837 | 75.3272 | 70.6904 | 47.8115 | 78.257 | 73.4618 | 49.6169 | 77.8232 | 73.063 | 49.3528 | 79.1397 | 74.3393 | 50.1869
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 8.2772 | 7.6833 | 5.2576 | 9.0297 | 8.3797 | 5.7219 | 9.3801 | 8.7037 | 5.9364 | 9.3294 | 8.6567 | 5.9047 | 9.4817 | 8.798 | 5.9997
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 8.2761 | 7.6832 | 5.248 | 9.0217 | 8.375 | 5.7194 | 9.3643 | 8.693 | 5.9359 | 9.3141 | 8.6464 | 5.9041 | 9.4648 | 8.7863 | 5.9994
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.99987 | 0.99998 | 0.99819 | 0.99911 | 0.99944 | 0.99955 | 0.99831 | 0.99876 | 0.99992 | 0.99836 | 0.9988 | 0.99991 | 0.99821 | 0.99867 | 0.99995
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0505 | 1.0528 | 1.0486 | 1.0369 | 1.0469 | 1.0485 | 1.0364 | 1.0466 | 1.0486 | 1.0364 | 1.0466 | 1.048 | 1.0353 | 1.0458
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 42.05% | 43.18% | 31.13% | 46.19% | 47.34% | 32.15% | 45.55% | 46.99% | 31.66% | 45.72% | 47.32% | 31.88% | 46.89% | 48.71% | 32.79%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 108.4936 | 127.3838 | 84.6806 | 119.1617 | 139.6523 | 87.4421 | 117.514 | 138.6104 | 86.1249 | 117.9472 | 139.5858 | 86.7112 | 120.9678 | 143.6879 | 89.1918
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 13.092 | 15.3436 | 10.2053 | 14.1559 | 16.5448 | 10.4714 | 13.9551 | 16.4095 | 10.3108 | 14.0071 | 16.5244 | 10.3809 | 14.351 | 16.989 | 10.6698
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 12.9313 | 15.2565 | 9.3039 | 13.4882 | 15.8707 | 10.0696 | 13.2381 | 15.7225 | 9.8656 | 13.3002 | 15.8404 | 9.9429 | 13.6176 | 16.2682 | 10.2172
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.98772 | 0.99432 | 0.91167 | 0.95282 | 0.95925 | 0.96154 | 0.94861 | 0.95813 | 0.95671 | 0.94952 | 0.95861 | 0.9577 | 0.94889 | 0.95757 | 0.95749
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0555 | 1.0536 | 1.0542 | 1.0387 | 1.0357 | 1.0473 | 1.0383 | 1.035 | 1.047 | 1.0384 | 1.0349 | 1.047 | 1.0373 | 1.0336 | 1.0462
NQ | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 17.1% | 18.25% | 16.65% | 17.1% | 18.25% | 16.64% | 17.15% | 18.43% | 16.69% | 16.74% | 17.97% | 16.29% | 17.61% | 18.88% | 17.16%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 32.3278 | 37.6043 | 30.9639 | 32.3194 | 37.6039 | 30.9573 | 32.4165 | 37.9653 | 31.0379 | 31.6365 | 37.014 | 30.2983 | 33.2811 | 38.8874 | 31.9162
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 3.6493 | 4.1735 | 3.5216 | 3.6492 | 4.1735 | 3.5215 | 3.6503 | 4.1769 | 3.5224 | 3.5643 | 4.0764 | 3.4401 | 3.758 | 4.2937 | 3.6285
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 3.3875 | 3.851 | 3.2751 | 3.3875 | 3.851 | 3.2751 | 3.3876 | 3.8512 | 3.2752 | 3.2747 | 3.7177 | 3.1675 | 3.5156 | 3.9913 | 3.4006
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.92824 | 0.9227 | 0.92999 | 0.92826 | 0.9227 | 0.93001 | 0.92801 | 0.92201 | 0.92978 | 0.91872 | 0.91199 | 0.92073 | 0.9355 | 0.92955 | 0.93716
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98749 | 0.97086 | 0.9949 | 0.98772 | 0.97087 | 0.99509 | 0.98505 | 0.96241 | 0.99277 | 0.98556 | 0.9634 | 0.99323 | 0.98776 | 0.96586 | 0.99452
NQ | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 21.03% | 19.95% | 22.48% | 16.13% | 14.71% | 10.47% | 15.29% | 13.92% | 9.693% | 14.94% | 13.61% | 9.565% | 15.08% | 13.74% | 9.632%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 72.5699 | 70.624 | 70.1348 | 55.6415 | 52.0721 | 32.6637 | 52.7614 | 49.2594 | 30.2424 | 51.5348 | 48.1813 | 29.8414 | 52.0269 | 48.6543 | 30.0533
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 8.6688 | 8.4264 | 8.4088 | 6.5851 | 6.155 | 3.8951 | 6.2419 | 5.8193 | 3.6054 | 6.0967 | 5.6918 | 3.5574 | 6.1482 | 5.741 | 3.5797
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 5.4267 | 4.9573 | 0.4007 | 6.2368 | 5.7594 | 2.5131 | 5.9204 | 5.4293 | 2.2264 | 5.7562 | 5.2794 | 2.1115 | 5.8121 | 5.337 | 2.1337
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.626 | 0.58831 | 0.047523 | 0.94711 | 0.93573 | 0.64518 | 0.94849 | 0.93299 | 0.61751 | 0.94416 | 0.92754 | 0.59354 | 0.94534 | 0.92962 | 0.59606
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Time | 16:30:00 | 17:00:00 | 02:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Min Voltage at Constrained Conductor (pu) | 1.045 | 1.0437 | 1.0488 | 1.0352 | 1.0339 | 1.0432 | 1.0348 | 1.0334 | 1.0429 | 1.0348 | 1.0334 | 1.0428 | 1.0337 | 1.0322 | 1.042
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 24.13% | 21.76% | 15.48% | 24.31% | 21.6% | 15.46% | 24.35% | 22.21% | 15.58% | 23.96% | 21.71% | 15.42% | 24.39% | 22.26% | 15.59%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163218_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163218_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 32108_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163218_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 32108_1 | TR_LINE 163213_1
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 68.7809 | 78.9767 | 51.3822 | 69.295 | 78.4167 | 51.3229 | 69.4073 | 81.2999 | 51.7393 | 68.2768 | 78.7965 | 51.188 | 69.5202 | 81.4801 | 51.7588
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 7.7924 | 8.8245 | 6.0017 | 7.7959 | 8.8134 | 6.006 | 7.7969 | 8.4559 | 5.9771 | 7.7032 | 8.7309 | 5.9241 | 7.7978 | 8.458 | 5.9758
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 7.7725 | 8.8231 | 5.6996 | 7.7808 | 8.8129 | 5.6988 | 7.7826 | 8.4228 | 5.7048 | 7.6826 | 8.7288 | 5.6348 | 7.7844 | 8.424 | 5.7051
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.99746 | 0.9998 | 0.94967 | 0.99806 | 0.99992 | 0.94885 | 0.99816 | 0.99608 | 0.95445 | 0.99733 | 0.99971 | 0.95116 | 0.99828 | 0.99598 | 0.9547
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 366 | 332 | 285 | 363 | 332 | 285 | 366 | 332
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97811 | 0.97589 | 1.0218 | 0.97084 | 0.98162 | 1.0237 | 0.9693 | 0.90982 | 1.0106 | 0.97414 | 0.96774 | 1.0124 | 0.96774 | 0.90803 | 1.01
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 15.06% | 14.39% | 11.89% | 14.84% | 14.07% | 11.76% | 14.85% | 14.2% | 11.74% | 14.82% | 14.15% | 11.74% | 14.86% | 14.21% | 11.74%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 39.4676 | 41.8834 | 31.3787 | 38.8771 | 40.9426 | 31.0499 | 38.9079 | 41.3197 | 30.9898 | 38.8324 | 41.1633 | 30.9977 | 38.9332 | 41.3545 | 30.9873
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 4.48 | 4.6986 | 3.6652 | 4.3825 | 4.6209 | 3.6336 | 4.3795 | 4.5863 | 3.5801 | 4.3895 | 4.6003 | 3.5874 | 4.3758 | 4.5844 | 3.5776
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 4.0831 | 4.3966 | 2.7799 | 3.984 | 4.2857 | 2.7163 | 3.9844 | 4.2908 | 2.717 | 3.9833 | 4.2887 | 2.7169 | 3.9847 | 4.2912 | 2.7171
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.9114 | 0.93573 | 0.75847 | 0.90906 | 0.92746 | 0.74757 | 0.90978 | 0.93557 | 0.75893 | 0.90746 | 0.93226 | 0.75735 | 0.91063 | 0.93605 | 0.75945
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99294 | 0.98132 | 1.0218 | 0.9861 | 0.98727 | 1.0237 | 0.98464 | 0.97095 | 1.0106 | 0.98881 | 0.97762 | 1.0124 | 0.98317 | 0.96972 | 1.01
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 15.22% | 11.61% | 9.495% | 15.23% | 11.62% | 9.497% | 15.32% | 11.81% | 9.516% | 15.32% | 11.82% | 9.472% | 18.16% | 13.97% | 11.24%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 25.7215 | 27.8534 | 22.2179 | 25.7452 | 27.8849 | 22.223 | 25.8913 | 28.3426 | 22.2674 | 25.8962 | 28.3639 | 22.1641 | 30.6975 | 33.5368 | 26.3113
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 2.9404 | 3.1405 | 2.5583 | 2.9437 | 3.1449 | 2.5594 | 2.9525 | 3.1704 | 2.5586 | 2.9542 | 3.1753 | 2.5476 | 3.5125 | 3.7639 | 3.0302
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 1.8991 | 2.0864 | 1.0363 | 1.9064 | 2.0961 | 1.0441 | 1.9322 | 2.1222 | 1.0636 | 1.9681 | 2.1629 | 1.0983 | 1.9512 | 2.0939 | 1.0862
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.64585 | 0.66436 | 0.40506 | 0.64762 | 0.66651 | 0.40795 | 0.65442 | 0.6694 | 0.41572 | 0.66621 | 0.68115 | 0.43112 | 0.55549 | 0.55631 | 0.35845
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1 | 0.98631 | 1.0073 | 1.0002 | 0.98657 | 1.0074 | 0.99756 | 0.97851 | 1.0051 | 0.99794 | 0.97931 | 1.0055 | 1.001 | 0.98178 | 1.0074
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 19.36% | 20.57% | 18.21% | 18.96% | 20.14% | 17.83% | 19.01% | 20.24% | 17.65% | 19% | 20.23% | 17.64% | 18.95% | 20.18% | 17.62%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 38.5327 | 45.874 | 37.1489 | 37.7279 | 44.9063 | 36.3761 | 37.8344 | 45.1445 | 36.0002 | 37.8182 | 45.1045 | 35.99 | 37.7196 | 44.9903 | 35.9471
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 4.3537 | 5.1255 | 4.2151 | 4.2645 | 5.0199 | 4.1288 | 4.265 | 5.0178 | 4.1293 | 4.265 | 5.0176 | 4.1292 | 4.2645 | 5.0204 | 4.129
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 3.6821 | 4.3165 | 3.5678 | 3.6083 | 4.2298 | 3.4963 | 3.6083 | 4.2296 | 3.4963 | 3.6083 | 4.2296 | 3.4963 | 3.6083 | 4.2299 | 3.4963
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.84572 | 0.84213 | 0.84643 | 0.8461 | 0.84258 | 0.8468 | 0.846 | 0.8429 | 0.84671 | 0.84602 | 0.84294 | 0.84672 | 0.84611 | 0.84251 | 0.84676
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 16:30:00 | 17:30:00 | 01:00:00 | 16:30:00 | 17:30:00 | 01:00:00 | 16:30:00 | 17:30:00 | 01:00:00 | 16:30:00 | 17:30:00 | 01:00:00 | 16:30:00 | 17:30:00 | 01:00:00
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98838 | 0.97738 | 0.99255 | 0.98878 | 0.97788 | 0.99289 | 0.98612 | 0.97231 | 1.0034 | 0.98653 | 0.97313 | 1.0036 | 0.98899 | 0.97615 | 1.0048
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 26.08% | 22.45% | 18.79% | 26.29% | 22.64% | 18.8% | 26.3% | 22.65% | 18.81% | 25.98% | 22.37% | 18.57% | 26.65% | 22.95% | 19.05%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 121605_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 121605_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 121605_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 121605_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 121605_1
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 67.2794 | 66.2225 | 51.1111 | 67.8402 | 66.7762 | 51.1425 | 67.8655 | 66.8098 | 51.1554 | 67.0223 | 65.9795 | 50.5234 | 68.7587 | 67.6914 | 51.8181
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 8.1183 | 7.9858 | 6.158 | 8.1186 | 7.986 | 6.158 | 8.1186 | 7.986 | 6.158 | 8.0182 | 7.8873 | 6.082 | 8.2191 | 8.0849 | 6.2341
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 8.1176 | 7.9851 | 6.1579 | 8.1177 | 7.9853 | 6.1579 | 8.1177 | 7.9853 | 6.1579 | 8.0174 | 7.8866 | 6.0818 | 8.2181 | 8.084 | 6.234
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.9999 | 0.99992 | 0.99998 | 0.99989 | 0.9999 | 0.99998 | 0.99989 | 0.9999 | 0.99998 | 0.9999 | 0.99991 | 0.99997 | 0.99987 | 0.99989 | 0.99998
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0555 | 1.0548 | 1.0539 | 1.0468 | 1.0461 | 1.0532 | 1.0464 | 1.0456 | 1.053 | 1.0465 | 1.0457 | 1.053 | 1.0456 | 1.0448 | 1.0523
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 29.29% | 25.31% | 22.9% | 29.41% | 25.41% | 22.91% | 29.42% | 25.42% | 22.91% | 29.14% | 25.18% | 22.73% | 29.71% | 25.67% | 23.09%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 75.5616 | 74.6547 | 62.2941 | 75.8874 | 74.9705 | 62.3049 | 75.9022 | 74.9899 | 62.3094 | 75.1857 | 74.2871 | 61.8162 | 76.6507 | 75.725 | 62.8158
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 9.1225 | 9.0073 | 7.5075 | 9.0865 | 8.9708 | 7.5042 | 9.0849 | 8.9686 | 7.5029 | 8.9996 | 8.885 | 7.4435 | 9.1674 | 9.0492 | 7.5593
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 8.1255 | 7.993 | 6.1642 | 8.1256 | 7.9931 | 6.1642 | 8.1256 | 7.9931 | 6.1642 | 8.0252 | 7.8944 | 6.0881 | 8.2259 | 8.0918 | 6.2402
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.89071 | 0.88739 | 0.82107 | 0.89425 | 0.89101 | 0.82143 | 0.8944 | 0.89123 | 0.82158 | 0.89173 | 0.8885 | 0.81791 | 0.8973 | 0.8942 | 0.8255
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0561 | 1.0554 | 1.0543 | 1.0474 | 1.0467 | 1.0536 | 1.047 | 1.0462 | 1.0533 | 1.0471 | 1.0462 | 1.0533 | 1.0462 | 1.0453 | 1.0527
NQ | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 83.55% | 65.48% | 52.78% | 83.37% | 65.36% | 52.68% | 83.93% | 66.15% | 53.02% | 83.52% | 65.79% | 52.75% | 84.18% | 66.26% | 53.34%
NQ | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 175.4614 | 206.2543 | 163.6297 | 175.0749 | 205.8712 | 163.3113 | 176.2498 | 208.3801 | 164.3499 | 175.3887 | 207.2375 | 163.5253 | 176.7728 | 208.7314 | 165.3495
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 20.9314 | 24.5283 | 19.5464 | 20.8861 | 24.4784 | 19.5091 | 20.9772 | 24.5911 | 19.5925 | 20.8767 | 24.4668 | 19.4956 | 21.0572 | 24.6679 | 19.7231
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 19.5138 | 22.5759 | 18.2804 | 19.4761 | 22.5343 | 18.2489 | 19.547 | 22.6174 | 18.3146 | 19.4495 | 22.4986 | 18.2203 | 19.8127 | 22.9085 | 18.5695
NQ | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.93227 | 0.9204 | 0.93523 | 0.93249 | 0.92058 | 0.93541 | 0.93182 | 0.91974 | 0.93478 | 0.93164 | 0.91956 | 0.93459 | 0.9409 | 0.92868 | 0.94151
NQ | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | MOPA_Clare South - Mona Park 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | MOPA_Clare South - Mona Park 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0435 | 1.0402 | 1.0449 | 1.0435 | 1.04 | 1.0449 | 1.0411 | 1.0322 | 1.0428 | 1.0412 | 1.0327 | 1.0428 | 1.042 | 1.0337 | 1.0434
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 45.99% | 38.37% | 27.15% | 45.81% | 38.24% | 27.04% | 45.87% | 38.5% | 27.04% | 45.44% | 38.13% | 26.76% | 45.67% | 38.24% | 27.03%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 91.5283 | 112.8145 | 78.4537 | 91.1635 | 112.4288 | 78.156 | 91.2733 | 113.1877 | 78.148 | 90.4248 | 112.1012 | 77.3332 | 90.8859 | 112.419 | 78.1045
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 10.4246 | 12.6549 | 8.9982 | 10.3854 | 12.6118 | 8.9658 | 10.3705 | 12.5889 | 8.9443 | 10.2782 | 12.479 | 8.8543 | 10.356 | 12.5497 | 8.9563
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 10.1577 | 12.1795 | 8.8279 | 10.1228 | 12.1413 | 8.7984 | 10.1075 | 12.1221 | 8.7776 | 10.0161 | 12.0131 | 8.6886 | 10.2091 | 12.2366 | 8.8622
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.9744 | 0.96243 | 0.98106 | 0.9747 | 0.9627 | 0.98133 | 0.97464 | 0.96291 | 0.98135 | 0.9745 | 0.96267 | 0.98129 | 0.98581 | 0.97505 | 0.98949
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99631 | 0.98126 | 1.0033 | 0.99654 | 0.98127 | 1.0035 | 0.99391 | 0.97292 | 1.0012 | 0.99431 | 0.97377 | 1.0016 | 0.99675 | 0.97653 | 1.0031
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 69.58% | 50.51% | 41.48% | 68.91% | 50.03% | 41.37% | 70.23% | 51.28% | 41.5% | 69.96% | 50.92% | 41.47% | 70.31% | 51.34% | 41.53%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 107.8466 | 115.6722 | 93.741 | 106.8086 | 114.5627 | 93.4959 | 108.8529 | 117.4268 | 93.7859 | 108.4414 | 116.6101 | 93.7206 | 108.9819 | 117.5673 | 93.8522
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 12.5936 | 13.4339 | 11.0347 | 12.4728 | 13.3143 | 11.0075 | 12.5628 | 13.448 | 10.949 | 12.5301 | 13.3801 | 10.9475 | 12.5719 | 13.459 | 10.9545
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 12.2808 | 13.3866 | 9.2475 | 12.1362 | 13.2466 | 9.1675 | 12.3187 | 13.434 | 9.2901 | 12.2574 | 13.3541 | 9.2506 | 12.3329 | 13.4462 | 9.298
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.97516 | 0.99647 | 0.83803 | 0.97301 | 0.99492 | 0.83283 | 0.98056 | 0.99896 | 0.84848 | 0.97823 | 0.99806 | 0.84499 | 0.98099 | 0.99905 | 0.84878
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0215 | 1.0159 | 1.0297 | 1.0215 | 1.0166 | 1.0299 | 1.0095 | 1.0017 | 1.0213 | 1.0107 | 1.0037 | 1.0218 | 1.0091 | 1.0014 | 1.021
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 40.91% | 37.17% | 40.77% | 40.9% | 37.17% | 40.76% | 41.09% | 37.18% | 41.19% | 41.21% | 37.14% | 41.16% | 41.1% | 37.2% | 41.2%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 76.9182 | 76.2021 | 75.4188 | 76.8833 | 76.2015 | 75.4043 | 77.2558 | 76.2286 | 76.1957 | 77.4738 | 76.1372 | 76.1429 | 77.2723 | 76.253 | 76.215
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 8.5944 | 8.5138 | 8.4838 | 8.5937 | 8.5122 | 8.4835 | 8.6139 | 8.3512 | 8.4995 | 8.635 | 8.4572 | 8.4985 | 8.6142 | 8.3517 | 8.4999
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 7.5826 | 7.5156 | 7.4968 | 7.5823 | 7.5142 | 7.4967 | 7.5968 | 7.3754 | 7.5024 | 7.6203 | 7.4695 | 7.502 | 7.5969 | 7.3756 | 7.5025
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.86856 | 0.86884 | 0.86936 | 0.86859 | 0.86884 | 0.86937 | 0.86836 | 0.86979 | 0.8688 | 0.86905 | 0.86946 | 0.86884 | 0.86835 | 0.86977 | 0.86878
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 15:00:00 | 21:00:00 | 22:00:00 | 15:00:00 | 21:30:00 | 22:00:00 | 13:30:00 | 19:30:00 | 22:00:00 | 12:30:00 | 20:00:00 | 22:00:00 | 13:30:00 | 19:30:00 | 22:00:00
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9607 | 0.96118 | 0.96873 | 0.9611 | 0.961 | 0.96891 | 0.9583 | 0.94126 | 0.95956 | 0.95771 | 0.95527 | 0.96018 | 0.95811 | 0.94098 | 0.95934
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 25.97% | 29.06% | 24.53% | 26.22% | 29.59% | 24.68% | 25.86% | 29.47% | 24.35% | 26.32% | 30.04% | 24.77% | 27.35% | 31.23% | 25.75%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 66.9956 | 85.7417 | 66.723 | 67.643 | 87.2979 | 67.1372 | 66.7199 | 86.946 | 66.2274 | 67.9137 | 88.6082 | 67.3633 | 70.559 | 92.1323 | 70.0483
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 8.0094 | 10.2082 | 7.9991 | 8.0278 | 10.3234 | 8.0241 | 7.9145 | 10.272 | 7.9069 | 8.055 | 10.4662 | 8.0414 | 8.3584 | 10.8666 | 8.3537
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 7.9992 | 10.2051 | 7.9484 | 8.0087 | 10.2532 | 8.0241 | 7.8825 | 10.1927 | 7.9055 | 8.0214 | 10.3813 | 8.0395 | 8.3107 | 10.7568 | 8.3479
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.99872 | 0.9997 | 0.99366 | 0.99759 | 0.99318 | 1 | 0.99592 | 0.99226 | 0.99981 | 0.99579 | 0.99186 | 0.99975 | 0.99426 | 0.98988 | 0.99929
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0458 | 1.0413 | 1.0487 | 1.038 | 1.0342 | 1.0455 | 1.0375 | 1.0333 | 1.0442 | 1.0374 | 1.0331 | 1.0441 | 1.0361 | 1.0315 | 1.0431
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 10.5% | 11.17% | 6.637% | 10.58% | 11.08% | 6.63% | 10.6% | 11.43% | 6.677% | 10.53% | 11.29% | 6.668% | 10.62% | 11.46% | 6.679%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 37.2676 | 43.3457 | 27.8748 | 37.5563 | 42.9818 | 27.8477 | 37.6295 | 44.3607 | 28.0438 | 37.3979 | 43.821 | 28.007 | 37.707 | 44.4665 | 28.0531
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 4.068 | 4.3511 | 3.2077 | 3.8939 | 4.3503 | 3.2112 | 3.8939 | 4.3536 | 3.188 | 4.0662 | 4.3523 | 3.1922 | 3.8941 | 4.3538 | 3.187
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 3.9986 | 4.2753 | 2.9197 | 3.8316 | 4.275 | 2.9194 | 3.8317 | 4.276 | 2.9217 | 4.0001 | 4.2756 | 2.9213 | 3.8317 | 4.276 | 2.9218
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.98293 | 0.98257 | 0.91022 | 0.98398 | 0.98268 | 0.90913 | 0.98399 | 0.98216 | 0.91646 | 0.98373 | 0.98235 | 0.91513 | 0.98396 | 0.98211 | 0.9168
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95486 | 0.8781 | 1.0067 | 0.90699 | 0.88538 | 1.0087 | 0.90522 | 0.8585 | 0.99444 | 0.95113 | 0.86883 | 0.99705 | 0.9034 | 0.85651 | 0.99379
NQ | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 13.14% | 15.95% | 13.25% | 13.13% | 16.05% | 13.24% | 13.14% | 16.06% | 13.24% | 13.14% | 16.06% | 13.24% | 13.15% | 16.08% | 13.23%
NQ | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 162083_1 | TR_LINE 31680_2 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 31680_2 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 31680_2 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 31680_2 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 31680_2 | TR_LINE 162083_1
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 12.6118 | 17.067 | 12.7202 | 12.8703 | 17.1711 | 12.7059 | 12.875 | 17.1855 | 12.7089 | 12.8759 | 17.187 | 12.7098 | 12.8864 | 17.2042 | 12.7009
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 1.5092 | 2.0122 | 1.5236 | 1.5321 | 2.0124 | 1.5236 | 1.5321 | 2.0124 | 1.5236 | 1.5321 | 2.0124 | 1.5236 | 1.5321 | 2.0124 | 1.5236
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 1.5044 | 2.0085 | 1.5188 | 1.5276 | 2.0087 | 1.5188 | 1.5276 | 2.0087 | 1.5188 | 1.5276 | 2.0087 | 1.5188 | 1.5277 | 2.0087 | 1.5188
NQ | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.99676 | 0.99686 | 0.99687 | 0.99709 | 0.99683 | 0.99684 | 0.9971 | 0.99682 | 0.99685 | 0.9971 | 0.99682 | 0.99685 | 0.99712 | 0.99682 | 0.99683
NQ | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 96 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96
NQ | ST-GI-1_Stuart-Giru 66 kV | Time | 06:00:00 | 18:00:00 | 05:30:00 | 16:30:00 | 18:00:00 | 05:30:00 | 16:30:00 | 18:00:00 | 05:30:00 | 16:30:00 | 18:00:00 | 05:30:00 | 16:30:00 | 18:00:00 | 05:30:00
NQ | ST-GI-1_Stuart-Giru 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0467 | 1.0304 | 1.0476 | 1.0412 | 1.0242 | 1.0488 | 1.0408 | 1.0234 | 1.0486 | 1.0407 | 1.0233 | 1.0485 | 1.0399 | 1.0222 | 1.0492
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 14.07% | 16.85% | 13.13% | 13.96% | 16.87% | 12.98% | 13.8% | 16.81% | 12.81% | 13.84% | 16.87% | 12.85% | 14.18% | 17.32% | 13.17%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 77.537 | 98.0772 | 68.8037 | 76.9399 | 98.1859 | 68.0039 | 76.0366 | 97.8401 | 67.1299 | 76.2345 | 98.2 | 67.3236 | 78.1585 | 100.8164 | 68.9999
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 9.3055 | 11.7422 | 8.2655 | 9.1808 | 11.6872 | 8.1496 | 9.0697 | 11.6368 | 8.0428 | 9.0927 | 11.6786 | 8.0653 | 9.3145 | 11.9783 | 8.261
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 9.0994 | 11.671 | 7.9124 | 9.0716 | 11.6632 | 7.9248 | 8.9699 | 11.6148 | 7.8318 | 8.9927 | 11.6574 | 7.8544 | 9.2272 | 11.9637 | 8.0672
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.97785 | 0.99394 | 0.95729 | 0.9881 | 0.99795 | 0.97241 | 0.989 | 0.99811 | 0.97376 | 0.989 | 0.99818 | 0.97384 | 0.99062 | 0.99878 | 0.97655
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0478 | 1.0431 | 1.05 | 1.041 | 1.0363 | 1.0468 | 1.0406 | 1.0354 | 1.0465 | 1.0405 | 1.0353 | 1.0464 | 1.0395 | 1.034 | 1.0456
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 28.85% | 29.56% | 24.6% | 28.91% | 29.69% | 24.56% | 28.76% | 29.65% | 24.41% | 28.94% | 29.86% | 24.58% | 29.92% | 30.89% | 25.41%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 184082_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32425_1
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 195.9116 | 215.7939 | 163.1073 | 196.2656 | 216.7518 | 162.8217 | 195.2872 | 216.438 | 161.8212 | 196.4816 | 217.9853 | 162.9447 | 203.1486 | 225.4926 | 168.4605
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 23.5122 | 25.8453 | 19.5943 | 23.3829 | 25.6666 | 19.5126 | 23.186 | 25.6107 | 19.3878 | 23.3251 | 25.778 | 19.5207 | 24.088 | 26.6288 | 20.1688
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 23.4966 | 25.8451 | 19.4514 | 23.3828 | 25.6606 | 19.4571 | 23.1859 | 25.6023 | 19.3431 | 23.325 | 25.7698 | 19.4783 | 24.0855 | 26.6109 | 20.1414
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.99933 | 0.99999 | 0.9927 | 1 | 0.99977 | 0.99715 | 1 | 0.99967 | 0.99769 | 1 | 0.99968 | 0.99782 | 0.9999 | 0.99933 | 0.99864
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0498 | 1.0477 | 1.0509 | 1.0407 | 1.0358 | 1.0483 | 1.0386 | 1.0351 | 1.048 | 1.0384 | 1.0344 | 1.048 | 1.0372 | 1.033 | 1.0473
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 22.72% | 17.67% | 19.32% | 19.03% | 14.72% | 14.3% | 18.56% | 14.39% | 13.95% | 18.35% | 14.25% | 13.92% | 18.55% | 14.44% | 14.05%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 57.0285 | 55.4702 | 54.4772 | 47.7765 | 46.2077 | 40.325 | 46.5868 | 45.1854 | 39.3266 | 46.0685 | 44.7438 | 39.2476 | 46.5486 | 45.3283 | 39.6337
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 6.8594 | 6.6544 | 6.5231 | 5.7547 | 5.5099 | 4.8344 | 5.6101 | 5.3849 | 4.7136 | 5.5482 | 5.3321 | 4.7037 | 5.6037 | 5.397 | 4.747
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 2.6212 | 2.1451 | 0.33371 | 3.3769 | 2.9051 | 1.1449 | 3.228 | 2.7263 | 0.99064 | 3.1065 | 2.5986 | 0.88526 | 3.1728 | 2.6609 | 0.91929
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.38214 | 0.32236 | 0.051145 | 0.58681 | 0.52725 | 0.23681 | 0.57539 | 0.50629 | 0.21017 | 0.55992 | 0.48735 | 0.1882 | 0.56619 | 0.49303 | 0.19366
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 12:00:00 | 17:00:00 | 05:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0522 | 1.0494 | 1.0474 | 1.0537 | 1.0431 | 1.0487 | 1.0534 | 1.0425 | 1.0485 | 1.0535 | 1.0425 | 1.0484 | 1.0531 | 1.0416 | 1.0477
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 41.48% | 41.1% | 35.13% | 41.82% | 41.6% | 35.09% | 42.34% | 42.18% | 35.52% | 42.4% | 42.29% | 35.61% | 43.43% | 43.38% | 36.45%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 382.0385 | 412.6136 | 322.4654 | 385.1745 | 417.6977 | 322.1156 | 389.9637 | 423.4815 | 326.0979 | 390.5289 | 424.58 | 326.896 | 399.9975 | 435.5109 | 334.6367
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 45.8391 | 49.3948 | 38.7279 | 45.9635 | 49.724 | 38.5954 | 46.5193 | 50.3657 | 39.0633 | 46.5839 | 50.4923 | 39.1558 | 47.6766 | 51.7446 | 40.0592
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 44.4959 | 48.4267 | 37.3703 | 45.4153 | 49.3945 | 37.5328 | 46.013 | 50.0599 | 38.0541 | 46.0847 | 50.1952 | 38.1612 | 47.2483 | 51.5081 | 39.1603
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.97064 | 0.98034 | 0.9649 | 0.98802 | 0.99333 | 0.97242 | 0.98907 | 0.99389 | 0.97412 | 0.98924 | 0.99408 | 0.97455 | 0.99097 | 0.9954 | 0.97751
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0496 | 1.0472 | 1.0506 | 1.0439 | 1.0413 | 1.0481 | 1.0435 | 1.0404 | 1.0479 | 1.0435 | 1.0403 | 1.0478 | 1.0426 | 1.0393 | 1.0472
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 42.01% | 42.06% | 35.51% | 43.38% | 43.44% | 35.83% | 43.98% | 44.06% | 36.34% | 44.06% | 44.19% | 36.45% | 45.22% | 45.41% | 37.43%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 386.9573 | 422.314 | 326.0008 | 399.5754 | 436.11 | 328.9411 | 405.0664 | 442.3917 | 333.6182 | 405.749 | 443.6722 | 334.6042 | 416.4723 | 455.9581 | 343.6295
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 46.4435 | 50.5599 | 39.1654 | 47.6834 | 51.9097 | 39.4232 | 48.3211 | 52.6073 | 39.9736 | 48.3994 | 52.755 | 40.0883 | 49.6381 | 54.163 | 41.1439
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 46.3965 | 50.4418 | 39.0523 | 47.3044 | 51.3874 | 39.2076 | 47.9175 | 52.0701 | 39.7427 | 47.9909 | 52.2088 | 39.8525 | 49.1846 | 53.555 | 40.8781
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.99899 | 0.99766 | 0.99711 | 0.99205 | 0.98994 | 0.99453 | 0.99165 | 0.98979 | 0.99423 | 0.99156 | 0.98965 | 0.99412 | 0.99086 | 0.98877 | 0.99354
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0499 | 1.0472 | 1.0509 | 1.0438 | 1.0411 | 1.0483 | 1.0434 | 1.0401 | 1.0481 | 1.0434 | 1.04 | 1.048 | 1.0425 | 1.039 | 1.0473
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 52.63% | 43.94% | 37.52% | 51.48% | 42.96% | 37.15% | 60.29% | 49.82% | 43.8% | 59.97% | 49.45% | 43.61% | 59.89% | 49.4% | 43.49%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 69.4727 | 73.3868 | 59.6612 | 67.9545 | 71.7413 | 59.0638 | 79.5845 | 83.1931 | 69.6497 | 79.1635 | 82.5781 | 69.3435 | 79.0565 | 82.5008 | 69.1428
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 8.2466 | 8.6723 | 7.1091 | 8.0306 | 8.4409 | 7.025 | 9.3649 | 9.7358 | 8.2568 | 9.3177 | 9.6678 | 8.2212 | 9.2957 | 9.6463 | 8.192
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 7.2434 | 7.7607 | 6.1032 | 6.917 | 7.4122 | 5.9636 | 8.309 | 8.8149 | 7.1979 | 8.2399 | 8.7136 | 7.1526 | 8.2439 | 8.7273 | 7.1343
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.87835 | 0.89489 | 0.85851 | 0.86134 | 0.87813 | 0.8489 | 0.88703 | 0.90501 | 0.87175 | 0.88412 | 0.90091 | 0.87002 | 0.88667 | 0.90437 | 0.87088
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0362 | 1.0312 | 1.0407 | 1.0319 | 1.027 | 1.0389 | 1.0268 | 1.0207 | 1.035 | 1.0271 | 1.0212 | 1.0351 | 1.026 | 1.0198 | 1.0344
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 26.62% | 21.57% | 16.04% | 29.01% | 23.71% | 17.46% | 30.14% | 24.64% | 18.12% | 29.97% | 24.51% | 18.02% | 30.48% | 24.93% | 18.32%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 56322_1
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 68.6669 | 63.6293 | 43.623 | 74.8513 | 69.9574 | 47.4975 | 77.7569 | 72.6895 | 49.2827 | 77.3298 | 72.2939 | 49.0201 | 78.6278 | 73.5332 | 49.8373
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 8.2652 | 7.6734 | 5.256 | 9.0137 | 8.3664 | 5.7192 | 9.362 | 8.6885 | 5.9326 | 9.3115 | 8.6417 | 5.901 | 9.4631 | 8.7822 | 5.9957
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 8.2646 | 7.6734 | 5.2449 | 9.0076 | 8.3631 | 5.7154 | 9.349 | 8.6799 | 5.9315 | 9.2989 | 8.6335 | 5.8998 | 9.4491 | 8.7729 | 5.9949
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.99992 | 1 | 0.99789 | 0.99932 | 0.99961 | 0.99934 | 0.99861 | 0.99902 | 0.99982 | 0.99865 | 0.99905 | 0.9998 | 0.99852 | 0.99894 | 0.99986
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0529 | 1.0549 | 1.0539 | 1.0534 | 1.0461 | 1.0532 | 1.0532 | 1.0456 | 1.0529 | 1.0533 | 1.0456 | 1.0529 | 1.0528 | 1.0447 | 1.0522
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 32.58% | 30.47% | 28.12% | 31.87% | 29.8% | 27.85% | 37.83% | 35.57% | 33.79% | 37.63% | 35.26% | 33.61% | 37.55% | 35.2% | 33.49%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 32389_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 32389_1 | TR_LINE 46566_1 | TR_LINE 46566_1
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 61.5772 | 62.7708 | 52.3016 | 60.2309 | 61.38 | 51.8017 | 71.5035 | 67.2223 | 56.7729 | 71.119 | 66.6346 | 56.4698 | 70.9758 | 66.5285 | 56.2658
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 7.2913 | 7.3965 | 6.2208 | 7.1025 | 7.2038 | 6.1509 | 8.3883 | 7.6543 | 6.6056 | 8.346 | 7.6004 | 6.5736 | 8.3203 | 7.572 | 6.5449
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 6.079 | 6.2129 | 4.9922 | 5.7547 | 5.8668 | 4.8532 | 7.129 | 6.4822 | 5.4452 | 7.0606 | 6.3902 | 5.4041 | 7.0648 | 6.4059 | 5.3886
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.83373 | 0.83998 | 0.80251 | 0.81023 | 0.8144 | 0.78903 | 0.84987 | 0.84687 | 0.82433 | 0.84599 | 0.84078 | 0.82208 | 0.84911 | 0.846 | 0.82334
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 189 | 168 | 189 | 189 | 168 | 189 | 189 | 168
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0316 | 1.0263 | 1.0376 | 1.0281 | 1.0231 | 1.0362 | 1.0208 | 0.99544 | 1.0174 | 1.0213 | 0.99717 | 1.0179 | 1.0201 | 0.99501 | 1.0171
SW | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 11.83% | 14.1% | 13.24% | 11.83% | 14.1% | 13.24% | 11.83% | 14.1% | 13.24% | 11.83% | 14.1% | 13.24% | 11.83% | 14.1% | 13.24%
SW | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 76.9043 | 92.8919 | 76.1127 | 76.9081 | 92.8966 | 76.1166 | 76.9115 | 92.9009 | 76.1201 | 76.9101 | 92.8968 | 76.1173 | 76.9146 | 92.9023 | 76.1213
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 18.6537 | 22.5031 | 18.2486 | 18.6534 | 22.503 | 18.2483 | 18.6532 | 22.5029 | 18.2481 | 18.6533 | 22.503 | 18.2483 | 18.6531 | 22.5028 | 18.248
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 18.0887 | 22.2003 | 17.6887 | 18.0887 | 22.2003 | 17.6887 | 18.0888 | 22.2004 | 17.6887 | 18.0888 | 22.2003 | 17.6887 | 18.0888 | 22.2004 | 17.6887
SW | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.96971 | 0.98654 | 0.96932 | 0.96973 | 0.98655 | 0.96933 | 0.96974 | 0.98656 | 0.96935 | 0.96973 | 0.98655 | 0.96934 | 0.96975 | 0.98656 | 0.96935
SW | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575
SW | 7235_Bulli Creek - Waggamba 132 kV | Time | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00 | 16:30:00 | 19:30:00 | 22:00:00
SW | 7235_Bulli Creek - Waggamba 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0609 | 1.0596 | 1.0487 | 1.0608 | 1.0595 | 1.0486 | 1.0608 | 1.0594 | 1.0485 | 1.0608 | 1.0595 | 1.0486 | 1.0607 | 1.0594 | 1.0485
SW | 3196_Tara 33 kV | % of Rated A | 19.07% | 16.35% | 13.02% | 20.25% | 17.36% | 13.75% | 20.25% | 17.36% | 13.76% | 20.24% | 17.35% | 13.75% | 19.08% | 16.35% | 13.02%
SW | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1
SW | 3196_Tara 33 kV | Loading (A) | 17.7383 | 18.963 | 15.1006 | 18.83 | 20.1404 | 15.9556 | 18.8315 | 20.1403 | 15.9563 | 18.8236 | 20.1287 | 15.953 | 17.7424 | 18.9657 | 15.1017
SW | 3196_Tara 33 kV | Loading (MVA) | 1.0148 | 1.0797 | 0.87103 | 1.0771 | 1.1466 | 0.92029 | 1.0771 | 1.1466 | 0.92025 | 1.0773 | 1.1467 | 0.92041 | 1.0147 | 1.0796 | 0.87098
SW | 3196_Tara 33 kV | Loading (MW) | 0.9805 | 1.0515 | 0.81044 | 1.0363 | 1.112 | 0.85322 | 1.0363 | 1.112 | 0.85322 | 1.0363 | 1.112 | 0.85322 | 0.98051 | 1.0515 | 0.81044
SW | 3196_Tara 33 kV | Power Factor | 0.96624 | 0.97392 | 0.93043 | 0.96208 | 0.96982 | 0.92713 | 0.96211 | 0.96982 | 0.92716 | 0.96194 | 0.96973 | 0.92699 | 0.96633 | 0.97397 | 0.9305
SW | 3196_Tara 33 kV | Rating (A) | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116
SW | 3196_Tara 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | 3196_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0008 | 0.9961 | 1.0092 | 1.0008 | 0.99604 | 1.0091 | 1.0007 | 0.99605 | 1.009 | 1.0012 | 0.9967 | 1.0094 | 1.0005 | 0.99592 | 1.009
SW | 3203_Miles 33 kV | % of Rated A | 68.41% | 72.76% | 55.82% | 68.44% | 72.79% | 55.84% | 68.44% | 72.54% | 55.84% | 67.89% | 72.23% | 55.38% | 68.99% | 73.12% | 56.3%
SW | 3203_Miles 33 kV | Limiting Line Name | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1
SW | 3203_Miles 33 kV | Loading (A) | 242.845 | 258.2823 | 198.1665 | 242.9459 | 258.3896 | 198.2313 | 242.969 | 257.5066 | 198.2441 | 241.0208 | 256.403 | 196.5876 | 244.9217 | 259.5799 | 199.8704
SW | 3203_Miles 33 kV | Loading (MVA) | 13.7955 | 14.6011 | 11.3127 | 13.7961 | 14.6017 | 11.313 | 13.7962 | 14.5998 | 11.3131 | 13.6957 | 14.4995 | 11.2261 | 13.8968 | 14.706 | 11.4
SW | 3203_Miles 33 kV | Loading (MW) | 13.5861 | 14.3749 | 11.1993 | 13.5863 | 14.3752 | 11.1995 | 13.5864 | 14.3748 | 11.1995 | 13.4901 | 14.2762 | 11.1153 | 13.6827 | 14.4763 | 11.2836
SW | 3203_Miles 33 kV | Power Factor | 0.98476 | 0.98445 | 0.98991 | 0.98474 | 0.98443 | 0.9899 | 0.98473 | 0.98454 | 0.9899 | 0.98493 | 0.98454 | 0.99007 | 0.98454 | 0.98433 | 0.98973
SW | 3203_Miles 33 kV | Rating (A) | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355
SW | 3203_Miles 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | 3203_Miles 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99384 | 0.98899 | 0.99874 | 0.99347 | 0.98863 | 0.99844 | 0.99338 | 0.99189 | 0.99838 | 0.99412 | 0.98932 | 0.99905 | 0.99265 | 0.99112 | 0.99787
SW | F060T_Tara 33 kV | % of Rated A | 19.07% | 15.54% | 12.99% | 20.24% | 16.51% | 13.72% | 20.24% | 16.51% | 13.72% | 20.24% | 16.5% | 13.72% | 19.07% | 15.55% | 12.99%
SW | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1
SW | F060T_Tara 33 kV | Loading (A) | 17.7347 | 18.9628 | 15.1952 | 18.8261 | 20.1402 | 16.0556 | 18.8276 | 20.1401 | 16.0563 | 18.8197 | 20.1285 | 16.0529 | 17.7387 | 18.9655 | 15.1963
SW | F060T_Tara 33 kV | Loading (MVA) | 1.0147 | 1.0799 | 0.8713 | 1.0772 | 1.1469 | 0.9206 | 1.0771 | 1.1469 | 0.92057 | 1.0773 | 1.147 | 0.92073 | 1.0147 | 1.0799 | 0.87125
SW | F060T_Tara 33 kV | Loading (MW) | 0.98033 | 1.0514 | 0.81039 | 1.0361 | 1.1119 | 0.85317 | 1.0361 | 1.1119 | 0.85317 | 1.0361 | 1.1119 | 0.85316 | 0.98034 | 1.0514 | 0.81039
SW | F060T_Tara 33 kV | Power Factor | 0.9661 | 0.97363 | 0.93008 | 0.96189 | 0.96948 | 0.92675 | 0.96193 | 0.96948 | 0.92678 | 0.96176 | 0.96939 | 0.92662 | 0.96619 | 0.97368 | 0.93015
SW | F060T_Tara 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | F060T_Tara 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F060T_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 1.001 | 0.9963 | 1.0032 | 1.001 | 0.99628 | 1.0031 | 1.0009 | 0.99628 | 1.003 | 1.0014 | 0.99693 | 1.0034 | 1.0007 | 0.99612 | 1.003
SW | F067C_Kogan 33 kV | % of Rated A | 56.6% | 36.04% | 30.4% | 56.61% | 36.06% | 30.41% | 56.61% | 36.06% | 30.41% | 56.61% | 36.05% | 30.41% | 56.64% | 36.1% | 30.43%
SW | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1
SW | F067C_Kogan 33 kV | Loading (A) | 52.6373 | 43.9727 | 35.5704 | 52.6476 | 43.9927 | 35.5819 | 52.6494 | 43.9974 | 35.5842 | 52.6451 | 43.9868 | 35.5762 | 52.6749 | 44.0434 | 35.6036
SW | F067C_Kogan 33 kV | Loading (MVA) | 2.9258 | 2.5038 | 1.9963 | 2.9258 | 2.504 | 1.9964 | 2.9258 | 2.5041 | 1.9964 | 2.9258 | 2.504 | 1.9964 | 2.926 | 2.5045 | 1.9965
SW | F067C_Kogan 33 kV | Loading (MW) | 2.3983 | 2.0964 | 1.6919 | 2.3984 | 2.0965 | 1.6919 | 2.3984 | 2.0965 | 1.6919 | 2.3984 | 2.0964 | 1.6919 | 2.3984 | 2.0966 | 1.6919
SW | F067C_Kogan 33 kV | Power Factor | 0.81712 | 0.83714 | 0.84429 | 0.81711 | 0.8371 | 0.84428 | 0.81711 | 0.8371 | 0.84427 | 0.81711 | 0.83712 | 0.84428 | 0.81708 | 0.837 | 0.84424
SW | F067C_Kogan 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | F067C_Kogan 33 kV | Time | 12:30:00 | 17:00:00 | 22:00:00 | 12:30:00 | 17:00:00 | 22:00:00 | 12:30:00 | 17:00:00 | 22:00:00 | 12:30:00 | 17:00:00 | 22:00:00 | 12:30:00 | 17:00:00 | 22:00:00
SW | F067C_Kogan 33 kV | Min Voltage at Constrained Conductor (pu) | 0.96531 | 0.99595 | 0.97894 | 0.96514 | 0.99558 | 0.97865 | 0.96511 | 0.99549 | 0.97859 | 0.96518 | 0.99569 | 0.97879 | 0.96467 | 0.99464 | 0.97809
SW | F069C_Brigalow 33 kV | % of Rated A | 4.934% | 4.881% | 4.962% | 4.933% | 4.879% | 4.961% | 4.933% | 4.879% | 4.961% | 4.933% | 4.879% | 4.961% | 4.931% | 4.874% | 4.964%
SW | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1
SW | F069C_Brigalow 33 kV | Loading (A) | 4.3416 | 4.2954 | 4.3663 | 4.3411 | 4.2937 | 4.3658 | 4.3409 | 4.2934 | 4.3657 | 4.3411 | 4.2939 | 4.3658 | 4.3396 | 4.2893 | 4.3685
SW | F069C_Brigalow 33 kV | Loading (MVA) | 0.25288 | 0.25047 | 0.25459 | 0.25282 | 0.25028 | 0.25454 | 0.2528 | 0.25024 | 0.25452 | 0.25282 | 0.2503 | 0.25454 | 0.25265 | 0.24978 | 0.25481
SW | F069C_Brigalow 33 kV | Loading (MW) | 0.037206 | 0.049713 | 0.032427 | 0.037206 | 0.049712 | 0.032427 | 0.037206 | 0.049712 | 0.032427 | 0.037206 | 0.049712 | 0.032427 | 0.037205 | 0.04971 | 0.032154
SW | F069C_Brigalow 33 kV | Power Factor | 0.14713 | 0.19848 | 0.12737 | 0.14716 | 0.19862 | 0.12739 | 0.14717 | 0.19866 | 0.1274 | 0.14716 | 0.19861 | 0.12739 | 0.14726 | 0.19902 | 0.12619
SW | F069C_Brigalow 33 kV | Rating (A) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
SW | F069C_Brigalow 33 kV | Time | 06:00:00 | 17:00:00 | 05:00:00 | 06:00:00 | 17:00:00 | 05:00:00 | 06:00:00 | 17:00:00 | 05:00:00 | 06:00:00 | 17:00:00 | 05:00:00 | 06:00:00 | 17:00:00 | 04:30:00
SW | F069C_Brigalow 33 kV | Min Voltage at Constrained Conductor (pu) | 1.019 | 1.0202 | 1.0201 | 1.0189 | 1.0198 | 1.02 | 1.0189 | 1.0197 | 1.02 | 1.0189 | 1.0198 | 1.02 | 1.0186 | 1.0188 | 1.0205
SW | F073C_Fairymeadow 33 kV | % of Rated A | 4.105% | 4.536% | 3.559% | 4.106% | 4.537% | 3.56% | 4.106% | 4.538% | 3.56% | 4.105% | 4.537% | 3.559% | 4.108% | 4.527% | 3.561%
SW | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1
SW | F073C_Fairymeadow 33 kV | Loading (A) | 3.8173 | 4.536 | 4.1282 | 3.8182 | 4.5375 | 4.1291 | 3.8184 | 4.5378 | 4.1292 | 3.818 | 4.5369 | 4.1286 | 3.8206 | 4.5267 | 4.1308
SW | F073C_Fairymeadow 33 kV | Loading (MVA) | 0.21948 | 0.25782 | 0.23784 | 0.21946 | 0.25782 | 0.23783 | 0.21946 | 0.25782 | 0.23783 | 0.21946 | 0.25782 | 0.23784 | 0.21941 | 0.25784 | 0.2378
SW | F073C_Fairymeadow 33 kV | Loading (MW) | 0.21505 | 0.23976 | 0.23434 | 0.21504 | 0.23976 | 0.23434 | 0.21504 | 0.23976 | 0.23434 | 0.21505 | 0.23976 | 0.23434 | 0.21504 | 0.23977 | 0.23433
SW | F073C_Fairymeadow 33 kV | Power Factor | 0.9798 | 0.92889 | 0.98526 | 0.97988 | 0.9289 | 0.98531 | 0.9799 | 0.92891 | 0.98532 | 0.97987 | 0.9289 | 0.98528 | 0.98009 | 0.92882 | 0.98541
SW | F073C_Fairymeadow 33 kV | Rating (A) | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116
SW | F073C_Fairymeadow 33 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
SW | F073C_Fairymeadow 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0059 | 0.99442 | 1.008 | 1.0056 | 0.99408 | 1.0077 | 1.0055 | 0.99401 | 1.0076 | 1.0056 | 0.99422 | 1.0078 | 1.0047 | 0.99653 | 1.0072
SW | F074C_Miles-Condamine 33 kV | % of Rated A | 17.81% | 14.72% | 12.05% | 17.82% | 14.73% | 12.05% | 17.82% | 14.67% | 12.06% | 17.8% | 14.72% | 12.05% | 17.83% | 14.69% | 12.06%
SW | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 23297_2 | TR_LINE 195522_1 | TR_LINE 138809_5 | TR_LINE 23297_2 | TR_LINE 195522_1 | TR_LINE 138809_5 | TR_LINE 23297_2 | TR_LINE 195522_1 | TR_LINE 138809_5 | TR_LINE 23297_2 | TR_LINE 195522_1 | TR_LINE 138809_5 | TR_LINE 23297_2 | TR_LINE 195522_1
SW | F074C_Miles-Condamine 33 kV | Loading (A) | 25.4662 | 43.4243 | 31.6945 | 25.4761 | 43.4414 | 31.704 | 25.4784 | 43.2903 | 31.7059 | 25.4585 | 43.4094 | 31.6847 | 25.4983 | 43.3257 | 31.7222
SW | F074C_Miles-Condamine 33 kV | Loading (MVA) | 1.4406 | 2.4536 | 1.8093 | 1.4406 | 2.4536 | 1.8093 | 1.4406 | 2.4532 | 1.8093 | 1.4406 | 2.4535 | 1.8093 | 1.4407 | 2.4533 | 1.8093
SW | F074C_Miles-Condamine 33 kV | Loading (MW) | 1.4398 | 2.4536 | 1.8056 | 1.4399 | 2.4536 | 1.8057 | 1.4399 | 2.4532 | 1.8057 | 1.4398 | 2.4535 | 1.8056 | 1.4399 | 2.4533 | 1.8057
SW | F074C_Miles-Condamine 33 kV | Power Factor | 0.99945 | 1 | 0.99797 | 0.99946 | 1 | 0.99798 | 0.99946 | 1 | 0.99799 | 0.99944 | 1 | 0.99796 | 0.99948 | 1 | 0.99801
SW | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263
SW | F074C_Miles-Condamine 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F074C_Miles-Condamine 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98922 | 0.98843 | 0.99873 | 0.98884 | 0.98806 | 0.99843 | 0.98875 | 0.99132 | 0.99837 | 0.98951 | 0.98875 | 0.99904 | 0.988 | 0.99055 | 0.99785
SW | F075S_St George Town 33 kV | % of Rated A | 63.57% | 66.93% | 44.61% | 63.55% | 66.95% | 44.6% | 62.47% | 65.8% | 43.85% | 62.48% | 65.81% | 43.85% | 62.46% | 65.8% | 43.85%
SW | F075S_St George Town 33 kV | Limiting Line Name | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1
SW | F075S_St George Town 33 kV | Loading (A) | 104.2497 | 109.7581 | 73.1596 | 104.2242 | 109.7905 | 73.1496 | 102.4443 | 107.9161 | 71.9135 | 102.4605 | 107.9358 | 71.9211 | 102.4406 | 107.9116 | 71.9124
SW | F075S_St George Town 33 kV | Loading (MVA) | 5.9371 | 6.2732 | 4.1384 | 5.9369 | 6.2734 | 4.1384 | 5.8342 | 6.1646 | 4.068 | 5.8342 | 6.1647 | 4.068 | 5.8341 | 6.1646 | 4.068
SW | F075S_St George Town 33 kV | Loading (MW) | 5.7538 | 6.0741 | 4.0286 | 5.7537 | 6.0742 | 4.0286 | 5.6556 | 5.9705 | 3.9608 | 5.6556 | 5.9706 | 3.9608 | 5.6556 | 5.9705 | 3.9608
SW | F075S_St George Town 33 kV | Power Factor | 0.96908 | 0.96821 | 0.97347 | 0.96909 | 0.9682 | 0.97347 | 0.96934 | 0.96847 | 0.97365 | 0.96934 | 0.96846 | 0.97364 | 0.96934 | 0.96847 | 0.97365
SW | F075S_St George Town 33 kV | Rating (A) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
SW | F075S_St George Town 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F075S_St George Town 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99637 | 0.99996 | 0.98546 | 0.9966 | 0.99969 | 0.98559 | 0.99636 | 0.99941 | 0.98556 | 0.99621 | 0.99924 | 0.98546 | 0.99639 | 0.99945 | 0.98557
SW | F077C_Wandoan 33 kV | % of Rated A | 43.57% | 28.88% | 19.55% | 43.59% | 28.8% | 19.55% | 43.6% | 28.81% | 19.56% | 43.56% | 28.78% | 19.54% | 43.64% | 28.83% | 19.57%
SW | F077C_Wandoan 33 kV | Limiting Line Name | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1
SW | F077C_Wandoan 33 kV | Loading (A) | 75.3809 | 80.2852 | 54.3408 | 75.4149 | 80.0733 | 54.3597 | 75.4227 | 80.0814 | 54.3635 | 75.3548 | 80.001 | 54.3213 | 75.4908 | 80.161 | 54.3959
SW | F077C_Wandoan 33 kV | Loading (MVA) | 4.1676 | 4.4057 | 3.0454 | 4.1678 | 4.4078 | 3.0455 | 4.1679 | 4.4079 | 3.0455 | 4.1675 | 4.4073 | 3.0453 | 4.1683 | 4.4084 | 3.0457
SW | F077C_Wandoan 33 kV | Loading (MW) | 4.0477 | 4.2799 | 2.9806 | 4.0478 | 4.2811 | 2.9807 | 4.0479 | 4.2811 | 2.9807 | 4.0476 | 4.2808 | 2.9806 | 4.0481 | 4.2814 | 2.9808
SW | F077C_Wandoan 33 kV | Power Factor | 0.97123 | 0.97145 | 0.97873 | 0.9712 | 0.97125 | 0.97872 | 0.9712 | 0.97125 | 0.97871 | 0.97125 | 0.9713 | 0.97875 | 0.97115 | 0.97119 | 0.97869
SW | F077C_Wandoan 33 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | F077C_Wandoan 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F077C_Wandoan 33 kV | Min Voltage at Constrained Conductor (pu) | 0.96721 | 0.96 | 0.98044 | 0.96683 | 0.963 | 0.98013 | 0.96674 | 0.96291 | 0.98007 | 0.96751 | 0.96376 | 0.98076 | 0.96597 | 0.96208 | 0.97954
SW | F077S_Main Camp 33 kV | % of Rated A | 80.76% | 59.86% | 48.19% | 80.74% | 59.85% | 48.18% | 80.76% | 59.87% | 48.19% | 80.76% | 59.88% | 48.2% | 80.75% | 59.86% | 48.19%
SW | F077S_Main Camp 33 kV | Limiting Line Name | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1
SW | F077S_Main Camp 33 kV | Loading (A) | 80.7563 | 59.8641 | 48.1906 | 80.7443 | 59.8469 | 48.183 | 80.7558 | 59.8661 | 48.1917 | 80.7631 | 59.8786 | 48.1976 | 80.7545 | 59.8636 | 48.1909
SW | F077S_Main Camp 33 kV | Loading (MVA) | 4.6166 | 3.416 | 2.7333 | 4.6165 | 3.4158 | 2.7332 | 4.6166 | 3.416 | 2.7333 | 4.6167 | 3.4161 | 2.7334 | 4.6166 | 3.416 | 2.7333
SW | F077S_Main Camp 33 kV | Loading (MW) | 4.0931 | 3.1234 | 2.557 | 4.0931 | 3.1234 | 2.5569 | 4.0931 | 3.1234 | 2.557 | 4.0932 | 3.1234 | 2.557 | 4.0931 | 3.1234 | 2.557
SW | F077S_Main Camp 33 kV | Power Factor | 0.88656 | 0.91429 | 0.93541 | 0.88659 | 0.91433 | 0.93543 | 0.88656 | 0.91428 | 0.9354 | 0.88655 | 0.91425 | 0.93539 | 0.88657 | 0.91429 | 0.93541
SW | F077S_Main Camp 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | F077S_Main Camp 33 kV | Time | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00
SW | F077S_Main Camp 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0002 | 0.99833 | 0.99232 | 1.0003 | 0.99856 | 0.99245 | 1.0002 | 0.9983 | 0.9923 | 1.0001 | 0.99813 | 0.9922 | 1.0002 | 0.99833 | 0.99231
SW | F079S_St George Meatworks 33 kV | % of Rated A | 43.54% | 50.77% | 44.04% | 43.53% | 50.76% | 44.04% | 43.54% | 50.77% | 44.04% | 43.54% | 50.78% | 44.04% | 43.53% | 50.77% | 44.04%
SW | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1
SW | F079S_St George Meatworks 33 kV | Loading (A) | 43.5354 | 50.7687 | 44.0402 | 43.5268 | 50.758 | 44.0351 | 43.536 | 50.7703 | 44.0409 | 43.5416 | 50.7785 | 44.0448 | 43.5347 | 50.7693 | 44.0404
SW | F079S_St George Meatworks 33 kV | Loading (MVA) | 2.4794 | 2.8973 | 2.4979 | 2.4795 | 2.8974 | 2.498 | 2.4794 | 2.8973 | 2.4979 | 2.4794 | 2.8973 | 2.4979 | 2.4794 | 2.8973 | 2.4979
SW | F079S_St George Meatworks 33 kV | Loading (MW) | 2.4788 | 2.8951 | 2.4975 | 2.4789 | 2.8951 | 2.4976 | 2.4788 | 2.8951 | 2.4975 | 2.4788 | 2.895 | 2.4975 | 2.4788 | 2.8951 | 2.4975
SW | F079S_St George Meatworks 33 kV | Power Factor | 0.99976 | 0.99916 | 0.99984 | 0.99976 | 0.99917 | 0.99984 | 0.99976 | 0.99916 | 0.99984 | 0.99977 | 0.99916 | 0.99984 | 0.99976 | 0.99916 | 0.99984
SW | F079S_St George Meatworks 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | F079S_St George Meatworks 33 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
SW | F079S_St George Meatworks 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99639 | 0.99846 | 0.99232 | 0.99661 | 0.99868 | 0.99245 | 0.99637 | 0.99842 | 0.9923 | 0.99623 | 0.99825 | 0.9922 | 0.99641 | 0.99844 | 0.99232
SW | F083C_Chinchilla 33 kV | % of Rated A | 75.11% | 82.53% | 59.52% | 75.13% | 82.51% | 59.54% | 75.14% | 82.51% | 59.54% | 75.13% | 82.5% | 59.53% | 76.66% | 84.2% | 60.72%
SW | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1
SW | F083C_Chinchilla 33 kV | Loading (A) | 250.8512 | 278.1299 | 173.8028 | 250.9411 | 278.0481 | 173.8531 | 250.9616 | 278.0732 | 173.863 | 250.9216 | 278.0245 | 173.8281 | 256.0403 | 283.7452 | 177.2968
SW | F083C_Chinchilla 33 kV | Loading (MVA) | 14.4183 | 15.9604 | 10.0137 | 14.4185 | 15.9602 | 10.0138 | 14.4186 | 15.9603 | 10.0138 | 14.4185 | 15.9601 | 10.0137 | 14.6986 | 16.274 | 10.2066
SW | F083C_Chinchilla 33 kV | Loading (MW) | 14.121 | 15.6036 | 9.8539 | 14.1211 | 15.6035 | 9.8539 | 14.1211 | 15.6035 | 9.8539 | 14.1211 | 15.6035 | 9.8539 | 14.3906 | 15.9037 | 10.0414
SW | F083C_Chinchilla 33 kV | Power Factor | 0.97938 | 0.97764 | 0.98404 | 0.97937 | 0.97765 | 0.98403 | 0.97937 | 0.97765 | 0.98403 | 0.97938 | 0.97765 | 0.98404 | 0.97905 | 0.97724 | 0.98381
SW | F083C_Chinchilla 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | F083C_Chinchilla 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F083C_Chinchilla 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0049 | 1.0032 | 1.0076 | 1.0046 | 1.0035 | 1.0073 | 1.0045 | 1.0034 | 1.0072 | 1.0047 | 1.0036 | 1.0074 | 1.0037 | 1.0027 | 1.0067
SW | F106R_Roma East 33 kV | % of Rated A | 88.98% | 88.41% | 62.82% | 93.72% | 93.12% | 66.07% | 93.72% | 93.11% | 66.07% | 92.11% | 91.43% | 64.95% | 93.74% | 93.13% | 66.07%
SW | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2
SW | F106R_Roma East 33 kV | Loading (A) | 227.7982 | 225.435 | 137.5747 | 239.936 | 237.4465 | 144.6932 | 239.9133 | 237.4208 | 144.6875 | 235.7965 | 233.1354 | 142.2356 | 239.9734 | 237.481 | 144.7032
SW | F106R_Roma East 33 kV | Loading (MVA) | 12.5089 | 12.3492 | 7.6164 | 13.1338 | 12.966 | 7.9962 | 13.1337 | 12.966 | 7.9962 | 12.9305 | 12.757 | 7.8694 | 13.1339 | 12.9661 | 7.9962
SW | F106R_Roma East 33 kV | Loading (MW) | 12.089 | 11.9366 | 7.4138 | 12.6854 | 12.5254 | 7.7789 | 12.6854 | 12.5254 | 7.7789 | 12.4874 | 12.3285 | 7.6572 | 12.6854 | 12.5255 | 7.779
SW | F106R_Roma East 33 kV | Power Factor | 0.96643 | 0.96659 | 0.97339 | 0.96586 | 0.96602 | 0.97283 | 0.96586 | 0.96602 | 0.97284 | 0.96573 | 0.96641 | 0.97303 | 0.96585 | 0.96601 | 0.97283
SW | F106R_Roma East 33 kV | Rating (A) | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219
SW | F106R_Roma East 33 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
SW | F106R_Roma East 33 kV | Min Voltage at Constrained Conductor (pu) | 0.95958 | 0.95726 | 0.96791 | 0.95647 | 0.95417 | 0.96614 | 0.95656 | 0.95426 | 0.96618 | 0.95822 | 0.95617 | 0.96727 | 0.95633 | 0.95403 | 0.96608
SW | F127R_Roma West 33 kV | % of Rated A | 85.29% | 66.55% | 44.09% | 85.48% | 66.49% | 44.14% | 85.47% | 66.48% | 44.14% | 83.79% | 65.16% | 43.3% | 85.49% | 66.5% | 44.14%
SW | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1
SW | F127R_Roma West 33 kV | Loading (A) | 98.9328 | 106.4799 | 68.7732 | 99.1535 | 106.3869 | 68.858 | 99.1443 | 106.3728 | 68.8553 | 97.1921 | 104.2526 | 67.5512 | 99.1687 | 106.4022 | 68.8628
SW | F127R_Roma West 33 kV | Loading (MVA) | 5.4174 | 5.7915 | 3.7933 | 5.4178 | 5.7939 | 3.7934 | 5.4178 | 5.7939 | 3.7934 | 5.3209 | 5.69 | 3.726 | 5.4179 | 5.794 | 3.7934
SW | F127R_Roma West 33 kV | Loading (MW) | 5.3118 | 5.675 | 3.7311 | 5.312 | 5.6757 | 3.7311 | 5.312 | 5.6757 | 3.7311 | 5.2182 | 5.5754 | 3.6654 | 5.312 | 5.6757 | 3.7311
SW | F127R_Roma West 33 kV | Power Factor | 0.98051 | 0.97989 | 0.98361 | 0.98046 | 0.9796 | 0.98359 | 0.98046 | 0.9796 | 0.98359 | 0.9807 | 0.97987 | 0.98373 | 0.98046 | 0.9796 | 0.98359
SW | F127R_Roma West 33 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
SW | F127R_Roma West 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F127R_Roma West 33 kV | Min Voltage at Constrained Conductor (pu) | 0.958 | 0.95154 | 0.96496 | 0.95593 | 0.95278 | 0.9638 | 0.95602 | 0.9529 | 0.96383 | 0.95777 | 0.95484 | 0.96499 | 0.95579 | 0.95265 | 0.96373
SW | F217R_St George 66 kV | % of Rated A | 34.95% | 38.09% | 34.61% | 35.07% | 37.94% | 34.69% | 34.8% | 37.64% | 34.48% | 34.72% | 37.55% | 34.42% | 34.82% | 37.68% | 34.49%
SW | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW | F217R_St George 66 kV | Loading (A) | 156.2222 | 172.9266 | 137.0568 | 156.7753 | 172.2498 | 137.3632 | 155.5459 | 170.8861 | 136.5574 | 155.1881 | 170.4674 | 136.3227 | 155.626 | 171.0782 | 136.5917
SW | F217R_St George 66 kV | Loading (MVA) | 17.5602 | 19.3565 | 15.5007 | 17.5983 | 19.3113 | 15.5227 | 17.4616 | 19.1606 | 15.4321 | 17.4369 | 19.1326 | 15.4151 | 17.4671 | 19.101 | 15.4345
SW | F217R_St George 66 kV | Loading (MW) | 16.2634 | 18.0736 | 14.2402 | 16.2815 | 18.049 | 14.2488 | 16.1406 | 17.8931 | 14.1563 | 16.129 | 17.878 | 14.1497 | 16.1432 | 17.7692 | 14.1572
SW | F217R_St George 66 kV | Power Factor | 0.92611 | 0.93368 | 0.91865 | 0.92513 | 0.93459 | 0.9179 | 0.92431 | 0.9338 | 0.9173 | 0.92495 | 0.93438 | 0.91788 | 0.92417 | 0.93023 | 0.91721
SW | F217R_St George 66 kV | Rating (A) | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396
SW | F217R_St George 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F217R_St George 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98328 | 0.97916 | 0.98933 | 0.98194 | 0.98071 | 0.98853 | 0.98201 | 0.98083 | 0.98856 | 0.98288 | 0.9818 | 0.98917 | 0.98182 | 0.97668 | 0.98847
SW | F7164 | % of Rated A | 79.27% | 51.2% | 42.98% | 80.1% | 51.5% | 43.27% | 79.92% | 51.38% | 43.2% | 79.38% | 51.02% | 42.99% | 79.94% | 51.43% | 43.2%
SW | F7164 | Limiting Line Name | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1
SW | F7164 | Loading (A) | 137.145 | 142.3403 | 119.4763 | 138.5683 | 143.1814 | 120.2792 | 138.2628 | 142.8406 | 120.0851 | 137.329 | 141.8326 | 119.5128 | 138.2988 | 142.9727 | 120.0995
SW | F7164 | Loading (MVA) | 32.8023 | 33.9565 | 28.5064 | 33.1196 | 34.2366 | 28.6845 | 33.0459 | 34.1548 | 28.6376 | 32.8374 | 33.9307 | 28.512 | 33.0478 | 34.0277 | 28.6383
SW | F7164 | Loading (MW) | 32.4992 | 33.7007 | 27.7612 | 32.8441 | 34.0033 | 27.9649 | 32.768 | 33.9188 | 27.9155 | 32.5415 | 33.6764 | 27.7714 | 32.7702 | 33.7864 | 27.9163
SW | F7164 | Power Factor | 0.99076 | 0.99247 | 0.97386 | 0.99168 | 0.99319 | 0.97491 | 0.99159 | 0.99309 | 0.97479 | 0.99099 | 0.9925 | 0.97403 | 0.9916 | 0.99291 | 0.97479
SW | F7164 | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | F7164 | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F7164 | Min Voltage at Constrained Conductor (pu) | 1.0161 | 1.0115 | 1.023 | 1.0145 | 1.0132 | 1.0221 | 1.0146 | 1.0133 | 1.0221 | 1.0156 | 1.0144 | 1.0228 | 1.0144 | 1.0087 | 1.022
SW | F7174 | % of Rated A | 79.31% | 51.22% | 43% | 80.13% | 51.53% | 43.29% | 79.96% | 51.4% | 43.22% | 79.42% | 51.04% | 43.01% | 79.98% | 51.45% | 43.22%
SW | F7174 | Limiting Line Name | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1)
SW | F7174 | Loading (A) | 137.2069 | 142.4047 | 119.529 | 138.6309 | 143.2463 | 120.3324 | 138.3252 | 142.9053 | 120.1382 | 137.391 | 141.8968 | 119.5656 | 138.3613 | 143.0374 | 120.1526
SW | F7174 | Loading (MVA) | 32.8171 | 33.9718 | 28.519 | 33.1345 | 34.2521 | 28.6972 | 33.0608 | 34.1703 | 28.6503 | 32.8522 | 33.9461 | 28.5245 | 33.0627 | 34.0432 | 28.6509
SW | F7174 | Loading (MW) | 32.5142 | 33.7162 | 27.774 | 32.8593 | 34.019 | 27.9778 | 32.7832 | 33.9344 | 27.9284 | 32.5565 | 33.6919 | 27.7842 | 32.7853 | 33.802 | 27.9292
SW | F7174 | Power Factor | 0.99077 | 0.99248 | 0.97388 | 0.99169 | 0.99319 | 0.97493 | 0.9916 | 0.9931 | 0.97481 | 0.991 | 0.99251 | 0.97405 | 0.99161 | 0.99292 | 0.97481
SW | F7174 | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | F7174 | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F7174 | Min Voltage at Constrained Conductor (pu) | 1.0161 | 1.0115 | 1.023 | 1.0145 | 1.0132 | 1.0221 | 1.0146 | 1.0133 | 1.0221 | 1.0156 | 1.0144 | 1.0228 | 1.0144 | 1.0087 | 1.022
SW | F7490 | % of Rated A | 35.53% | 36.81% | 31.26% | 35.87% | 37.01% | 31.46% | 35.79% | 36.93% | 31.41% | 35.57% | 36.69% | 31.27% | 35.8% | 36.97% | 31.41%
SW | F7490 | Limiting Line Name | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b
SW | F7490 | Loading (A) | 138.9086 | 143.9458 | 122.2416 | 140.2538 | 144.7271 | 122.993 | 139.9565 | 144.3959 | 122.8052 | 139.0739 | 143.4423 | 122.2702 | 139.9914 | 144.534 | 122.8191
SW | F7490 | Loading (MVA) | 33.5762 | 34.7371 | 29.3464 | 33.8906 | 35.016 | 29.5189 | 33.8163 | 34.9335 | 29.4723 | 33.6097 | 34.7106 | 29.3508 | 33.8181 | 34.8054 | 29.4728
SW | F7490 | Loading (MW) | 33.0537 | 34.2961 | 28.1886 | 33.4096 | 34.6054 | 28.3977 | 33.3312 | 34.5182 | 28.347 | 33.0974 | 34.2678 | 28.199 | 33.3336 | 34.3868 | 28.3479
SW | F7490 | Power Factor | 0.98444 | 0.9873 | 0.96055 | 0.98581 | 0.98827 | 0.96202 | 0.98565 | 0.98811 | 0.96182 | 0.98476 | 0.98724 | 0.96076 | 0.98567 | 0.98797 | 0.96183
SW | F7490 | Rating (A) | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SW | F7490 | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F7490 | Min Voltage at Constrained Conductor (pu) | 1.0461 | 1.0434 | 1.0436 | 1.0454 | 1.0458 | 1.0431 | 1.0454 | 1.0458 | 1.0431 | 1.0459 | 1.0464 | 1.0435 | 1.0452 | 1.041 | 1.043
SW | F7491 | % of Rated A | 35.48% | 36.77% | 31.23% | 35.83% | 36.97% | 31.42% | 35.75% | 36.89% | 31.37% | 35.53% | 36.64% | 31.23% | 35.76% | 36.92% | 31.37%
SW | F7491 | Limiting Line Name | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1
SW | F7491 | Loading (A) | 138.7427 | 143.7737 | 122.0972 | 140.0862 | 144.5539 | 122.8476 | 139.7893 | 144.2231 | 122.6601 | 138.9078 | 143.2707 | 122.1257 | 139.8241 | 144.3611 | 122.674
SW | F7491 | Loading (MVA) | 33.5362 | 34.6956 | 29.3118 | 33.8501 | 34.9741 | 29.484 | 33.7758 | 34.8917 | 29.4375 | 33.5696 | 34.6691 | 29.3161 | 33.7777 | 34.7637 | 29.438
SW | F7491 | Loading (MW) | 33.0137 | 34.2546 | 28.1545 | 33.3692 | 34.5636 | 28.3634 | 33.2908 | 34.4764 | 28.3127 | 33.0573 | 34.2263 | 28.1649 | 33.2932 | 34.3452 | 28.3136
SW | F7491 | Power Factor | 0.98442 | 0.98729 | 0.96052 | 0.98579 | 0.98826 | 0.96199 | 0.98564 | 0.9881 | 0.96179 | 0.98474 | 0.98723 | 0.96073 | 0.98566 | 0.98796 | 0.9618
SW | F7491 | Rating (A) | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SW | F7491 | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F7491 | Min Voltage at Constrained Conductor (pu) | 1.0461 | 1.0434 | 1.0436 | 1.0454 | 1.0458 | 1.0431 | 1.0454 | 1.0458 | 1.0431 | 1.0459 | 1.0464 | 1.0435 | 1.0452 | 1.041 | 1.043
SW | 3153_Cecil Plains Road 33 kV | % of Rated A | 62.98% | 54.87% | 57.02% | 62.98% | 54.87% | 57.02% | 62.96% | 54.87% | 56.99% | 62.92% | 54.83% | 57% | 62.96% | 54.86% | 56.99%
SW | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1
SW | 3153_Cecil Plains Road 33 kV | Loading (A) | 58.576 | 54.8706 | 57.017 | 58.5721 | 54.8697 | 57.0174 | 58.554 | 54.8676 | 56.993 | 58.5194 | 54.8269 | 56.9977 | 58.5567 | 54.8634 | 56.9903
SW | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 3.4173 | 3.2217 | 3.3366 | 3.4173 | 3.2217 | 3.3366 | 3.4172 | 3.2217 | 3.3365 | 3.4171 | 3.2215 | 3.3366 | 3.4173 | 3.2217 | 3.3365
SW | 3153_Cecil Plains Road 33 kV | Loading (MW) | 3.2705 | 3.1094 | 3.2245 | 3.2705 | 3.1094 | 3.2245 | 3.2705 | 3.1094 | 3.2245 | 3.2705 | 3.1093 | 3.2245 | 3.2705 | 3.1094 | 3.2245
SW | 3153_Cecil Plains Road 33 kV | Power Factor | 0.95703 | 0.96496 | 0.96624 | 0.95704 | 0.96496 | 0.96624 | 0.95706 | 0.96496 | 0.96626 | 0.95709 | 0.965 | 0.96625 | 0.95705 | 0.96496 | 0.96626
SW | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW | 3153_Cecil Plains Road 33 kV | Time | 14:00:00 | 20:00:00 | 00:00:00 | 14:00:00 | 20:00:00 | 00:00:00 | 14:00:00 | 20:00:00 | 00:00:00 | 14:00:00 | 20:00:00 | 00:00:00 | 14:00:00 | 20:00:00 | 00:00:00
SW | 3153_Cecil Plains Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0206 | 1.0272 | 1.0238 | 1.0207 | 1.0273 | 1.0238 | 1.021 | 1.0273 | 1.0242 | 1.0215 | 1.028 | 1.0242 | 1.0209 | 1.0274 | 1.0243
SW | 3154_Central Dalby 1 33 kV | % of Rated A | 40.63% | 42.83% | 26.73% | 40.34% | 42.51% | 26.55% | 40.07% | 42.23% | 26.37% | 39.66% | 41.81% | 26.11% | 39.97% | 41.91% | 26.28%
SW | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1
SW | 3154_Central Dalby 1 33 kV | Loading (A) | 182.8493 | 192.7152 | 109.6003 | 181.5373 | 191.2972 | 108.8418 | 180.3348 | 190.0423 | 108.1309 | 178.4534 | 188.1607 | 107.04 | 179.8609 | 188.5774 | 107.7371
SW | 3154_Central Dalby 1 33 kV | Loading (MVA) | 10.4593 | 10.9607 | 6.3922 | 10.386 | 10.8818 | 6.3481 | 10.3184 | 10.8116 | 6.3068 | 10.2209 | 10.7143 | 6.2469 | 10.2909 | 10.7833 | 6.2844
SW | 3154_Central Dalby 1 33 kV | Loading (MW) | 10.1925 | 10.67 | 6.2804 | 10.1231 | 10.5957 | 6.2377 | 10.0584 | 10.5286 | 6.1976 | 9.9678 | 10.4344 | 6.1406 | 10.0308 | 10.4985 | 6.175
SW | 3154_Central Dalby 1 33 kV | Power Factor | 0.97428 | 0.97327 | 0.98251 | 0.97448 | 0.97349 | 0.98262 | 0.97459 | 0.97361 | 0.98268 | 0.97503 | 0.97367 | 0.98298 | 0.97452 | 0.97338 | 0.98259
SW | 3154_Central Dalby 1 33 kV | Rating (A) | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410
SW | 3154_Central Dalby 1 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | 3154_Central Dalby 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0008 | 0.99506 | 1.0204 | 1.0009 | 0.99522 | 1.0204 | 1.0011 | 0.99533 | 1.0204 | 1.0021 | 0.99623 | 1.021 | 1.001 | 1.0004 | 1.0205
SW | 3178_Wilkie Creek 33 kV | % of Rated A | 4.182% | 4.149% | 4.18% | 4.182% | 4.149% | 4.182% | 4.183% | 4.156% | 4.182% | 4.184% | 4.151% | 4.183% | 4.182% | 4.156% | 4.182%
SW | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1
SW | 3178_Wilkie Creek 33 kV | Loading (A) | 3.8891 | 3.8588 | 3.8873 | 3.8897 | 3.859 | 3.8894 | 3.8897 | 3.8653 | 3.8893 | 3.8909 | 3.8602 | 3.8901 | 3.8892 | 3.8651 | 3.8892
SW | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.2249 | 0.22253 | 0.2242 | 0.22497 | 0.22256 | 0.22443 | 0.22498 | 0.22381 | 0.22443 | 0.22511 | 0.2227 | 0.22452 | 0.22491 | 0.22378 | 0.22446
SW | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0082584 | 0.012161 | 0.0065923 | 0.0082588 | 0.012161 | 0.0065607 | 0.0082589 | 0.014127 | 0.0065606 | 0.0082598 | 0.012162 | 0.0065613 | 0.0082584 | 0.014127 | 0.0066922
SW | 3178_Wilkie Creek 33 kV | Power Factor | 0.03672 | 0.054648 | 0.029403 | 0.036711 | 0.054642 | 0.029232 | 0.03671 | 0.063123 | 0.029233 | 0.036692 | 0.054612 | 0.029224 | 0.036718 | 0.063131 | 0.029815
SW | 3178_Wilkie Creek 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | 3178_Wilkie Creek 33 kV | Time | 13:00:00 | 21:30:00 | 04:30:00 | 13:00:00 | 21:30:00 | 04:00:00 | 13:00:00 | 20:00:00 | 04:00:00 | 13:00:00 | 21:30:00 | 04:00:00 | 13:00:00 | 20:00:00 | 03:30:00
SW | 3178_Wilkie Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0117 | 1.009 | 1.0091 | 1.0119 | 1.009 | 1.0096 | 1.0119 | 1.013 | 1.0096 | 1.0122 | 1.0093 | 1.0098 | 1.0118 | 1.0129 | 1.0097
SW | 3900_Peranga 33 kV | % of Rated A | 26.95% | 32.84% | 20.23% | 26.96% | 32.86% | 20.24% | 26.97% | 32.87% | 20.24% | 26.96% | 32.86% | 20.24% | 26.97% | 32.67% | 20.24%
SW | 3900_Peranga 33 kV | Limiting Line Name | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1
SW | 3900_Peranga 33 kV | Loading (A) | 26.9491 | 32.844 | 20.2348 | 26.9573 | 32.8557 | 20.237 | 26.9663 | 32.868 | 20.239 | 26.9614 | 32.8612 | 20.2375 | 26.974 | 32.668 | 20.241
SW | 3900_Peranga 33 kV | Loading (MVA) | 1.578 | 1.9189 | 1.1812 | 1.5781 | 1.919 | 1.1812 | 1.5782 | 1.9191 | 1.1812 | 1.5781 | 1.919 | 1.1812 | 1.5782 | 1.9175 | 1.1812
SW | 3900_Peranga 33 kV | Loading (MW) | 1.5162 | 1.8269 | 1.1495 | 1.5162 | 1.827 | 1.1495 | 1.5162 | 1.827 | 1.1495 | 1.5162 | 1.827 | 1.1495 | 1.5162 | 1.8264 | 1.1496
SW | 3900_Peranga 33 kV | Power Factor | 0.96067 | 0.95196 | 0.97305 | 0.96065 | 0.95193 | 0.97304 | 0.96062 | 0.9519 | 0.97303 | 0.96064 | 0.95192 | 0.97304 | 0.9606 | 0.9524 | 0.97302
SW | 3900_Peranga 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 3900_Peranga 33 kV | Time | 16:30:00 | 17:30:00 | 05:30:00 | 16:30:00 | 17:30:00 | 05:30:00 | 16:30:00 | 17:30:00 | 05:30:00 | 16:30:00 | 17:30:00 | 05:30:00 | 16:30:00 | 17:30:00 | 05:30:00
SW | 3900_Peranga 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0245 | 1.0222 | 1.0213 | 1.0242 | 1.0219 | 1.0212 | 1.0239 | 1.0215 | 1.0211 | 1.0241 | 1.0217 | 1.0212 | 1.0236 | 1.0269 | 1.021
SW | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 25.87% | 28.18% | 20.88% | 27.17% | 29.49% | 21.82% | 28.59% | 30.87% | 22.83% | 28.53% | 30.77% | 22.37% | 29.14% | 31.56% | 22.84%
SW | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 227.1034 | 271.6115 | 178.2977 | 238.578 | 284.2416 | 186.3047 | 250.9833 | 297.5487 | 194.9952 | 250.4535 | 296.5916 | 191.0006 | 255.8254 | 304.2052 | 195.0356
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 45.0723 | 53.6399 | 35.7217 | 47.302 | 56.0696 | 37.2988 | 49.7125 | 58.632 | 39.0151 | 49.6204 | 58.4624 | 38.2294 | 50.6485 | 59.793 | 39.0212
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 43.9982 | 51.9553 | 35.2116 | 45.9774 | 54.0403 | 36.6515 | 48.1654 | 56.3489 | 38.2625 | 48.1095 | 56.2392 | 37.5267 | 49.0586 | 57.4272 | 38.2763
SW | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.97617 | 0.9686 | 0.98559 | 0.972 | 0.96381 | 0.98263 | 0.96888 | 0.96106 | 0.98071 | 0.96955 | 0.96197 | 0.98162 | 0.96861 | 0.96043 | 0.98091
SW | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 7233_Middle Ridge-Torrington 110 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | 7233_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0385 | 1.032 | 1.0498 | 1.0371 | 1.0303 | 1.0488 | 1.0356 | 1.0288 | 1.0479 | 1.0359 | 1.0292 | 1.0484 | 1.035 | 1.026 | 1.0479
SW | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 26.8% | 29.19% | 21.63% | 28.15% | 30.55% | 22.6% | 29.62% | 31.98% | 23.66% | 29.55% | 31.88% | 23.17% | 30.19% | 32.7% | 23.66%
SW | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 235.2864 | 281.4062 | 184.7168 | 247.1814 | 294.4918 | 193.012 | 260.0341 | 308.2874 | 202.0154 | 259.4852 | 307.2958 | 197.8769 | 265.0509 | 315.1842 | 202.0572
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 46.6943 | 55.5693 | 37.0078 | 49.005 | 58.0856 | 38.6415 | 51.5016 | 60.7409 | 40.4193 | 51.4062 | 60.5652 | 39.6055 | 52.4711 | 61.9432 | 40.4256
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 45.6117 | 53.8634 | 36.4986 | 47.6644 | 56.0277 | 37.9931 | 49.9344 | 58.4201 | 39.6643 | 49.876 | 58.3059 | 38.901 | 50.8605 | 59.5383 | 39.6785
SW | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.97682 | 0.9693 | 0.98621 | 0.97264 | 0.96457 | 0.98322 | 0.96957 | 0.96179 | 0.98132 | 0.97023 | 0.9627 | 0.98221 | 0.96931 | 0.96118 | 0.98152
SW | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 7234_Middle Ridge-Torrington 110 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | 7234_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0382 | 1.0317 | 1.0496 | 1.0368 | 1.03 | 1.0486 | 1.0353 | 1.0284 | 1.0477 | 1.0356 | 1.0288 | 1.0482 | 1.0347 | 1.0256 | 1.0477
SW | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 27.01% | 27.71% | 20.39% | 27% | 27.72% | 20.38% | 27.05% | 27.79% | 20.42% | 27% | 27.75% | 20.39% | 27.35% | 28.08% | 20.57%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 277.8972 | 294.3198 | 194.3036 | 277.7954 | 294.3496 | 194.2317 | 278.3777 | 295.084 | 194.579 | 277.8324 | 294.6591 | 194.3177 | 281.4037 | 298.1636 | 196.0562
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 55.4462 | 58.4942 | 39.089 | 55.3924 | 58.4596 | 39.0586 | 55.4728 | 58.5637 | 39.1133 | 55.3758 | 58.4944 | 39.0707 | 56.0546 | 59.0348 | 39.4077
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 55.3468 | 58.4582 | 37.9857 | 55.2929 | 58.4217 | 37.954 | 55.3764 | 58.5281 | 38.0157 | 55.2756 | 58.4571 | 37.9631 | 55.9654 | 59.0028 | 38.3047
SW | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.99813 | 0.99933 | 0.97174 | 0.99812 | 0.9993 | 0.97169 | 0.99819 | 0.99934 | 0.97191 | 0.99811 | 0.99931 | 0.97162 | 0.99833 | 0.99941 | 0.97197
SW | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 728_Middle Ridge-South Toowoomba 110 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | 728_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0469 | 1.0428 | 1.0559 | 1.0463 | 1.0421 | 1.0555 | 1.0456 | 1.0413 | 1.0551 | 1.0458 | 1.0416 | 1.0553 | 1.0452 | 1.0388 | 1.055
SW | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 27.01% | 27.72% | 20.39% | 27% | 27.73% | 20.39% | 27.06% | 27.8% | 20.42% | 27.01% | 27.76% | 20.4% | 27.36% | 28.09% | 20.58%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 277.982 | 294.42 | 194.3623 | 277.8807 | 294.4505 | 194.2907 | 278.4638 | 295.1859 | 194.6386 | 277.9189 | 294.7615 | 194.3775 | 281.4931 | 298.2696 | 196.1179
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 55.4631 | 58.5142 | 39.1008 | 55.4094 | 58.4796 | 39.0704 | 55.4899 | 58.5839 | 39.1253 | 55.393 | 58.5148 | 39.0827 | 56.0724 | 59.0558 | 39.4201
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 55.3637 | 58.4781 | 37.9975 | 55.3098 | 58.4417 | 37.9659 | 55.3935 | 58.5483 | 38.0277 | 55.2928 | 58.4774 | 37.9752 | 55.9831 | 59.0238 | 38.3172
SW | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.99813 | 0.99933 | 0.97175 | 0.99812 | 0.9993 | 0.9717 | 0.99818 | 0.99934 | 0.97192 | 0.99811 | 0.99931 | 0.97163 | 0.99833 | 0.99941 | 0.97198
SW | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 730_Middle Ridge-South Toowoomba 110 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | 730_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0469 | 1.0428 | 1.0559 | 1.0463 | 1.0421 | 1.0555 | 1.0456 | 1.0413 | 1.0551 | 1.0458 | 1.0416 | 1.0553 | 1.0452 | 1.0388 | 1.055
SW | 7314_Dalby East 110 kV | % of Rated A | 4.921% | 4.422% | 4.943% | 4.965% | 4.516% | 4.993% | 4.965% | 4.516% | 4.993% | 4.966% | 4.518% | 4.995% | 4.922% | 4.422% | 4.947%
SW | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW | 7314_Dalby East 110 kV | Loading (A) | 12.9414 | 13.045 | 12.999 | 13.057 | 13.3224 | 13.1327 | 13.0569 | 13.3212 | 13.1317 | 13.06 | 13.3289 | 13.1364 | 12.944 | 13.0441 | 13.0117
SW | 7314_Dalby East 110 kV | Loading (MVA) | 2.5768 | 2.5367 | 2.595 | 2.5997 | 2.5812 | 2.5937 | 2.5997 | 2.5807 | 2.5933 | 2.6009 | 2.584 | 2.5952 | 2.5778 | 2.5363 | 2.5985
SW | 7314_Dalby East 110 kV | Loading (MW) | 0.59682 | 1.0792 | 0.56745 | 0.62512 | 1.178 | 0.93801 | 0.62512 | 1.178 | 0.93801 | 0.62512 | 1.178 | 0.93801 | 0.59682 | 1.0792 | 0.55158
SW | 7314_Dalby East 110 kV | Power Factor | 0.23161 | 0.42544 | 0.21867 | 0.24045 | 0.45637 | 0.36166 | 0.24046 | 0.45646 | 0.36171 | 0.24035 | 0.45587 | 0.36144 | 0.23152 | 0.4255 | 0.21226
SW | 7314_Dalby East 110 kV | Rating (A) | 263 | 295 | 263 | 263 | 295 | 263 | 263 | 295 | 263 | 263 | 295 | 263 | 263 | 295 | 263
SW | 7314_Dalby East 110 kV | Time | 06:00:00 | 19:30:00 | 04:30:00 | 06:00:00 | 19:00:00 | 22:00:00 | 06:00:00 | 19:00:00 | 22:00:00 | 06:00:00 | 19:00:00 | 22:00:00 | 06:00:00 | 19:30:00 | 04:00:00
SW | 7314_Dalby East 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0451 | 1.0206 | 1.0478 | 1.045 | 1.0169 | 1.0366 | 1.045 | 1.0168 | 1.0365 | 1.0453 | 1.0175 | 1.0369 | 1.0453 | 1.0206 | 1.0482
SW | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 17.12% | 14.6% | 9.081% | 17.04% | 14.55% | 9.061% | 16.96% | 14.49% | 9.042% | 16.79% | 14.37% | 9.004% | 17.05% | 14.56% | 9.061%
SW | 7448_South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1
SW | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 71.9122 | 61.3042 | 38.1403 | 71.587 | 61.09 | 38.0579 | 71.2374 | 60.8752 | 37.9757 | 70.539 | 60.3708 | 37.8164 | 71.5999 | 61.134 | 38.0563
SW | 7448_South Toowoomba-TWCE 110 kV | Loading (MVA) | 14.5131 | 12.2001 | 7.6787 | 14.4434 | 12.1486 | 7.659 | 14.3735 | 12.0971 | 7.6395 | 14.2337 | 12.0008 | 7.6095 | 14.4435 | 12.1449 | 7.6554
SW | 7448_South Toowoomba-TWCE 110 kV | Loading (MW) | 13.9871 | 11.842 | 5.9214 | 13.9214 | 11.7868 | 5.894 | 13.8557 | 11.7315 | 5.8667 | 13.7244 | 11.6213 | 5.8123 | 13.9214 | 11.7866 | 5.8939
SW | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 0.9619 | 0.97065 | 0.77114 | 0.962 | 0.97022 | 0.76955 | 0.9621 | 0.96977 | 0.76794 | 0.96232 | 0.96838 | 0.76382 | 0.96199 | 0.97049 | 0.76991
SW | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 7448_South Toowoomba-TWCE 110 kV | Time | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00 | 14:00:00 | 17:00:00 | 22:00:00
SW | 7448_South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0593 | 1.0445 | 1.0567 | 1.059 | 1.0438 | 1.0563 | 1.059 | 1.043 | 1.0559 | 1.0591 | 1.0433 | 1.0561 | 1.0588 | 1.0427 | 1.0558
SW | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 9.976% | 9.119% | 7.563% | 9.95% | 9.098% | 7.558% | 9.923% | 9.077% | 7.553% | 9.871% | 9.037% | 7.545% | 9.95% | 9.097% | 7.556%
SW | 7449 South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1
SW | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 41.8977 | 38.2979 | 31.7654 | 41.7881 | 38.2113 | 31.7427 | 41.6771 | 38.1247 | 31.7207 | 41.4562 | 37.9563 | 31.6882 | 41.789 | 38.2091 | 31.736
SW | 7449 South Toowoomba-TWCE 110 kV | Loading (MVA) | 8.4572 | 7.6216 | 6.4228 | 8.4327 | 7.5988 | 6.4168 | 8.4106 | 7.5761 | 6.4112 | 8.3667 | 7.5452 | 6.4052 | 8.4314 | 7.5907 | 6.4137
SW | 7449 South Toowoomba-TWCE 110 kV | Loading (MW) | 7.0985 | 5.9762 | 3.0158 | 7.0657 | 5.9485 | 3.0022 | 7.0329 | 5.9208 | 2.9885 | 6.9674 | 5.8659 | 2.9614 | 7.0656 | 5.9483 | 3.0021
SW | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 0.83935 | 0.78411 | 0.46955 | 0.83789 | 0.78282 | 0.46786 | 0.83619 | 0.78151 | 0.46615 | 0.83275 | 0.77744 | 0.46235 | 0.83801 | 0.78363 | 0.46808
SW | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 7449 South Toowoomba-TWCE 110 kV | Time | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00 | 14:00:00 | 17:00:00 | 05:30:00
SW | 7449 South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0595 | 1.0445 | 1.0612 | 1.0592 | 1.0438 | 1.061 | 1.0592 | 1.043 | 1.0608 | 1.0593 | 1.0433 | 1.0609 | 1.059 | 1.0427 | 1.0607
SW | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 27.66% | 31.94% | 27.32% | 27.67% | 31.95% | 27.33% | 27.69% | 31.97% | 27.33% | 27.68% | 31.94% | 27.32% | 28.04% | 32.43% | 27.65%
SW | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1
SW | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 66.118 | 80.1715 | 60.6491 | 66.1417 | 80.1985 | 60.6616 | 66.1737 | 80.2344 | 60.6754 | 66.1444 | 80.1792 | 60.6581 | 67.0149 | 81.4114 | 61.3742
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 12.9174 | 15.477 | 12.1083 | 12.9161 | 15.4769 | 12.1068 | 12.9144 | 15.4769 | 12.1052 | 12.916 | 15.477 | 12.1073 | 13.0658 | 15.6852 | 12.2391
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 12.6172 | 15.4156 | 11.5482 | 12.6176 | 15.4161 | 11.5484 | 12.6181 | 15.4168 | 11.5486 | 12.6176 | 15.4157 | 11.5483 | 12.7895 | 15.635 | 11.7077
SW | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.97676 | 0.99603 | 0.95374 | 0.97689 | 0.99607 | 0.95387 | 0.97706 | 0.99612 | 0.95402 | 0.9769 | 0.99604 | 0.95383 | 0.97886 | 0.9968 | 0.95659
SW | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 239 | 251 | 222 | 239 | 251 | 222 | 239 | 251 | 222 | 239 | 251 | 222 | 239 | 251 | 222
SW | 790_Warwick-Stanthorpe 110 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | 790_Warwick-Stanthorpe 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0254 | 1.0132 | 1.0478 | 1.0249 | 1.0128 | 1.0475 | 1.0243 | 1.0124 | 1.0471 | 1.0249 | 1.0131 | 1.0476 | 1.0233 | 1.0112 | 1.0466
SW | EB10_Acland 33 kV | % of Rated A | 12.21% | 8.968% | 7.049% | 12.21% | 8.972% | 7.05% | 12.21% | 8.975% | 7.052% | 12.21% | 8.973% | 7.05% | 12.21% | 8.977% | 7.052%
SW | EB10_Acland 33 kV | Limiting Line Name | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1
SW | EB10_Acland 33 kV | Loading (A) | 11.3542 | 8.3406 | 6.5552 | 11.3551 | 8.3437 | 6.5566 | 11.356 | 8.3469 | 6.5579 | 11.3553 | 8.3448 | 6.5568 | 11.3573 | 8.3489 | 6.5584
SW | EB10_Acland 33 kV | Loading (MVA) | 0.66794 | 0.48773 | 0.38174 | 0.66795 | 0.48775 | 0.38175 | 0.66796 | 0.48778 | 0.38176 | 0.66795 | 0.48776 | 0.38175 | 0.66797 | 0.48779 | 0.38176
SW | EB10_Acland 33 kV | Loading (MW) | 0.56274 | 0.41833 | 0.33192 | 0.56274 | 0.41833 | 0.33192 | 0.56274 | 0.41834 | 0.33192 | 0.56274 | 0.41833 | 0.33192 | 0.56275 | 0.41834 | 0.33192
SW | EB10_Acland 33 kV | Power Factor | 0.8399 | 0.85421 | 0.86506 | 0.8399 | 0.85418 | 0.86505 | 0.83989 | 0.85414 | 0.86503 | 0.83989 | 0.85416 | 0.86504 | 0.83988 | 0.85412 | 0.86502
SW | EB10_Acland 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | EB10_Acland 33 kV | Time | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00 | 12:00:00 | 17:00:00 | 22:00:00
SW | EB10_Acland 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0292 | 1.0231 | 1.0188 | 1.0292 | 1.0227 | 1.0187 | 1.0291 | 1.0224 | 1.0185 | 1.0291 | 1.0226 | 1.0186 | 1.029 | 1.0222 | 1.0184
SW | F008D_Central Dalby 2 33 kV | % of Rated A | 38.79% | 40.88% | 24.21% | 38.51% | 40.58% | 24.04% | 38.25% | 40.31% | 23.88% | 37.86% | 39.91% | 23.64% | 38.15% | 40% | 23.79%
SW | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1
SW | F008D_Central Dalby 2 33 kV | Loading (A) | 193.9379 | 204.3946 | 116.1859 | 192.5472 | 202.8915 | 115.3819 | 191.2726 | 201.5615 | 114.6285 | 189.2784 | 199.5671 | 113.4722 | 190.7703 | 200.0096 | 114.2111
SW | F008D_Central Dalby 2 33 kV | Loading (MVA) | 11.0936 | 11.625 | 6.8254 | 11.0159 | 11.5414 | 6.7778 | 10.9443 | 11.467 | 6.7334 | 10.8409 | 11.3638 | 6.6687 | 10.915 | 11.437 | 6.7092
SW | F008D_Central Dalby 2 33 kV | Loading (MW) | 10.5015 | 10.9879 | 6.5294 | 10.4311 | 10.9126 | 6.4852 | 10.3651 | 10.8442 | 6.4436 | 10.274 | 10.7475 | 6.385 | 10.3363 | 10.812 | 6.4195
SW | F008D_Central Dalby 2 33 kV | Power Factor | 0.94637 | 0.94493 | 0.95664 | 0.94665 | 0.94525 | 0.95683 | 0.94682 | 0.94542 | 0.95696 | 0.94744 | 0.9455 | 0.95746 | 0.94672 | 0.94509 | 0.95682
SW | F008D_Central Dalby 2 33 kV | Rating (A) | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480
SW | F008D_Central Dalby 2 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F008D_Central Dalby 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0008 | 0.99506 | 1.0204 | 1.0009 | 0.99522 | 1.0204 | 1.0011 | 0.99533 | 1.0205 | 1.0021 | 0.99623 | 1.0211 | 1.001 | 1.0004 | 1.0205
SW | F019D_West Dalby No 1 33 kV | % of Rated A | 44.97% | 43.09% | 27.46% | 44.73% | 42.85% | 27.32% | 44.43% | 42.57% | 27.14% | 44.02% | 42.19% | 26.89% | 44.27% | 42.19% | 27%
SW | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1
SW | F019D_West Dalby No 1 33 kV | Loading (A) | 168.6513 | 176.2368 | 101.0486 | 167.7548 | 175.2681 | 100.5351 | 166.6173 | 174.0946 | 99.8597 | 165.0631 | 172.5458 | 98.9526 | 166.0105 | 172.5444 | 99.3607
SW | F019D_West Dalby No 1 33 kV | Loading (MVA) | 9.7479 | 10.1359 | 5.9263 | 9.6967 | 10.0807 | 5.8959 | 9.6313 | 10.0134 | 5.8563 | 9.5496 | 9.9321 | 5.8061 | 9.5957 | 9.9739 | 5.8274
SW | F019D_West Dalby No 1 33 kV | Loading (MW) | 9.2574 | 9.6163 | 5.6951 | 9.2102 | 9.5657 | 5.6662 | 9.1499 | 9.5038 | 5.6288 | 9.0784 | 9.4293 | 5.5833 | 9.1155 | 9.4654 | 5.6003
SW | F019D_West Dalby No 1 33 kV | Power Factor | 0.94969 | 0.94874 | 0.96099 | 0.94983 | 0.94892 | 0.96104 | 0.95001 | 0.9491 | 0.96115 | 0.95066 | 0.94937 | 0.96163 | 0.94995 | 0.94902 | 0.96102
SW | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368
SW | F019D_West Dalby No 1 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F019D_West Dalby No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0078 | 1.0026 | 1.0242 | 1.0079 | 1.0027 | 1.0242 | 1.0079 | 1.0027 | 1.0242 | 1.0088 | 1.0035 | 1.0248 | 1.0079 | 1.0078 | 1.0243
SW | F039D_West Dalby No 2 33 kV | % of Rated A | 31.75% | 29.57% | 18.23% | 31.99% | 29.9% | 18.41% | 31.76% | 29.67% | 18.26% | 31.58% | 29.63% | 18.23% | 31.52% | 29.09% | 17.98%
SW | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1
SW | F039D_West Dalby No 2 33 kV | Loading (A) | 90.1669 | 83.9775 | 51.7694 | 90.8537 | 84.904 | 52.2824 | 90.2021 | 84.2522 | 51.8608 | 89.6951 | 84.1584 | 51.7823 | 89.5223 | 82.6201 | 51.0711
SW | F039D_West Dalby No 2 33 kV | Loading (MVA) | 5.2208 | 4.7656 | 3.015 | 5.2611 | 4.8189 | 3.0448 | 5.2244 | 4.7825 | 3.0204 | 5.1989 | 4.7816 | 3.0177 | 5.1848 | 4.7142 | 2.9748
SW | F039D_West Dalby No 2 33 kV | Loading (MW) | 4.9853 | 4.6064 | 2.9057 | 5.0234 | 4.6561 | 2.9343 | 4.9876 | 4.6206 | 2.9106 | 4.9719 | 4.6266 | 2.9108 | 4.9471 | 4.5569 | 2.8643
SW | F039D_West Dalby No 2 33 kV | Power Factor | 0.95477 | 0.96647 | 0.96359 | 0.9547 | 0.9661 | 0.96353 | 0.95456 | 0.96603 | 0.96347 | 0.95622 | 0.96747 | 0.96443 | 0.95403 | 0.96652 | 0.9627
SW | F039D_West Dalby No 2 33 kV | Rating (A) | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284
SW | F039D_West Dalby No 2 33 kV | Time | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00 | 15:00:00 | 17:30:00 | 22:00:00
SW | F039D_West Dalby No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.013 | 0.99285 | 1.0189 | 1.0131 | 0.99298 | 1.0189 | 1.0133 | 0.99311 | 1.019 | 1.0141 | 0.99403 | 1.0196 | 1.0133 | 0.99826 | 1.0191
SW | F095D_Kaimkillenbun 33 kV | % of Rated A | 23.67% | 24.96% | 21.05% | 23.67% | 24.95% | 21.05% | 23.67% | 24.95% | 21.05% | 23.65% | 24.93% | 21.04% | 23.67% | 24.95% | 21.05%
SW | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_LINE 23016_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23016_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23016_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23016_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23016_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1
SW | F095D_Kaimkillenbun 33 kV | Loading (A) | 22.0116 | 24.9557 | 21.0527 | 22.0107 | 24.955 | 21.0537 | 22.0105 | 24.9518 | 21.0543 | 21.9918 | 24.9342 | 21.0436 | 22.0123 | 24.9477 | 21.0529
SW | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 1.2756 | 1.4454 | 1.2382 | 1.2756 | 1.4454 | 1.2382 | 1.2756 | 1.4454 | 1.2382 | 1.2755 | 1.4456 | 1.2382 | 1.2756 | 1.4454 | 1.2382
SW | F095D_Kaimkillenbun 33 kV | Loading (MW) | 1.2743 | 1.4434 | 1.2382 | 1.2743 | 1.4434 | 1.2382 | 1.2743 | 1.4434 | 1.2382 | 1.2743 | 1.4435 | 1.2381 | 1.2743 | 1.4434 | 1.2382
SW | F095D_Kaimkillenbun 33 kV | Power Factor | 0.99885 | 0.99826 | 0.99989 | 0.99885 | 0.99826 | 0.99989 | 0.99885 | 0.99826 | 0.99989 | 0.99887 | 0.99817 | 0.9999 | 0.99885 | 0.99827 | 0.99989
SW | F095D_Kaimkillenbun 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW | F095D_Kaimkillenbun 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F095D_Kaimkillenbun 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0128 | 1.0133 | 1.029 | 1.0129 | 1.0134 | 1.0289 | 1.0129 | 1.0135 | 1.0289 | 1.0137 | 1.0143 | 1.0294 | 1.0128 | 1.0136 | 1.029
SW | F097D_Jandowae 33 kV | % of Rated A | 43.9% | 33.35% | 21.88% | 43.89% | 33.35% | 21.88% | 43.88% | 33.34% | 21.88% | 42.87% | 32.62% | 21.43% | 42.77% | 32.45% | 21.26%
SW | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3
SW | F097D_Jandowae 33 kV | Loading (A) | 62.7713 | 70.7066 | 45.7229 | 62.7614 | 70.7012 | 45.7227 | 62.7514 | 70.6785 | 45.7204 | 61.3062 | 69.1499 | 44.7896 | 61.162 | 68.7881 | 44.4351
SW | F097D_Jandowae 33 kV | Loading (MVA) | 3.5719 | 4.0008 | 2.6566 | 3.5718 | 4.0008 | 2.6566 | 3.5718 | 4.0006 | 2.6566 | 3.4933 | 3.9188 | 2.6042 | 3.4813 | 3.8938 | 2.5822
SW | F097D_Jandowae 33 kV | Loading (MW) | 3.3811 | 3.7863 | 2.5568 | 3.3811 | 3.7863 | 2.5568 | 3.3811 | 3.7863 | 2.5568 | 3.3161 | 3.7188 | 2.5121 | 3.2913 | 3.6818 | 2.4824
SW | F097D_Jandowae 33 kV | Power Factor | 0.94657 | 0.94639 | 0.96207 | 0.94658 | 0.9464 | 0.96207 | 0.94659 | 0.94642 | 0.96207 | 0.94923 | 0.94895 | 0.96428 | 0.94536 | 0.94555 | 0.96097
SW | F097D_Jandowae 33 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
SW | F097D_Jandowae 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F097D_Jandowae 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99356 | 0.98754 | 1.0155 | 0.9937 | 0.98761 | 1.0155 | 0.99384 | 0.98789 | 1.0155 | 0.99498 | 0.98916 | 1.0162 | 0.99393 | 0.98804 | 1.0157
SW | F099D_Warra 33 kV | % of Rated A | 56.25% | 43.27% | 22.12% | 56.25% | 43.27% | 22.12% | 56.24% | 43.26% | 22.12% | 56.22% | 43.21% | 22.11% | 56.24% | 43.26% | 22.12%
SW | F099D_Warra 33 kV | Limiting Line Name | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1
SW | F099D_Warra 33 kV | Loading (A) | 56.2479 | 76.5922 | 34.7237 | 56.2461 | 76.5858 | 34.7236 | 56.2409 | 76.5777 | 34.7218 | 56.2176 | 76.4897 | 34.709 | 56.2401 | 76.5738 | 34.7276
SW | F099D_Warra 33 kV | Loading (MVA) | 3.2303 | 4.3587 | 2.0212 | 3.2303 | 4.3587 | 2.0212 | 3.2303 | 4.3587 | 2.0212 | 3.2303 | 4.3584 | 2.0217 | 3.2303 | 4.3587 | 2.0218
SW | F099D_Warra 33 kV | Loading (MW) | 3.1302 | 4.2086 | 1.948 | 3.1302 | 4.2086 | 1.948 | 3.1302 | 4.2086 | 1.948 | 3.1302 | 4.2085 | 1.948 | 3.1302 | 4.2086 | 1.948
SW | F099D_Warra 33 kV | Power Factor | 0.96888 | 0.96555 | 0.96367 | 0.96888 | 0.96555 | 0.96367 | 0.96888 | 0.96556 | 0.96368 | 0.96888 | 0.9656 | 0.96345 | 0.96888 | 0.96556 | 0.96341
SW | F099D_Warra 33 kV | Rating (A) | 100 | 177 | 157 | 100 | 177 | 157 | 100 | 177 | 157 | 100 | 177 | 157 | 100 | 177 | 157
SW | F099D_Warra 33 kV | Time | 10:00:00 | 17:00:00 | 22:00:00 | 10:00:00 | 17:00:00 | 22:00:00 | 10:00:00 | 17:00:00 | 22:00:00 | 10:00:00 | 17:00:00 | 22:00:00 | 10:00:00 | 17:00:00 | 22:00:00
SW | F099D_Warra 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0048 | 0.99497 | 1.0182 | 1.0048 | 0.99505 | 1.0182 | 1.0049 | 0.99515 | 1.0182 | 1.0053 | 0.99623 | 1.0188 | 1.0049 | 0.99519 | 1.0183
SW | F2060_Sladevale 1 33kV | % of Rated A | 13.51% | 15.92% | 11.31% | 13.52% | 15.93% | 11.32% | 13.52% | 15.93% | 11.32% | 13.51% | 15.92% | 11.31% | 13.8% | 16.28% | 11.53%
SW | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW | F2060_Sladevale 1 33kV | Loading (A) | 85.7815 | 101.0663 | 71.8297 | 85.8206 | 101.1264 | 71.851 | 85.8796 | 101.1841 | 71.8757 | 85.8104 | 101.0786 | 71.8388 | 87.6512 | 103.3904 | 73.1905
SW | F2060_Sladevale 1 33kV | Loading (MVA) | 5.0212 | 5.8347 | 4.2204 | 5.0214 | 5.8354 | 4.2203 | 5.0219 | 5.8361 | 4.2203 | 5.0214 | 5.8348 | 4.2204 | 5.1191 | 5.9567 | 4.2949
SW | F2060_Sladevale 1 33kV | Loading (MW) | 5.0158 | 5.8314 | 4.1756 | 5.0161 | 5.832 | 4.1758 | 5.0167 | 5.8326 | 4.176 | 5.016 | 5.8315 | 4.1757 | 5.1161 | 5.9509 | 4.2566
SW | F2060_Sladevale 1 33kV | Power Factor | 0.99892 | 0.99942 | 0.98939 | 0.99894 | 0.99941 | 0.98944 | 0.99897 | 0.99939 | 0.9895 | 0.99894 | 0.99942 | 0.98941 | 0.9994 | 0.99901 | 0.99109
SW | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | F2060_Sladevale 1 33kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F2060_Sladevale 1 33kV | Min Voltage at Constrained Conductor (pu) | 1.0241 | 1.01 | 1.0279 | 1.0237 | 1.0096 | 1.0276 | 1.0231 | 1.0091 | 1.0273 | 1.0238 | 1.0099 | 1.0278 | 1.0218 | 1.008 | 1.0266
SW | F2325_Broxburn 33 kV | % of Rated A | 70.12% | 70.74% | 52.97% | 69.82% | 70.42% | 52.82% | 69.88% | 70.47% | 52.85% | 69.18% | 69.75% | 52.36% | 70.63% | 71.24% | 53.35%
SW | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1
SW | F2325_Broxburn 33 kV | Loading (A) | 234.2001 | 238.3905 | 154.6756 | 233.1833 | 237.2995 | 154.2489 | 233.3988 | 237.4695 | 154.3234 | 231.0776 | 235.0695 | 152.8882 | 235.9096 | 240.0652 | 155.7944
SW | F2325_Broxburn 33 kV | Loading (MVA) | 12.3598 | 12.6235 | 8.6028 | 12.3312 | 12.5937 | 8.5897 | 12.3318 | 12.5942 | 8.5898 | 12.228 | 12.488 | 8.5186 | 12.4361 | 12.7009 | 8.6611
SW | F2325_Broxburn 33 kV | Loading (MW) | 11.4947 | 11.7353 | 8.0684 | 11.6031 | 11.846 | 8.1445 | 11.6031 | 11.846 | 8.1445 | 11.5088 | 11.7497 | 8.0783 | 11.6975 | 11.9423 | 8.2107
SW | F2325_Broxburn 33 kV | Power Factor | 0.93001 | 0.92964 | 0.93788 | 0.94095 | 0.94063 | 0.94817 | 0.94091 | 0.94059 | 0.94816 | 0.94118 | 0.94087 | 0.94831 | 0.94061 | 0.94027 | 0.948
SW | F2325_Broxburn 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | F2325_Broxburn 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F2325_Broxburn 33 kV | Min Voltage at Constrained Conductor (pu) | 0.92306 | 0.92618 | 0.97291 | 0.92495 | 0.92825 | 0.97412 | 0.92413 | 0.92762 | 0.97366 | 0.92557 | 0.92919 | 0.97466 | 0.92203 | 0.92536 | 0.97247
SW | F2450_Carrington Road 33 kV | % of Rated A | 28.67% | 34.41% | 23.71% | 28.39% | 34.55% | 23.77% | 28.47% | 34.66% | 23.81% | 28.46% | 34.61% | 23.79% | 28.95% | 34.91% | 24.18%
SW | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW | F2450_Carrington Road 33 kV | Loading (A) | 96.6077 | 115.9773 | 79.9111 | 95.6814 | 116.4186 | 80.0989 | 95.9587 | 116.8079 | 80.2527 | 95.9046 | 116.6193 | 80.1746 | 97.548 | 117.6609 | 81.4925
SW | F2450_Carrington Road 33 kV | Loading (MVA) | 5.5933 | 6.7192 | 4.653 | 5.5918 | 6.7201 | 4.6533 | 5.5904 | 6.7209 | 4.6535 | 5.5903 | 6.7205 | 4.6534 | 5.6765 | 6.8012 | 4.7248
SW | F2450_Carrington Road 33 kV | Loading (MW) | 5.4093 | 6.4845 | 4.5095 | 5.4091 | 6.4846 | 4.5096 | 5.409 | 6.4847 | 4.5096 | 5.4089 | 6.4847 | 4.5096 | 5.4911 | 6.562 | 4.578
SW | F2450_Carrington Road 33 kV | Power Factor | 0.96704 | 0.96499 | 0.9691 | 0.96726 | 0.96489 | 0.96905 | 0.96747 | 0.96479 | 0.96902 | 0.96749 | 0.96484 | 0.96904 | 0.96727 | 0.96475 | 0.96887
SW | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337
SW | F2450_Carrington Road 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
SW | F2450_Carrington Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0129 | 1.0136 | 1.0187 | 1.0225 | 1.0099 | 1.0164 | 1.0193 | 1.0067 | 1.0145 | 1.0198 | 1.0082 | 1.0154 | 1.0181 | 1.0113 | 1.0144
SW | F2460_Cecil Plains 33 kV | % of Rated A | 27.36% | 19.29% | 18.58% | 27.36% | 19.29% | 18.52% | 27.34% | 19.35% | 18.52% | 27.35% | 19.29% | 18.52% | 27.7% | 19.72% | 18.73%
SW | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW | F2460_Cecil Plains 33 kV | Loading (A) | 39.1181 | 40.6971 | 38.6471 | 39.1181 | 40.7025 | 38.524 | 39.0996 | 40.8336 | 38.5129 | 39.1138 | 40.7022 | 38.5254 | 39.6147 | 41.6033 | 38.9653
SW | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.2821 | 2.381 | 2.3269 | 2.2821 | 2.3697 | 2.2933 | 2.2793 | 2.3927 | 2.2917 | 2.2815 | 2.3819 | 2.2935 | 2.305 | 2.4334 | 2.3156
SW | F2460_Cecil Plains 33 kV | Loading (MW) | 1.0863 | 1.2995 | 1 | 1.0863 | 1.313 | 1.0321 | 1.0863 | 1.3131 | 1.032 | 1.0863 | 1.2995 | 1.0321 | 1.1691 | 1.4135 | 1.1106
SW | F2460_Cecil Plains 33 kV | Power Factor | 0.47522 | 0.54519 | 0.42909 | 0.47522 | 0.55348 | 0.44949 | 0.47579 | 0.54821 | 0.44981 | 0.47535 | 0.54499 | 0.44945 | 0.50652 | 0.58027 | 0.47926
SW | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
SW | F2460_Cecil Plains 33 kV | Time | 16:30:00 | 18:00:00 | 22:30:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F2460_Cecil Plains 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0207 | 1.0236 | 1.0534 | 1.0207 | 1.0186 | 1.0415 | 1.0199 | 1.0252 | 1.0411 | 1.0205 | 1.0238 | 1.0416 | 1.018 | 1.0233 | 1.0397
SW | F2520_Clifton 33 kV | % of Rated A | 58.92% | 74.04% | 53.04% | 58.95% | 74.1% | 53.06% | 57.77% | 72.42% | 52.02% | 57.75% | 72.39% | 52.01% | 58.14% | 72.35% | 52.38%
SW | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1
SW | F2520_Clifton 33 kV | Loading (A) | 71.8794 | 90.3243 | 64.7088 | 71.922 | 90.3964 | 64.7318 | 70.4737 | 88.3582 | 63.4678 | 70.4519 | 88.3204 | 63.4495 | 70.9297 | 88.2621 | 63.9061
SW | F2520_Clifton 33 kV | Loading (MVA) | 3.9765 | 4.7805 | 3.6312 | 3.976 | 4.7801 | 3.6308 | 3.8999 | 4.6769 | 3.5639 | 3.9001 | 4.6771 | 3.5642 | 3.9768 | 4.7771 | 3.6311
SW | F2520_Clifton 33 kV | Loading (MW) | 3.8713 | 4.7213 | 3.4938 | 3.8714 | 4.7214 | 3.4938 | 3.7884 | 4.6199 | 3.419 | 3.7883 | 4.6199 | 3.419 | 3.8706 | 4.7193 | 3.4933
SW | F2520_Clifton 33 kV | Power Factor | 0.97352 | 0.98759 | 0.96213 | 0.97366 | 0.98769 | 0.96224 | 0.97137 | 0.98778 | 0.95932 | 0.9713 | 0.98772 | 0.95922 | 0.97326 | 0.98787 | 0.962
SW | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
SW | F2520_Clifton 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F2520_Clifton 33 kV | Min Voltage at Constrained Conductor (pu) | 0.96771 | 0.92573 | 0.98164 | 0.96702 | 0.92491 | 0.98118 | 0.968 | 0.92584 | 0.98228 | 0.96837 | 0.92627 | 0.98267 | 0.98074 | 0.94671 | 0.99394
SW | F2777_East Stanthorpe 33 kV | % of Rated A | 1.541% | 1.122% | 1.18% | 1.541% | 1.122% | 1.18% | 1.541% | 1.126% | 1.18% | 1.542% | 1.122% | 1.18% | 1.541% | 1.126% | 1.181%
SW | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW | F2777_East Stanthorpe 33 kV | Loading (A) | 2.3737 | 2.3346 | 2.3708 | 2.3738 | 2.3338 | 2.371 | 2.3735 | 2.3429 | 2.3727 | 2.374 | 2.3347 | 2.3714 | 2.3731 | 2.3425 | 2.3728
SW | F2777_East Stanthorpe 33 kV | Loading (MVA) | 0.14224 | 0.13699 | 0.14179 | 0.14225 | 0.13689 | 0.14182 | 0.14222 | 0.13828 | 0.14202 | 0.14227 | 0.13701 | 0.14186 | 0.14216 | 0.13823 | 0.14204
SW | F2777_East Stanthorpe 33 kV | Loading (MW) | 6.0226e-05 | 5.8527e-05 | 6.0124e-05 | 6.0231e-05 | 5.8486e-05 | 6.0135e-05 | 6.0217e-05 | 5.8806e-05 | 6.022e-05 | 6.0242e-05 | 5.8536e-05 | 6.0154e-05 | 6.0194e-05 | 5.8788e-05 | 6.0227e-05
SW | F2777_East Stanthorpe 33 kV | Power Factor | 0.00042157 | 0.00042537 | 0.00042218 | 0.00042157 | 0.00042537 | 0.00042218 | 0.00042157 | 0.00042342 | 0.00042218 | 0.00042157 | 0.00042537 | 0.00042218 | 0.00042157 | 0.00042342 | 0.00042218
SW | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201
SW | F2777_East Stanthorpe 33 kV | Time | 10:30:00 | 20:30:00 | 01:30:00 | 13:00:00 | 20:30:00 | 02:00:00 | 10:30:00 | 21:30:00 | 02:30:00 | 13:00:00 | 20:30:00 | 02:00:00 | 10:30:00 | 21:30:00 | 02:30:00
SW | F2777_East Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0484 | 1.0266 | 1.0464 | 1.0484 | 1.0263 | 1.0464 | 1.0483 | 1.0326 | 1.0472 | 1.0485 | 1.0267 | 1.0466 | 1.0481 | 1.0324 | 1.0473
SW | F2780_East Warwick No 1 33 kV | % of Rated A | 36.28% | 35.78% | 25.75% | 35.98% | 35.49% | 25.55% | 35.84% | 35.35% | 25.46% | 35.5% | 35.01% | 25.24% | 36.04% | 35.64% | 25.57%
SW | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW | F2780_East Warwick No 1 33 kV | Loading (A) | 192.3083 | 194.2976 | 122.8449 | 190.6975 | 192.6855 | 121.8833 | 189.9643 | 191.96 | 121.422 | 188.1565 | 190.1037 | 120.3825 | 191.0165 | 193.5034 | 121.9712
SW | F2780_East Warwick No 1 33 kV | Loading (MVA) | 11.2685 | 11.2401 | 7.2212 | 11.1697 | 11.1412 | 7.1625 | 11.1201 | 11.0915 | 7.1329 | 11.022 | 10.9934 | 7.0756 | 11.1687 | 11.1391 | 7.1612
SW | F2780_East Warwick No 1 33 kV | Loading (MW) | 11.2201 | 11.1994 | 6.9988 | 11.1189 | 11.0984 | 6.9358 | 11.0683 | 11.0479 | 6.9043 | 10.967 | 10.9467 | 6.8413 | 11.1191 | 11.099 | 6.9358
SW | F2780_East Warwick No 1 33 kV | Power Factor | 0.99568 | 0.99636 | 0.96916 | 0.99543 | 0.99614 | 0.96831 | 0.99532 | 0.99605 | 0.96792 | 0.99498 | 0.99573 | 0.96686 | 0.99554 | 0.99638 | 0.9685
SW | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | F2780_East Warwick No 1 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F2780_East Warwick No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0251 | 1.012 | 1.0284 | 1.0247 | 1.0115 | 1.0281 | 1.0241 | 1.0108 | 1.0277 | 1.0248 | 1.0117 | 1.0283 | 1.0229 | 1.007 | 1.0272
SW | F2785_East Warwick No 2 33 kV | % of Rated A | 36.11% | 35.61% | 25.63% | 35.8% | 35.31% | 25.43% | 35.67% | 35.18% | 25.33% | 35.33% | 34.84% | 25.11% | 35.86% | 35.46% | 25.44%
SW | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW | F2785_East Warwick No 2 33 kV | Loading (A) | 191.3578 | 193.3373 | 122.2379 | 189.755 | 191.7331 | 121.2811 | 189.0255 | 191.0113 | 120.822 | 187.2266 | 189.1642 | 119.7876 | 190.0724 | 192.547 | 121.3685
SW | F2785_East Warwick No 2 33 kV | Loading (MVA) | 11.2128 | 11.1845 | 7.1855 | 11.1145 | 11.0861 | 7.1271 | 11.0651 | 11.0367 | 7.0977 | 10.9675 | 10.9391 | 7.0406 | 11.1135 | 11.084 | 7.1258
SW | F2785_East Warwick No 2 33 kV | Loading (MW) | 11.1651 | 11.1445 | 6.9649 | 11.0644 | 11.0439 | 6.9023 | 11.0141 | 10.9937 | 6.8709 | 10.9132 | 10.893 | 6.8082 | 11.0646 | 11.0446 | 6.9023
SW | F2785_East Warwick No 2 33 kV | Power Factor | 0.99572 | 0.9964 | 0.96926 | 0.99547 | 0.99617 | 0.96841 | 0.99536 | 0.99608 | 0.96802 | 0.99502 | 0.99577 | 0.96696 | 0.99557 | 0.99642 | 0.9686
SW | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | F2785_East Warwick No 2 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F2785_East Warwick No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0251 | 1.012 | 1.0284 | 1.0247 | 1.0115 | 1.0281 | 1.0241 | 1.0108 | 1.0277 | 1.0248 | 1.0116 | 1.0283 | 1.0229 | 1.007 | 1.0272
SW | F3040 Hampton Street | % of Rated A | 0.3092% | 0.3088% | 0.3093% | 0.3093% | 0.3086% | 0.3092% | 0.3093% | 0.3085% | 0.3092% | 0.3092% | 0.3086% | 0.3092% | 0.3093% | 0.3085% | 0.3092%
SW | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW | F3040 Hampton Street | Loading (A) | 1.5461 | 1.5439 | 1.5463 | 1.5464 | 1.5432 | 1.5461 | 1.5464 | 1.5425 | 1.5458 | 1.5461 | 1.5431 | 1.546 | 1.5463 | 1.5427 | 1.5459
SW | F3040 Hampton Street | Loading (MVA) | 0.093644 | 0.093374 | 0.093666 | 0.093673 | 0.093292 | 0.093641 | 0.093682 | 0.093203 | 0.0936 | 0.093643 | 0.093274 | 0.093632 | 0.093671 | 0.093235 | 0.093616
SW | F3040 Hampton Street | Loading (MW) | 0.0013197 | 0.0013159 | 0.00132 | 0.0013201 | 0.0013148 | 0.0013197 | 0.0013202 | 0.0013135 | 0.0013191 | 0.0013197 | 0.0013145 | 0.0013195 | 0.0013201 | 0.001314 | 0.0013193
SW | F3040 Hampton Street | Power Factor | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534
SW | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | F3040 Hampton Street | Time | 15:30:00 | 21:00:00 | 00:30:00 | 13:00:00 | 21:00:00 | 05:00:00 | 08:00:00 | 21:00:00 | 05:00:00 | 13:00:00 | 21:00:00 | 05:00:00 | 08:00:00 | 21:00:00 | 00:30:00
SW | F3040 Hampton Street | Min Voltage at Constrained Conductor (pu) | 1.0596 | 1.0581 | 1.0598 | 1.0598 | 1.0577 | 1.0596 | 1.0599 | 1.0571 | 1.0594 | 1.0596 | 1.0576 | 1.0596 | 1.0598 | 1.0573 | 1.0595
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | % of Rated A | 63.85% | 49.75% | 43.69% | 64.96% | 50.64% | 44.21% | 65.01% | 50.67% | 44.23% | 64.27% | 50.04% | 43.84% | 65.04% | 50.68% | 44.23%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (A) | 107.9142 | 119.4015 | 102.2387 | 109.7791 | 121.5409 | 103.4451 | 109.8636 | 121.6157 | 103.4922 | 108.6136 | 120.0937 | 102.5777 | 109.913 | 121.6286 | 103.5
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 6.0324 | 6.5997 | 5.7085 | 6.1256 | 6.7041 | 5.7692 | 6.1257 | 6.7041 | 5.7692 | 6.0621 | 6.6286 | 5.723 | 6.1257 | 6.7042 | 5.7692
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MW) | 5.9437 | 6.5005 | 5.6131 | 6.0377 | 6.6057 | 5.6746 | 6.0378 | 6.6057 | 5.6746 | 5.9745 | 6.5308 | 5.6284 | 6.0378 | 6.6057 | 5.6746
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Power Factor | 0.9853 | 0.98496 | 0.98328 | 0.98566 | 0.98533 | 0.98361 | 0.98565 | 0.98532 | 0.98361 | 0.98555 | 0.98526 | 0.98348 | 0.98564 | 0.98532 | 0.98361
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor (pu) | 0.97799 | 0.96702 | 0.97685 | 0.97622 | 0.96501 | 0.97571 | 0.97548 | 0.96443 | 0.97528 | 0.97647 | 0.96565 | 0.97609 | 0.97505 | 0.96433 | 0.9752
SW | F3255_Jennings Street 33 kV | % of Rated A | 42.73% | 44.81% | 29.99% | 42.76% | 44.8% | 30% | 42.93% | 44.98% | 30.11% | 42.92% | 44.96% | 30.1% | 44.21% | 46.42% | 30.98%
SW | F3255_Jennings Street 33 kV | Limiting Line Name | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1
SW | F3255_Jennings Street 33 kV | Loading (A) | 263.647 | 276.478 | 185.0433 | 263.8101 | 276.3877 | 185.1167 | 264.8743 | 277.5262 | 185.79 | 264.7867 | 277.4177 | 185.7284 | 272.7845 | 286.4227 | 191.1369
SW | F3255_Jennings Street 33 kV | Loading (MVA) | 15.6674 | 16.5341 | 11.0504 | 15.6681 | 16.5204 | 11.0506 | 15.7199 | 16.5752 | 11.0862 | 15.7195 | 16.5748 | 11.086 | 16.1797 | 17.064 | 11.4051
SW | F3255_Jennings Street 33 kV | Loading (MW) | 15.3218 | 16.1379 | 10.8856 | 15.3219 | 16.1364 | 10.8856 | 15.3704 | 16.1876 | 10.9199 | 15.3704 | 16.1875 | 10.9199 | 15.8062 | 16.6471 | 11.2287
SW | F3255_Jennings Street 33 kV | Power Factor | 0.97776 | 0.97585 | 0.98493 | 0.97773 | 0.97658 | 0.98492 | 0.97759 | 0.97643 | 0.98485 | 0.97761 | 0.97645 | 0.98486 | 0.97674 | 0.97538 | 0.98437
SW | F3255_Jennings Street 33 kV | Rating (A) | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617
SW | F3255_Jennings Street 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F3255_Jennings Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0397 | 1.0463 | 1.0448 | 1.0391 | 1.0457 | 1.0444 | 1.0383 | 1.0449 | 1.044 | 1.0386 | 1.0453 | 1.0443 | 1.0377 | 1.0423 | 1.044
SW | F3315_Sladevale 2 33kV | % of Rated A | 7.632% | 8.268% | 7.283% | 7.631% | 8.268% | 7.282% | 7.629% | 8.268% | 7.282% | 7.631% | 8.268% | 7.284% | 7.625% | 8.267% | 7.279%
SW | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW | F3315_Sladevale 2 33kV | Loading (A) | 48.4624 | 52.5039 | 46.2488 | 48.4545 | 52.5014 | 46.2403 | 48.4425 | 52.499 | 46.239 | 48.4565 | 52.5034 | 46.2538 | 48.4196 | 52.4937 | 46.2235
SW | F3315_Sladevale 2 33kV | Loading (MVA) | 2.8445 | 3.0406 | 2.7236 | 2.8429 | 3.0391 | 2.7223 | 2.8405 | 3.0376 | 2.7213 | 2.8433 | 3.0403 | 2.7236 | 2.8358 | 3.0341 | 2.7189
SW | F3315_Sladevale 2 33kV | Loading (MW) | 1.7957 | 2.2709 | 1.4662 | 1.7958 | 2.271 | 1.4662 | 1.7959 | 2.2711 | 1.4662 | 1.7958 | 2.2709 | 1.4662 | 1.796 | 2.2713 | 1.4662
SW | F3315_Sladevale 2 33kV | Power Factor | 0.63131 | 0.74685 | 0.53832 | 0.63168 | 0.74726 | 0.53859 | 0.63224 | 0.74766 | 0.53879 | 0.63159 | 0.74694 | 0.53832 | 0.63332 | 0.74857 | 0.53928
SW | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | F3315_Sladevale 2 33kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F3315_Sladevale 2 33kV | Min Voltage at Constrained Conductor (pu) | 1.0269 | 1.0132 | 1.0303 | 1.0265 | 1.0127 | 1.03 | 1.0259 | 1.0123 | 1.0297 | 1.0266 | 1.0131 | 1.0302 | 1.0247 | 1.0112 | 1.0291
SW | F3530_Millmerran 33 kV | % of Rated A | 52.16% | 43.53% | 29.46% | 52.16% | 43.52% | 29.46% | 52.21% | 43.55% | 29.48% | 52.12% | 43.46% | 29.44% | 52.32% | 43% | 29.51%
SW | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1
SW | F3530_Millmerran 33 kV | Loading (A) | 66.2424 | 78.3503 | 51.5625 | 66.2423 | 78.3363 | 51.563 | 66.3041 | 78.3954 | 51.5892 | 66.1934 | 78.2347 | 51.523 | 66.451 | 77.4073 | 51.6471
SW | F3530_Millmerran 33 kV | Loading (MVA) | 3.8526 | 4.5378 | 3.0152 | 3.8526 | 4.5377 | 3.0152 | 3.853 | 4.5381 | 3.0153 | 3.851 | 4.535 | 3.0145 | 3.8539 | 4.5325 | 3.0151
SW | F3530_Millmerran 33 kV | Loading (MW) | 3.7893 | 4.4497 | 2.9766 | 3.7893 | 4.4496 | 2.9766 | 3.7896 | 4.4499 | 2.9766 | 3.7928 | 4.4535 | 2.9794 | 3.7902 | 4.4455 | 2.9767
SW | F3530_Millmerran 33 kV | Power Factor | 0.98356 | 0.98058 | 0.9859 | 0.98356 | 0.98059 | 0.9859 | 0.98353 | 0.98056 | 0.9859 | 0.98488 | 0.98203 | 0.98716 | 0.98346 | 0.98081 | 0.98603
SW | F3530_Millmerran 33 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | F3530_Millmerran 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F3530_Millmerran 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98253 | 0.97023 | 0.99798 | 0.98253 | 0.9704 | 0.99797 | 0.98163 | 0.96968 | 0.99747 | 0.98293 | 0.97127 | 0.99848 | 0.97951 | 0.98206 | 0.99619
SW | F3815 North Street No 1 33 kV | % of Rated A | 0.7517% | 0.6631% | 0.7521% | 0.7515% | 0.6645% | 0.752% | 0.7521% | 0.6642% | 0.7521% | 0.7521% | 0.6644% | 0.752% | 0.7521% | 0.6644% | 0.7521%
SW | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1
SW | F3815 North Street No 1 33 kV | Loading (A) | 2.3454 | 2.3472 | 2.3465 | 2.3448 | 2.3523 | 2.3463 | 2.3467 | 2.3512 | 2.3466 | 2.3466 | 2.3521 | 2.3462 | 2.3464 | 2.3518 | 2.3465
SW | F3815 North Street No 1 33 kV | Loading (MVA) | 0.13926 | 0.13947 | 0.13938 | 0.13918 | 0.14008 | 0.13936 | 0.13941 | 0.13995 | 0.1394 | 0.13939 | 0.14005 | 0.13935 | 0.13938 | 0.14002 | 0.13938
SW | F3815 North Street No 1 33 kV | Loading (MW) | 0.00044461 | 0.00044529 | 0.000445 | 0.00044437 | 0.00044723 | 0.00044493 | 0.00044508 | 0.0004468 | 0.00044505 | 0.00044504 | 0.00044714 | 0.00044489 | 0.00044499 | 0.00044704 | 0.00044501
SW | F3815 North Street No 1 33 kV | Power Factor | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927
SW | F3815 North Street No 1 33 kV | Rating (A) | 312 | 354 | 312 | 312 | 354 | 312 | 312 | 354 | 312 | 312 | 354 | 312 | 312 | 354 | 312
SW | F3815 North Street No 1 33 kV | Time | 06:00:00 | 20:30:00 | 05:30:00 | 06:00:00 | 21:00:00 | 04:30:00 | 08:00:00 | 21:00:00 | 04:00:00 | 08:00:00 | 21:00:00 | 04:30:00 | 08:00:00 | 17:30:00 | 04:00:00
SW | F3815 North Street No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0388 | 1.0396 | 1.0392 | 1.0385 | 1.0418 | 1.0392 | 1.0393 | 1.0413 | 1.0393 | 1.0393 | 1.0417 | 1.0391 | 1.0392 | 1.0416 | 1.0392
SW | F3820_Boundary Road 33 kV | % of Rated A | 50.7% | 52% | 36.22% | 60.86% | 63.32% | 43.84% | 71.62% | 73.54% | 51.49% | 71.31% | 73.21% | 51.25% | 72.44% | 74.58% | 52.05%
SW | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW | F3820_Boundary Road 33 kV | Loading (A) | 349.8258 | 358.7728 | 249.8955 | 419.9643 | 436.8863 | 302.4984 | 494.1678 | 507.3988 | 355.2858 | 492.0682 | 505.1147 | 353.6526 | 499.8312 | 514.609 | 359.1184
SW | F3820_Boundary Road 33 kV | Loading (MVA) | 20.4495 | 20.9985 | 14.6658 | 24.7746 | 25.467 | 17.7116 | 29.063 | 29.8571 | 20.7627 | 28.9551 | 29.7453 | 20.6867 | 29.3678 | 30.1782 | 20.9868
SW | F3820_Boundary Road 33 kV | Loading (MW) | 20.1184 | 20.6476 | 14.5144 | 24.0884 | 24.7332 | 17.3652 | 28.151 | 28.8936 | 20.302 | 28.0512 | 28.7908 | 20.2303 | 28.4495 | 29.2026 | 20.5158
SW | F3820_Boundary Road 33 kV | Power Factor | 0.98346 | 0.98294 | 0.98938 | 0.97194 | 0.97084 | 0.9801 | 0.96832 | 0.96744 | 0.97743 | 0.96848 | 0.96762 | 0.97756 | 0.96844 | 0.96739 | 0.97717
SW | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | F3820_Boundary Road 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F3820_Boundary Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0227 | 1.0239 | 1.0268 | 1.032 | 1.0197 | 1.0244 | 1.0287 | 1.0293 | 1.0224 | 1.0293 | 1.03 | 1.0234 | 1.0277 | 1.0257 | 1.0224
SW | F3830_Norwin 33 kV | % of Rated A | 28.11% | 33.21% | 30.78% | 28.11% | 33.22% | 30.78% | 28.14% | 33.24% | 30.79% | 28.12% | 33.21% | 30.78% | 29.58% | 34.95% | 32.36%
SW | F3830_Norwin 33 kV | Limiting Line Name | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1
SW | F3830_Norwin 33 kV | Loading (A) | 32.6126 | 38.5272 | 35.7062 | 32.6126 | 38.5318 | 35.7065 | 32.6385 | 38.5624 | 35.7139 | 32.6186 | 38.5265 | 35.7046 | 34.3155 | 40.5401 | 37.5353
SW | F3830_Norwin 33 kV | Loading (MVA) | 1.8156 | 2.126 | 2.0226 | 1.8156 | 2.126 | 2.0226 | 1.8156 | 2.1261 | 2.0221 | 1.8156 | 2.126 | 2.0226 | 1.9032 | 2.2282 | 2.1197
SW | F3830_Norwin 33 kV | Loading (MW) | 1.4464 | 1.6906 | 1.6096 | 1.4464 | 1.6906 | 1.6096 | 1.4464 | 1.6906 | 1.6096 | 1.4464 | 1.6906 | 1.6096 | 1.5153 | 1.7711 | 1.6863
SW | F3830_Norwin 33 kV | Power Factor | 0.79655 | 0.79511 | 0.79577 | 0.79655 | 0.79511 | 0.79577 | 0.79654 | 0.79509 | 0.79593 | 0.79655 | 0.79511 | 0.79577 | 0.79613 | 0.7948 | 0.7955
SW | F3830_Norwin 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
SW | F3830_Norwin 33 kV | Time | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00 | 16:30:00 | 19:00:00 | 22:00:00
SW | F3830_Norwin 33 kV | Min Voltage at Constrained Conductor (pu) | 0.974 | 0.96545 | 0.99102 | 0.974 | 0.96534 | 0.99101 | 0.97324 | 0.96459 | 0.99058 | 0.97383 | 0.96547 | 0.99107 | 0.97032 | 0.96162 | 0.988
SW | F3855 Omaras Road 33 kV | % of Rated A | 17.71% | 18.42% | 18.21% | 17.55% | 18.48% | 18.25% | 17.6% | 18.31% | 18.29% | 17.6% | 18.28% | 18.27% | 17.62% | 18.32% | 18.29%
SW | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW | F3855 Omaras Road 33 kV | Loading (A) | 41.2717 | 42.9072 | 42.4307 | 40.8906 | 43.0632 | 42.5276 | 41.0189 | 42.6695 | 42.607 | 40.9966 | 42.604 | 42.5667 | 41.0591 | 42.6935 | 42.6066
SW | F3855 Omaras Road 33 kV | Loading (MVA) | 2.4007 | 2.5 | 2.4783 | 2.4007 | 2.5 | 2.4783 | 2.4007 | 2.4723 | 2.4783 | 2.4007 | 2.4722 | 2.4783 | 2.4007 | 2.5 | 2.4783
SW | F3855 Omaras Road 33 kV | Loading (MW) | 2.1491 | 2.2379 | 2.2184 | 2.1491 | 2.2379 | 2.2184 | 2.1491 | 2.213 | 2.2184 | 2.1491 | 2.213 | 2.2184 | 2.1491 | 2.2379 | 2.2184
SW | F3855 Omaras Road 33 kV | Power Factor | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895
SW | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
SW | F3855 Omaras Road 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F3855 Omaras Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0177 | 1.0194 | 1.0219 | 1.0272 | 1.0157 | 1.0195 | 1.024 | 1.0137 | 1.0176 | 1.0245 | 1.0152 | 1.0186 | 1.023 | 1.0245 | 1.0176
SW | F3867_Pampas 33 kV | % of Rated A | 64.03% | 72.79% | 53.75% | 64.03% | 72.77% | 53.75% | 64.09% | 72.83% | 53.78% | 63.89% | 72.57% | 53.63% | 64.72% | 73.47% | 54.28%
SW | F3867_Pampas 33 kV | Limiting Line Name | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1
SW | F3867_Pampas 33 kV | Loading (A) | 192.0948 | 218.3555 | 158.0376 | 192.0944 | 218.3179 | 158.0393 | 192.2688 | 218.4768 | 158.1182 | 191.6605 | 217.6952 | 157.6831 | 194.154 | 220.4226 | 159.5978
SW | F3867_Pampas 33 kV | Loading (MVA) | 10.3878 | 11.7562 | 8.8307 | 10.3878 | 11.7561 | 8.8307 | 10.3885 | 11.7568 | 8.831 | 10.3656 | 11.7285 | 8.8133 | 10.4696 | 11.8363 | 8.9026
SW | F3867_Pampas 33 kV | Loading (MW) | 9.5282 | 10.7687 | 8.0991 | 9.5282 | 10.7687 | 8.0991 | 9.5284 | 10.769 | 8.0992 | 9.5185 | 10.7563 | 8.0916 | 9.5954 | 10.8358 | 8.1599
SW | F3867_Pampas 33 kV | Power Factor | 0.91714 | 0.91589 | 0.91716 | 0.91714 | 0.9159 | 0.91715 | 0.91711 | 0.91586 | 0.91714 | 0.91817 | 0.91699 | 0.91811 | 0.9164 | 0.91535 | 0.91657
SW | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294
SW | F3867_Pampas 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F3867_Pampas 33 kV | Min Voltage at Constrained Conductor (pu) | 0.94609 | 0.94195 | 0.97756 | 0.94609 | 0.9421 | 0.97755 | 0.9453 | 0.94148 | 0.97709 | 0.94621 | 0.94259 | 0.97782 | 0.94343 | 0.93948 | 0.97589
SW | F3970_Pozieres 33 kV | % of Rated A | 40.37% | 31.74% | 23.58% | 40.39% | 31.75% | 23.58% | 40.42% | 31.77% | 23.59% | 40.4% | 31.74% | 23.58% | 40.49% | 31.83% | 23.62%
SW | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2
SW | F3970_Pozieres 33 kV | Loading (A) | 57.7308 | 66.0201 | 47.3861 | 57.7623 | 66.048 | 47.4043 | 57.8045 | 66.0852 | 47.4242 | 57.7658 | 66.028 | 47.3991 | 57.9055 | 66.2104 | 47.4733
SW | F3970_Pozieres 33 kV | Loading (MVA) | 3.3635 | 3.7852 | 2.8749 | 3.3635 | 3.7853 | 2.8749 | 3.3636 | 3.7854 | 2.875 | 3.3635 | 3.7852 | 2.8749 | 3.3637 | 3.7844 | 2.8751
SW | F3970_Pozieres 33 kV | Loading (MW) | 2.98 | 3.35 | 2.5603 | 2.98 | 3.35 | 2.5603 | 2.98 | 3.35 | 2.5603 | 2.98 | 3.35 | 2.5603 | 2.9801 | 3.35 | 2.5603
SW | F3970_Pozieres 33 kV | Power Factor | 0.886 | 0.88502 | 0.89047 | 0.88599 | 0.885 | 0.89046 | 0.88597 | 0.88498 | 0.89045 | 0.88598 | 0.88501 | 0.89047 | 0.88594 | 0.88521 | 0.89042
SW | F3970_Pozieres 33 kV | Rating (A) | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201
SW | F3970_Pozieres 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0193 | 1.0028 | 1.0613 | 1.0187 | 1.0024 | 1.0609 | 1.018 | 1.0018 | 1.0605 | 1.0187 | 1.0026 | 1.061 | 1.0163 | 0.99967 | 1.0595
SW | F3980_Purrawunda 33 kV | % of Rated A | 50.68% | 54.57% | 48.36% | 50.32% | 54.86% | 48.44% | 50.44% | 55% | 48.51% | 50.42% | 54.93% | 48.47% | 51.18% | 55.07% | 49.17%
SW | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | F3980_Purrawunda 33 kV | Loading (A) | 106.9258 | 115.1392 | 102.0456 | 106.1754 | 115.7465 | 102.213 | 106.4264 | 116.0504 | 102.3506 | 106.3827 | 115.903 | 102.2807 | 107.9798 | 116.1885 | 103.7385
SW | F3980_Purrawunda 33 kV | Loading (MVA) | 6.2527 | 6.7515 | 5.9904 | 6.2661 | 6.7629 | 5.9867 | 6.2615 | 6.7594 | 5.9838 | 6.2623 | 6.7611 | 5.9853 | 6.3467 | 6.8553 | 6.065
SW | F3980_Purrawunda 33 kV | Loading (MW) | 6.0659 | 6.6152 | 5.7605 | 6.0627 | 6.6175 | 5.7611 | 6.0638 | 6.6189 | 5.7617 | 6.0636 | 6.6182 | 5.7614 | 6.1616 | 6.7193 | 5.8541
SW | F3980_Purrawunda 33 kV | Power Factor | 0.97012 | 0.97982 | 0.96161 | 0.96755 | 0.9785 | 0.96232 | 0.96843 | 0.97921 | 0.96289 | 0.96827 | 0.97887 | 0.9626 | 0.97083 | 0.98016 | 0.96524
SW | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SW | F3980_Purrawunda 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor (pu) | 1.023 | 1.0258 | 1.027 | 1.0325 | 1.0222 | 1.0247 | 1.0293 | 1.019 | 1.0228 | 1.0298 | 1.0205 | 1.0238 | 1.0283 | 1.0322 | 1.0228
SW | F4005_Racecourse 33 kV | % of Rated A | 27.35% | 29.46% | 19.2% | 26.84% | 29.3% | 19.07% | 26.68% | 28.74% | 18.93% | 26.41% | 28.45% | 18.74% | 26.7% | 28.84% | 18.93%
SW | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1
SW | F4005_Racecourse 33 kV | Loading (A) | 193.0715 | 207.9608 | 135.5474 | 189.4721 | 206.8237 | 134.6311 | 188.3347 | 202.8963 | 133.6532 | 186.4764 | 200.8439 | 132.2912 | 188.526 | 203.6272 | 133.6518
SW | F4005_Racecourse 33 kV | Loading (MVA) | 11.2203 | 12.0941 | 7.924 | 11.1148 | 11.9802 | 7.8528 | 11.0141 | 11.866 | 7.7816 | 10.9121 | 11.7559 | 7.7099 | 11.0145 | 11.8675 | 7.7816
SW | F4005_Racecourse 33 kV | Loading (MW) | 10.9852 | 11.8281 | 7.7888 | 10.8861 | 11.7213 | 7.7191 | 10.7879 | 11.6144 | 7.6495 | 10.6894 | 11.5084 | 7.5797 | 10.7879 | 11.6147 | 7.6495
SW | F4005_Racecourse 33 kV | Power Factor | 0.97895 | 0.9779 | 0.98285 | 0.97932 | 0.97829 | 0.98289 | 0.97936 | 0.9787 | 0.98293 | 0.9795 | 0.97885 | 0.98303 | 0.97934 | 0.9786 | 0.98293
SW | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
SW | F4005_Racecourse 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F4005_Racecourse 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0167 | 1.0175 | 1.0228 | 1.0263 | 1.0134 | 1.0205 | 1.0232 | 1.0232 | 1.0186 | 1.0238 | 1.024 | 1.0196 | 1.0222 | 1.0196 | 1.0186
SW | F4015_Ramsay Street 33 kV | % of Rated A | 43.28% | 45.39% | 30.38% | 43.3% | 45.37% | 30.39% | 43.48% | 45.55% | 30.5% | 43.46% | 45.54% | 30.49% | 44.78% | 47.02% | 31.38%
SW | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1
SW | F4015_Ramsay Street 33 kV | Loading (A) | 259.6597 | 272.3478 | 182.2791 | 259.8203 | 272.2077 | 182.3515 | 260.8684 | 273.3289 | 183.0147 | 260.7822 | 273.2221 | 182.9541 | 268.659 | 282.0909 | 188.2817
SW | F4015_Ramsay Street 33 kV | Loading (MVA) | 15.4155 | 16.2705 | 10.8782 | 15.4162 | 16.254 | 10.8784 | 15.467 | 16.3079 | 10.9134 | 15.4667 | 16.3075 | 10.9132 | 15.9189 | 16.7881 | 11.2271
SW | F4015_Ramsay Street 33 kV | Loading (MW) | 15.0952 | 15.9021 | 10.7268 | 15.0953 | 15.8978 | 10.7268 | 15.1432 | 15.9482 | 10.7606 | 15.1431 | 15.9481 | 10.7606 | 15.5724 | 16.4009 | 11.0649
SW | F4015_Ramsay Street 33 kV | Power Factor | 0.97906 | 0.97719 | 0.98594 | 0.97902 | 0.97791 | 0.98592 | 0.9789 | 0.97777 | 0.98586 | 0.97891 | 0.97779 | 0.98587 | 0.97807 | 0.97676 | 0.9854
SW | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
SW | F4015_Ramsay Street 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F4015_Ramsay Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0387 | 1.0452 | 1.0441 | 1.0381 | 1.0447 | 1.0437 | 1.0373 | 1.0439 | 1.0433 | 1.0376 | 1.0442 | 1.0436 | 1.0367 | 1.0412 | 1.0432
SW | F4132_Shirley Road 33 kV | % of Rated A | 69.4% | 56.46% | 34.1% | 69.08% | 56.95% | 34.35% | 70.4% | 58.01% | 34.95% | 70.71% | 54.53% | 31.44% | 73.1% | 56.53% | 32.45%
SW | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1
SW | F4132_Shirley Road 33 kV | Loading (A) | 291.4912 | 381.0985 | 230.1919 | 290.1363 | 384.4451 | 231.8933 | 295.687 | 391.576 | 235.8875 | 296.9852 | 368.0703 | 212.202 | 307.0044 | 381.5805 | 219.0235
SW | F4132_Shirley Road 33 kV | Loading (MVA) | 16.7143 | 22.2111 | 13.47 | 16.7958 | 22.3244 | 13.5385 | 17.0554 | 22.6632 | 13.7452 | 17.1478 | 21.5613 | 12.3824 | 17.6843 | 22.2529 | 12.7672
SW | F4132_Shirley Road 33 kV | Loading (MW) | 16.6611 | 21.946 | 13.4171 | 16.744 | 22.0549 | 13.4849 | 17.0013 | 22.3772 | 13.6882 | 17.1078 | 21.3628 | 12.3507 | 17.64 | 22.0305 | 12.7315
SW | F4132_Shirley Road 33 kV | Power Factor | 0.99682 | 0.98791 | 0.99594 | 0.99692 | 0.98778 | 0.99591 | 0.99683 | 0.98723 | 0.99571 | 0.99767 | 0.99065 | 0.9973 | 0.9975 | 0.98986 | 0.99707
SW | F4132_Shirley Road 33 kV | Rating (A) | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675
SW | F4132_Shirley Road 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F4132_Shirley Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0032 | 1.0196 | 1.0238 | 1.0128 | 1.0159 | 1.0214 | 1.0091 | 1.0125 | 1.0195 | 1.0102 | 1.0248 | 1.0209 | 1.0078 | 1.0203 | 1.0198
SW | F4245_Stanthorpe 33 kV | % of Rated A | 55.25% | 68.5% | 51.5% | 55.27% | 68.52% | 51.51% | 55.3% | 68.55% | 51.52% | 55.27% | 68.51% | 51.51% | 56.19% | 69.8% | 52.29%
SW | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1
SW | F4245_Stanthorpe 33 kV | Loading (A) | 161.3317 | 200.0246 | 150.3793 | 161.39 | 200.0913 | 150.4132 | 161.4684 | 200.1803 | 150.4503 | 161.3966 | 200.0436 | 150.4036 | 164.0878 | 203.8287 | 152.6879
SW | F4245_Stanthorpe 33 kV | Loading (MVA) | 9.6212 | 11.6288 | 9.2505 | 9.6197 | 11.6282 | 9.2493 | 9.6178 | 11.6273 | 9.2479 | 9.6196 | 11.6287 | 9.2496 | 9.7564 | 11.8117 | 9.3765
SW | F4245_Stanthorpe 33 kV | Loading (MW) | 9.1967 | 11.4417 | 8.7024 | 9.1967 | 11.4417 | 8.7024 | 9.1967 | 11.4417 | 8.7025 | 9.1967 | 11.4417 | 8.7024 | 9.3571 | 11.6415 | 8.8549
SW | F4245_Stanthorpe 33 kV | Power Factor | 0.95588 | 0.9839 | 0.94066 | 0.95602 | 0.98396 | 0.94079 | 0.95622 | 0.98404 | 0.94093 | 0.95604 | 0.98392 | 0.94075 | 0.95907 | 0.98559 | 0.94428
SW | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
SW | F4245_Stanthorpe 33 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F4245_Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0433 | 1.0171 | 1.0761 | 1.0428 | 1.0167 | 1.0757 | 1.0421 | 1.0162 | 1.0753 | 1.0427 | 1.017 | 1.0758 | 1.0402 | 1.0138 | 1.0743
SW | F4470 Vacy Street | % of Rated A | 0.4543% | 0.4536% | 0.4543% | 0.4543% | 0.4534% | 0.4543% | 0.4544% | 0.4532% | 0.4542% | 0.4543% | 0.4534% | 0.4542% | 0.4543% | 0.4533% | 0.4542%
SW | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW | F4470 Vacy Street | Loading (A) | 2.2713 | 2.2681 | 2.2716 | 2.2717 | 2.2671 | 2.2713 | 2.2718 | 2.266 | 2.2708 | 2.2713 | 2.2669 | 2.2712 | 2.2717 | 2.2664 | 2.271
SW | F4470 Vacy Street | Loading (MVA) | 0.13757 | 0.13717 | 0.1376 | 0.13761 | 0.13705 | 0.13756 | 0.13762 | 0.13692 | 0.1375 | 0.13757 | 0.13703 | 0.13755 | 0.13761 | 0.13697 | 0.13753
SW | F4470 Vacy Street | Loading (MW) | 0.0023914 | 0.0023845 | 0.002392 | 0.0023921 | 0.0023824 | 0.0023913 | 0.0023924 | 0.0023801 | 0.0023903 | 0.0023914 | 0.002382 | 0.0023911 | 0.0023921 | 0.002381 | 0.0023907
SW | F4470 Vacy Street | Power Factor | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605
SW | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | F4470 Vacy Street | Time | 15:30:00 | 21:00:00 | 00:30:00 | 13:00:00 | 21:00:00 | 05:00:00 | 08:00:00 | 21:00:00 | 05:00:00 | 13:00:00 | 21:00:00 | 05:00:00 | 08:00:00 | 21:00:00 | 00:30:00
SW | F4470 Vacy Street | Min Voltage at Constrained Conductor (pu) | 1.0596 | 1.0581 | 1.0598 | 1.0598 | 1.0577 | 1.0596 | 1.0599 | 1.0571 | 1.0594 | 1.0596 | 1.0576 | 1.0596 | 1.0598 | 1.0573 | 1.0595
SW | F4605_West Warwick 33 kV | % of Rated A | 48.27% | 58.47% | 42.75% | 48.29% | 58.5% | 42.76% | 48.32% | 58.53% | 42.78% | 47.89% | 58% | 42.41% | 48.77% | 59.07% | 43.15%
SW | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW | F4605_West Warwick 33 kV | Loading (A) | 187.7584 | 229.204 | 145.3422 | 187.8385 | 229.3199 | 145.3886 | 187.9591 | 229.4314 | 145.4423 | 186.2991 | 227.3569 | 144.1962 | 189.7149 | 231.5638 | 146.6946
SW | F4605_West Warwick 33 kV | Loading (MVA) | 11.0019 | 13.255 | 8.5436 | 11.0022 | 13.2555 | 8.5437 | 11.0026 | 13.2561 | 8.5439 | 10.9131 | 13.1469 | 8.4752 | 11.0926 | 13.3656 | 8.6127
SW | F4605_West Warwick 33 kV | Loading (MW) | 10.7225 | 12.8606 | 8.3625 | 10.7226 | 12.8608 | 8.3626 | 10.7228 | 12.861 | 8.3627 | 10.6376 | 12.7583 | 8.2965 | 10.8081 | 12.9638 | 8.4288
SW | F4605_West Warwick 33 kV | Power Factor | 0.97461 | 0.97024 | 0.97881 | 0.97459 | 0.97022 | 0.9788 | 0.97457 | 0.9702 | 0.97879 | 0.97476 | 0.97044 | 0.97892 | 0.97436 | 0.96994 | 0.97865
SW | F4605_West Warwick 33 kV | Rating (A) | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340
SW | F4605_West Warwick 33 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
SW | F4605_West Warwick 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0249 | 1.0115 | 1.0283 | 1.0245 | 1.011 | 1.0279 | 1.0239 | 1.0106 | 1.0276 | 1.0246 | 1.0114 | 1.0281 | 1.0227 | 1.0095 | 1.027
SW | F4685_Wyalla Street 33 kV | % of Rated A | 24.7% | 26.61% | 17.34% | 24.24% | 26.46% | 17.23% | 24.1% | 25.96% | 17.1% | 23.86% | 25.7% | 16.93% | 24.12% | 26.05% | 17.1%
SW | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1
SW | F4685_Wyalla Street 33 kV | Loading (A) | 170.4405 | 183.583 | 119.665 | 167.2635 | 182.579 | 118.8561 | 166.2595 | 179.1126 | 117.9929 | 164.6192 | 177.301 | 116.7907 | 166.4283 | 179.7577 | 117.9916
SW | F4685_Wyalla Street 33 kV | Loading (MVA) | 9.9051 | 10.6764 | 6.9955 | 9.812 | 10.5758 | 6.9327 | 9.7231 | 10.4751 | 6.8698 | 9.6331 | 10.3778 | 6.8065 | 9.7234 | 10.4764 | 6.8698
SW | F4685_Wyalla Street 33 kV | Loading (MW) | 9.6893 | 10.4326 | 6.8705 | 9.6019 | 10.3384 | 6.8091 | 9.5153 | 10.2443 | 6.7477 | 9.4285 | 10.1507 | 6.6861 | 9.5154 | 10.2445 | 6.7477
SW | F4685_Wyalla Street 33 kV | Power Factor | 0.9781 | 0.97704 | 0.98202 | 0.97848 | 0.97744 | 0.98206 | 0.97851 | 0.97785 | 0.98211 | 0.97865 | 0.978 | 0.9822 | 0.97849 | 0.97775 | 0.98211
SW | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | F4685_Wyalla Street 33 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F4685_Wyalla Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0167 | 1.0175 | 1.0228 | 1.0263 | 1.0134 | 1.0205 | 1.0232 | 1.0232 | 1.0186 | 1.0238 | 1.024 | 1.0196 | 1.0222 | 1.0196 | 1.0186
SW | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 35.05% | 35.65% | 25.28% | 34.9% | 35.51% | 25.2% | 34.7% | 35.3% | 25.07% | 34.4% | 34.98% | 24.88% | 34.57% | 35.15% | 24.94%
SW | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 92.5428 | 95.909 | 59.4168 | 92.1366 | 95.5185 | 59.2171 | 91.6077 | 94.9516 | 58.9107 | 90.8095 | 94.0892 | 58.4583 | 91.254 | 94.5421 | 58.62
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 17.901 | 18.4786 | 11.7358 | 17.8209 | 18.402 | 11.6952 | 17.7167 | 18.2929 | 11.6338 | 17.5722 | 18.1384 | 11.5488 | 17.6464 | 18.2121 | 11.5768
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 17.3645 | 17.8889 | 11.6155 | 17.2983 | 17.8209 | 11.5794 | 17.2027 | 17.7216 | 11.5205 | 17.0753 | 17.5865 | 11.4406 | 17.1299 | 17.6389 | 11.4623
SW | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.96999 | 0.96805 | 0.98971 | 0.97064 | 0.96838 | 0.99006 | 0.97095 | 0.96873 | 0.99022 | 0.97168 | 0.96954 | 0.9906 | 0.97069 | 0.96848 | 0.99006
SW | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235
SW | F5540_7244 Tangkam-Dalby 110 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F5540_7244 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0152 | 1.0112 | 1.0367 | 1.0152 | 1.0111 | 1.0366 | 1.015 | 1.0111 | 1.0365 | 1.0156 | 1.0118 | 1.0369 | 1.0149 | 1.011 | 1.0366
SW | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 76.12% | 55.66% | 35.47% | 75.79% | 55.43% | 35.35% | 75.35% | 55.11% | 35.17% | 74.7% | 54.61% | 34.9% | 75.06% | 54.87% | 35%
SW | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 96.6732 | 100.1906 | 62.0779 | 96.2499 | 99.7829 | 61.8705 | 95.6973 | 99.1906 | 61.5506 | 94.864 | 98.2903 | 61.0789 | 95.3266 | 98.7617 | 61.2458
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 18.7159 | 19.321 | 12.2664 | 18.6322 | 19.2409 | 12.2242 | 18.5231 | 19.1266 | 12.16 | 18.3719 | 18.9648 | 12.0713 | 18.4493 | 19.0418 | 12.1003
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 18.0884 | 18.632 | 12.1227 | 18.0204 | 18.5616 | 12.0856 | 17.9212 | 18.4587 | 12.0244 | 17.7895 | 18.3191 | 11.9416 | 17.8449 | 18.3721 | 11.9634
SW | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.96633 | 0.96421 | 0.98813 | 0.96703 | 0.96457 | 0.98851 | 0.96737 | 0.96495 | 0.9887 | 0.96816 | 0.96582 | 0.98911 | 0.9671 | 0.96469 | 0.98854
SW | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | F5545_7245 Tangkam-Dalby 110 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F5545_7245 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 1.016 | 1.012 | 1.0371 | 1.0159 | 1.012 | 1.037 | 1.0158 | 1.012 | 1.0369 | 1.0164 | 1.0126 | 1.0373 | 1.0157 | 1.0118 | 1.037
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 25.49% | 28.03% | 23.52% | 25.46% | 27.98% | 23.47% | 25.48% | 28% | 23.43% | 25.33% | 27.83% | 23.4% | 25.87% | 36.36% | 22.86%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 73.1634 | 80.163 | 58.0897 | 73.0562 | 80.0212 | 57.9621 | 73.1239 | 80.0792 | 57.8738 | 72.687 | 79.5962 | 57.7913 | 74.241 | 103.9835 | 56.4576
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 14.2099 | 15.4592 | 11.4581 | 14.1837 | 15.4279 | 11.4302 | 14.187 | 15.4308 | 11.4125 | 14.1082 | 15.3457 | 11.3967 | 14.3911 | 19.7011 | 11.1285
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 13.0698 | 14.1127 | 8.6695 | 13.1209 | 14.1645 | 7.9368 | 13.1221 | 14.1656 | 8.6996 | 13.0611 | 14.1013 | 7.91 | 13.2936 | 14.5196 | 10.4659
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.91973 | 0.91286 | 0.75659 | 0.92503 | 0.91806 | 0.69434 | 0.9249 | 0.91796 | 0.76226 | 0.92574 | 0.91886 | 0.69403 | 0.92369 | 0.73693 | 0.94042
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 16:30:00 | 18:00:00 | 05:00:00 | 16:30:00 | 18:00:00 | 02:00:00 | 16:30:00 | 18:00:00 | 05:00:00 | 16:30:00 | 18:00:00 | 02:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0194 | 1.0122 | 1.0353 | 1.019 | 1.0119 | 1.035 | 1.0183 | 1.0114 | 1.035 | 1.0187 | 1.0119 | 1.0351 | 1.0174 | 0.99443 | 1.0346
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 25.47% | 28.01% | 23.51% | 25.43% | 27.96% | 23.46% | 25.46% | 27.98% | 23.42% | 25.3% | 27.81% | 23.39% | 25.85% | 36.34% | 22.84%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 73.1018 | 80.0954 | 58.0689 | 72.9939 | 79.953 | 57.9483 | 73.0615 | 80.0109 | 57.8526 | 72.625 | 79.5283 | 57.7777 | 74.1776 | 103.9189 | 56.4101
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 14.1979 | 15.4461 | 11.4539 | 14.1716 | 15.4147 | 11.4274 | 14.1748 | 15.4176 | 11.4083 | 14.0961 | 15.3325 | 11.3939 | 14.3788 | 19.6887 | 11.1192
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 13.0774 | 14.1229 | 8.6841 | 13.1279 | 14.1741 | 7.9543 | 13.1291 | 14.1752 | 8.7139 | 13.0679 | 14.1107 | 7.9274 | 13.3009 | 14.5557 | 10.4679
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.92044 | 0.91363 | 0.75768 | 0.92572 | 0.91882 | 0.69558 | 0.92559 | 0.91871 | 0.76333 | 0.92643 | 0.91961 | 0.69526 | 0.92439 | 0.73837 | 0.94095
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 16:30:00 | 18:00:00 | 05:00:00 | 16:30:00 | 18:00:00 | 02:00:00 | 16:30:00 | 18:00:00 | 05:00:00 | 16:30:00 | 18:00:00 | 02:00:00 | 16:30:00 | 17:30:00 | 22:00:00
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0194 | 1.0122 | 1.0353 | 1.019 | 1.0119 | 1.035 | 1.0183 | 1.0114 | 1.035 | 1.0187 | 1.0119 | 1.035 | 1.0174 | 0.99442 | 1.0346
SW | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 48.89% | 43.7% | 32.76% | 48.74% | 43.57% | 32.68% | 48.68% | 43.52% | 32.64% | 48.41% | 43.28% | 32.51% | 49.1% | 43.95% | 32.89%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 125.6503 | 139.8468 | 96.308 | 125.2567 | 139.4355 | 96.0757 | 125.101 | 139.2674 | 95.9713 | 124.4156 | 138.4878 | 95.566 | 126.1913 | 140.6444 | 96.7063
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 25.0706 | 27.7921 | 19.3678 | 24.977 | 27.6966 | 19.3132 | 24.9299 | 27.6496 | 19.2848 | 24.7986 | 27.5026 | 19.2084 | 25.1376 | 27.9112 | 19.4309
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 24.0908 | 27.2257 | 17.4021 | 23.9905 | 27.1251 | 17.3419 | 23.9434 | 27.0774 | 17.3128 | 23.7911 | 26.9132 | 17.2149 | 24.1874 | 27.3713 | 17.5007
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.96092 | 0.97962 | 0.89851 | 0.96051 | 0.97936 | 0.89793 | 0.96043 | 0.9793 | 0.89774 | 0.95937 | 0.97857 | 0.89622 | 0.9622 | 0.98066 | 0.90066
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0462 | 1.0417 | 1.0479 | 1.0455 | 1.0412 | 1.0475 | 1.0449 | 1.0406 | 1.0471 | 1.0451 | 1.041 | 1.0476 | 1.0444 | 1.0402 | 1.0467
SW | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 19.85% | 21.79% | 16.72% | 19.78% | 21.73% | 16.68% | 19.76% | 21.7% | 16.66% | 19.64% | 21.57% | 16.59% | 19.94% | 21.93% | 16.79%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141754_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141754_1 | TR_LINE 141691_1
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 151.4254 | 169.7829 | 114.5491 | 150.9273 | 169.2661 | 114.2665 | 150.7352 | 169.058 | 114.1402 | 149.8494 | 168.061 | 113.6438 | 152.1513 | 170.8261 | 115.0398
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 29.5847 | 32.7781 | 23.0314 | 29.4738 | 32.6673 | 22.9653 | 29.4182 | 32.6124 | 22.9311 | 29.2618 | 32.4425 | 22.8377 | 29.6656 | 32.9142 | 23.1095
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 29.4431 | 32.3687 | 22.8956 | 29.3358 | 32.2637 | 22.8267 | 29.2809 | 32.2104 | 22.7916 | 29.1332 | 32.0561 | 22.6899 | 29.5127 | 32.4815 | 22.9855
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.99521 | 0.98751 | 0.99411 | 0.99531 | 0.98764 | 0.99396 | 0.99533 | 0.98767 | 0.99392 | 0.9956 | 0.98809 | 0.99353 | 0.99484 | 0.98685 | 0.99464
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0254 | 1.0133 | 1.0551 | 1.025 | 1.0129 | 1.0547 | 1.0243 | 1.0125 | 1.0543 | 1.0249 | 1.0132 | 1.0546 | 1.0233 | 1.0113 | 1.0542
WB | 6112_Agnes Water 66 kV | % of Rated A | 17.65% | 12.67% | 9.399% | 17.66% | 12.68% | 9.402% | 17.67% | 12.71% | 9.404% | 17.67% | 12.71% | 9.403% | 18.19% | 13.05% | 9.679%
WB | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
WB | 6112_Agnes Water 66 kV | Loading (A) | 50.1381 | 61.0881 | 45.3953 | 50.167 | 61.139 | 45.41 | 50.1815 | 61.2491 | 45.4202 | 50.1788 | 61.247 | 45.4176 | 51.667 | 62.9239 | 46.7511
WB | 6112_Agnes Water 66 kV | Loading (MVA) | 5.798 | 7.1058 | 5.2508 | 5.7979 | 7.1056 | 5.2508 | 5.7979 | 7.1053 | 5.2507 | 5.7979 | 7.1053 | 5.2507 | 5.9639 | 7.3087 | 5.4005
WB | 6112_Agnes Water 66 kV | Loading (MW) | 5.7548 | 7.0263 | 5.2076 | 5.7548 | 7.0263 | 5.2075 | 5.7547 | 7.0262 | 5.2075 | 5.7547 | 7.0262 | 5.2075 | 5.9207 | 7.2293 | 5.3575
WB | 6112_Agnes Water 66 kV | Power Factor | 0.99252 | 0.98878 | 0.99173 | 0.99253 | 0.9888 | 0.99174 | 0.99253 | 0.98883 | 0.99174 | 0.99253 | 0.98883 | 0.99174 | 0.99273 | 0.98909 | 0.99199
WB | 6112_Agnes Water 66 kV | Rating (A) | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483
WB | 6112_Agnes Water 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | 6112_Agnes Water 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0116 | 1.0175 | 1.0118 | 1.011 | 1.0167 | 1.0115 | 1.0107 | 1.0148 | 1.0113 | 1.0107 | 1.0148 | 1.0113 | 1.0097 | 1.0161 | 1.0105
WB | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 8.575% | 7.917% | 6.496% | 8.579% | 7.888% | 6.497% | 8.581% | 7.892% | 6.496% | 8.581% | 7.891% | 6.496% | 8.763% | 8.084% | 6.641%
WB | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 32.4147 | 33.4116 | 25.0753 | 32.4303 | 33.2888 | 25.0801 | 32.438 | 33.3023 | 25.0749 | 32.4366 | 33.2982 | 25.0741 | 33.1253 | 34.1151 | 25.6351
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 7.7459 | 7.9589 | 6.0488 | 7.7452 | 7.9172 | 6.0481 | 7.7448 | 7.9168 | 6.0486 | 7.7448 | 7.9169 | 6.0487 | 7.9032 | 8.0922 | 6.1802
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 7.5545 | 7.765 | 5.5997 | 7.5545 | 7.7788 | 5.5997 | 7.5545 | 7.7788 | 5.5599 | 7.5545 | 7.7788 | 5.5599 | 7.7225 | 7.963 | 5.7112
WB | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.97528 | 0.97563 | 0.92576 | 0.97538 | 0.98171 | 0.92587 | 0.97543 | 0.98171 | 0.9192 | 0.97542 | 0.98171 | 0.91918 | 0.97713 | 0.98206 | 0.9241
WB | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386
WB | 7188_Gin Gin - Korenan QR 132 kV | Time | 16:30:00 | 17:00:00 | 22:30:00 | 16:30:00 | 17:00:00 | 22:30:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
WB | 7188_Gin Gin - Korenan QR 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0407 | 1.0373 | 1.0526 | 1.0401 | 1.0362 | 1.0522 | 1.0398 | 1.0358 | 1.0527 | 1.0398 | 1.0359 | 1.0527 | 1.0389 | 1.0345 | 1.052
WB | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 35.72% | 47.15% | 39.59% | 35.79% | 47.3% | 39.62% | 35.38% | 47.64% | 39.69% | 35.68% | 47.97% | 39.95% | 37.06% | 49.01% | 41.34%
WB | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 176530_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 7315_1 | TR_LINE 176527_1
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 141.796 | 205.5941 | 140.9245 | 142.0875 | 206.2316 | 141.0627 | 140.4423 | 207.6896 | 141.2844 | 141.6676 | 209.1286 | 142.2322 | 147.136 | 213.6942 | 147.1821
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 16.0061 | 23.2204 | 16.0939 | 16.0071 | 23.2155 | 16.0918 | 15.9597 | 23.2293 | 16.0984 | 16.1489 | 23.3904 | 16.2115 | 16.674 | 24.1669 | 16.7306
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 16.0061 | 23.1737 | 16.0931 | 16.0071 | 23.1657 | 16.0906 | 15.9597 | 23.1785 | 16.0975 | 16.1488 | 23.341 | 16.2108 | 16.6736 | 24.1068 | 16.7306
WB | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 1 | 0.99799 | 0.99995 | 1 | 0.99785 | 0.99993 | 1 | 0.99781 | 0.99994 | 1 | 0.99789 | 0.99995 | 0.99998 | 0.99751 | 1
WB | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 6205_East Bundaberg-BUCE 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | 6205_East Bundaberg-BUCE 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9873 | 0.98746 | 0.99886 | 0.98533 | 0.98419 | 0.99775 | 0.99374 | 0.97786 | 0.9966 | 0.99421 | 0.97786 | 0.99691 | 0.99097 | 0.98873 | 0.99422
WB | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 73.69% | 78.47% | 68.17% | 73.42% | 78.35% | 67.97% | 72.61% | 78.9% | 68.04% | 72.46% | 78.84% | 68.01% | 74.34% | 79.85% | 69.63%
WB | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 292.5383 | 342.1228 | 242.6914 | 291.4933 | 341.6209 | 241.9808 | 288.274 | 343.9848 | 242.2293 | 287.6566 | 343.7386 | 242.1178 | 295.1435 | 348.1547 | 247.8855
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 33.1985 | 39.0481 | 27.8107 | 33.0129 | 38.8594 | 27.6974 | 33.0297 | 38.8807 | 27.6944 | 32.9646 | 38.8794 | 27.69 | 33.7366 | 39.8229 | 28.2792
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 33.048 | 38.9913 | 27.2095 | 32.8549 | 38.8049 | 27.0806 | 32.852 | 38.8209 | 27.0879 | 32.8011 | 38.8167 | 27.0756 | 33.5806 | 39.7759 | 27.7277
WB | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.9946 | 0.99795 | 0.97688 | 0.99433 | 0.99801 | 0.97621 | 0.99371 | 0.99784 | 0.97659 | 0.99417 | 0.99775 | 0.97629 | 0.99451 | 0.99827 | 0.97903
WB | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 6302_Bundaberg Central - WEBU 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | 6302_Bundaberg Central - WEBU 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98768 | 0.99207 | 0.99916 | 0.98572 | 0.9887 | 0.99805 | 0.9974 | 0.98239 | 0.99689 | 0.99754 | 0.98308 | 0.99721 | 0.99483 | 0.99407 | 0.99453
WB | 6366_Gootchie 66 kV | % of Rated A | 2.582% | 2.023% | 2.142% | 2.581% | 2.019% | 2.14% | 2.586% | 2.017% | 2.14% | 2.587% | 2.017% | 2.14% | 2.586% | 2.02% | 2.137%
WB | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1
WB | 6366_Gootchie 66 kV | Loading (A) | 3.408 | 3.3786 | 3.4062 | 3.4067 | 3.372 | 3.4027 | 3.4141 | 3.3692 | 3.4025 | 3.4143 | 3.369 | 3.4026 | 3.413 | 3.3737 | 3.3985
WB | 6366_Gootchie 66 kV | Loading (MVA) | 0.4025 | 0.39558 | 0.40207 | 0.40218 | 0.39403 | 0.40124 | 0.40392 | 0.39337 | 0.40119 | 0.40397 | 0.39333 | 0.40121 | 0.40368 | 0.39442 | 0.40024
WB | 6366_Gootchie 66 kV | Loading (MW) | 0.00013561 | 0.00013328 | 0.00013547 | 0.00013551 | 0.00013276 | 0.00013519 | 0.00013609 | 0.00013254 | 0.00013517 | 0.00013611 | 0.00013253 | 0.00013518 | 0.00013601 | 0.00013289 | 0.00013486
WB | 6366_Gootchie 66 kV | Power Factor | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693 | 0.00033693
WB | 6366_Gootchie 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 6366_Gootchie 66 kV | Time | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 20:30:00 | 03:30:00
WB | 6366_Gootchie 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0331 | 1.0242 | 1.0326 | 1.0327 | 1.0222 | 1.0315 | 1.035 | 1.0214 | 1.0315 | 1.035 | 1.0213 | 1.0315 | 1.0347 | 1.0227 | 1.0302
WB | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 62.58% | 64.19% | 54.37% | 63.11% | 64.87% | 54.78% | 63.47% | 65.36% | 55.06% | 63.37% | 65.28% | 55% | 64.29% | 66.3% | 55.68%
WB | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 424.9008 | 469.2204 | 360.4612 | 428.5015 | 474.233 | 363.1639 | 430.9403 | 477.7936 | 365.0278 | 430.2622 | 477.1891 | 364.6695 | 436.4963 | 484.658 | 369.1464
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 101.5359 | 111.5124 | 86.9989 | 102.3304 | 112.5958 | 87.6224 | 102.8798 | 114.5726 | 88.052 | 102.7238 | 114.4436 | 87.9706 | 104.124 | 116.3917 | 88.9949
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 101.5223 | 111.3163 | 86.6212 | 102.3041 | 112.3386 | 87.2796 | 102.8463 | 114.0876 | 87.733 | 102.6915 | 113.972 | 87.6454 | 104.0701 | 115.7901 | 88.7288
WB | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99987 | 0.99824 | 0.99566 | 0.99974 | 0.99772 | 0.99609 | 0.99967 | 0.99577 | 0.99638 | 0.99969 | 0.99588 | 0.9963 | 0.99948 | 0.99483 | 0.99701
WB | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663
WB | 7187_Gin Gin - Bundaberg 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | 7187_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0452 | 1.0241 | 1.0557 | 1.0318 | 1.0226 | 1.0553 | 1.0313 | 1.0318 | 1.0551 | 1.0314 | 1.032 | 1.0551 | 1.0301 | 1.0327 | 1.0545
WB | 7190_Woolooga-Mungar 132 kV | % of Rated A | 2.63% | 2.373% | 2.625% | 2.63% | 2.373% | 2.625% | 2.63% | 2.373% | 2.625% | 2.63% | 2.373% | 2.625% | 2.63% | 2.373% | 2.625%
WB | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2
WB | 7190_Woolooga-Mungar 132 kV | Loading (A) | 14.2566 | 14.2367 | 14.2289 | 14.2566 | 14.2366 | 14.2289 | 14.2566 | 14.2367 | 14.2289 | 14.2567 | 14.2368 | 14.229 | 14.2566 | 14.2362 | 14.2288
WB | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 3.4441 | 3.4364 | 3.4365 | 3.4441 | 3.4363 | 3.4366 | 3.4441 | 3.4364 | 3.4366 | 3.4442 | 3.4364 | 3.4366 | 3.4441 | 3.4361 | 3.4365
WB | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 0.068066 | 0.075507 | 0.09202 | 0.068066 | 0.075507 | 0.09202 | 0.068066 | 0.075507 | 0.09202 | 0.068066 | 0.075507 | 0.09202 | 0.068066 | 0.075507 | 0.09202
WB | 7190_Woolooga-Mungar 132 kV | Power Factor | 0.019763 | 0.021973 | 0.026777 | 0.019763 | 0.021973 | 0.026777 | 0.019763 | 0.021973 | 0.026777 | 0.019763 | 0.021973 | 0.026776 | 0.019763 | 0.021974 | 0.026777
WB | 7190_Woolooga-Mungar 132 kV | Rating (A) | 542 | 600 | 542 | 542 | 600 | 542 | 542 | 600 | 542 | 542 | 600 | 542 | 542 | 600 | 542
WB | 7190_Woolooga-Mungar 132 kV | Time | 08:30:00 | 19:00:00 | 23:00:00 | 08:30:00 | 19:00:00 | 23:00:00 | 08:30:00 | 19:00:00 | 23:00:00 | 08:30:00 | 19:00:00 | 23:00:00 | 08:30:00 | 19:00:00 | 23:00:00
WB | 7190_Woolooga-Mungar 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0566 | 1.0557 | 1.0564 | 1.0566 | 1.0557 | 1.0564 | 1.0566 | 1.0557 | 1.0564 | 1.0566 | 1.0557 | 1.0564 | 1.0566 | 1.0557 | 1.0564
WB | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 1.317% | 0.674% | 1.104% | 1.318% | 0.6745% | 1.104% | 1.318% | 0.6748% | 1.104% | 1.318% | 0.6749% | 1.104% | 1.313% | 0.6759% | 1.105%
WB | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 11.6716 | 6.6123 | 9.2599 | 11.6775 | 6.6173 | 9.2633 | 11.6817 | 6.6201 | 9.2659 | 11.6789 | 6.6209 | 9.2651 | 11.6367 | 6.6301 | 9.2717
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 2.7684 | 1.5578 | 2.2097 | 2.7682 | 1.5572 | 2.2095 | 2.768 | 1.5569 | 2.2094 | 2.7681 | 1.5568 | 2.2094 | 2.7699 | 1.5558 | 2.209
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 2.5067 | 1.3122 | 1.9554 | 2.5067 | 1.3122 | 1.9554 | 2.5067 | 1.3122 | 1.9554 | 2.5067 | 1.3122 | 1.9554 | 2.5067 | 1.3122 | 1.9554
WB | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.90535 | 0.84227 | 0.88483 | 0.90543 | 0.84258 | 0.88491 | 0.90548 | 0.84276 | 0.88497 | 0.90544 | 0.84281 | 0.88496 | 0.90487 | 0.84338 | 0.88512
WB | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839
WB | 7204_Bundaberg - Clayton 132 kV | Time | 15:00:00 | 21:00:00 | 05:30:00 | 15:00:00 | 21:00:00 | 05:30:00 | 15:00:00 | 21:00:00 | 05:30:00 | 15:00:00 | 21:00:00 | 05:30:00 | 15:00:00 | 21:00:00 | 05:30:00
WB | 7204_Bundaberg - Clayton 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0375 | 1.0305 | 1.0438 | 1.0368 | 1.0293 | 1.0433 | 1.0364 | 1.0286 | 1.0429 | 1.0367 | 1.0285 | 1.043 | 1.0411 | 1.0263 | 1.0421
WB | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 62.62% | 41.05% | 37.9% | 63.07% | 41.45% | 38.14% | 62.97% | 41.17% | 38.11% | 63.08% | 41.23% | 38.14% | 63.15% | 41.29% | 38.18%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 155.3009 | 162.5717 | 148.9572 | 156.4091 | 164.1355 | 149.8784 | 156.1696 | 163.0201 | 149.7534 | 156.4397 | 163.2814 | 149.8793 | 156.6106 | 163.4916 | 150.0498
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 36.1387 | 37.365 | 35.5042 | 36.3421 | 37.6428 | 35.6934 | 36.2594 | 37.6487 | 35.6422 | 36.327 | 37.7122 | 35.6776 | 36.2965 | 37.7451 | 35.6612
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 33.789 | 34.3992 | 33.2293 | 34.0713 | 34.733 | 33.4558 | 33.9683 | 35.6118 | 33.3524 | 34.0429 | 35.6801 | 33.4009 | 34.0118 | 35.8169 | 33.3462
WB | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.93498 | 0.92063 | 0.93593 | 0.93752 | 0.9227 | 0.93731 | 0.93682 | 0.9459 | 0.93576 | 0.93712 | 0.94612 | 0.93619 | 0.93705 | 0.94892 | 0.93508
WB | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 7215_Bundaberg - ISIS No 1 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | 7215_Bundaberg - ISIS No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0178 | 1.0053 | 1.0425 | 1.0163 | 1.0031 | 1.0416 | 1.0155 | 1.0101 | 1.041 | 1.0157 | 1.0102 | 1.0412 | 1.0137 | 1.0094 | 1.0395
WB | 7315_Aramara 132 kV | % of Rated A | 24.6% | 28.74% | 15.13% | 25.15% | 29.38% | 15.51% | 25.42% | 28.99% | 15.71% | 25.39% | 28.98% | 15.69% | 26.23% | 29.74% | 16.32%
WB | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1
WB | 7315_Aramara 132 kV | Loading (A) | 268.644 | 346.257 | 167.4799 | 274.6038 | 354.0418 | 171.7333 | 277.6107 | 349.2802 | 173.9626 | 277.2488 | 349.1662 | 173.7332 | 286.408 | 358.4171 | 180.6616
WB | 7315_Aramara 132 kV | Loading (MVA) | 63.1925 | 80.843 | 40.1834 | 64.5022 | 82.5147 | 41.1722 | 65.1703 | 81.6135 | 41.6951 | 65.0866 | 81.5831 | 41.6418 | 67.1219 | 83.6815 | 43.2476
WB | 7315_Aramara 132 kV | Loading (MW) | 58.5545 | 72.9516 | 37.9934 | 59.6456 | 74.3876 | 38.8904 | 60.2456 | 74.1776 | 39.4005 | 60.1537 | 74.1253 | 39.3515 | 62.0093 | 76.169 | 40.8066
WB | 7315_Aramara 132 kV | Power Factor | 0.9266 | 0.90239 | 0.94549 | 0.92471 | 0.90151 | 0.94457 | 0.92443 | 0.90889 | 0.94496 | 0.92421 | 0.90859 | 0.94499 | 0.92383 | 0.91023 | 0.94354
WB | 7315_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 7315_Aramara 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | 7315_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0288 | 1.0211 | 1.0494 | 1.0273 | 1.0193 | 1.0486 | 1.0267 | 1.0219 | 1.0483 | 1.0268 | 1.0219 | 1.0484 | 1.025 | 1.0211 | 1.047
WB | 7316_Aramara 132 kV | % of Rated A | 24.6% | 28.73% | 15.13% | 25.14% | 29.38% | 15.51% | 25.42% | 28.98% | 15.71% | 25.39% | 28.97% | 15.69% | 26.22% | 29.74% | 16.32%
WB | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1
WB | 7316_Aramara 132 kV | Loading (A) | 268.6065 | 346.2086 | 167.4566 | 274.5656 | 353.9924 | 171.7094 | 277.5719 | 349.2314 | 173.9385 | 277.2101 | 349.1175 | 173.7091 | 286.368 | 358.367 | 180.6365
WB | 7316_Aramara 132 kV | Loading (MVA) | 63.1837 | 80.8317 | 40.1778 | 64.4933 | 82.5032 | 41.1664 | 65.1612 | 81.6021 | 41.6893 | 65.0775 | 81.5718 | 41.636 | 67.1126 | 83.6698 | 43.2416
WB | 7316_Aramara 132 kV | Loading (MW) | 58.5462 | 72.9414 | 37.9881 | 59.6372 | 74.3772 | 38.8849 | 60.2372 | 74.1672 | 39.395 | 60.1453 | 74.1149 | 39.346 | 62.0006 | 76.1583 | 40.8008
WB | 7316_Aramara 132 kV | Power Factor | 0.9266 | 0.90239 | 0.94549 | 0.9247 | 0.90151 | 0.94457 | 0.92443 | 0.90889 | 0.94495 | 0.92421 | 0.90858 | 0.94499 | 0.92383 | 0.91022 | 0.94354
WB | 7316_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 7316_Aramara 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | 7316_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0288 | 1.0211 | 1.0494 | 1.0273 | 1.0193 | 1.0486 | 1.0267 | 1.0219 | 1.0483 | 1.0268 | 1.0219 | 1.0484 | 1.025 | 1.0211 | 1.047
WB | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 62.49% | 40.97% | 37.82% | 62.94% | 41.36% | 38.06% | 62.84% | 41.08% | 38.03% | 62.95% | 41.15% | 38.06% | 63.02% | 41.2% | 38.1%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 154.9754 | 162.2318 | 148.6456 | 156.0808 | 163.792 | 149.5647 | 155.8419 | 162.6763 | 149.4401 | 156.1114 | 162.9369 | 149.5657 | 156.2819 | 163.1463 | 149.7359
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 36.0629 | 37.2867 | 35.4299 | 36.2658 | 37.5638 | 35.6186 | 36.1832 | 37.5693 | 35.5676 | 36.2507 | 37.6326 | 35.6028 | 36.2202 | 37.6654 | 35.5865
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 33.7212 | 34.3309 | 33.1624 | 34.0028 | 34.6639 | 33.3884 | 33.9 | 35.5398 | 33.2853 | 33.9745 | 35.608 | 33.3336 | 33.9434 | 35.7443 | 33.2791
WB | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.93507 | 0.92073 | 0.936 | 0.9376 | 0.9228 | 0.93739 | 0.9369 | 0.94598 | 0.93583 | 0.93721 | 0.9462 | 0.93626 | 0.93714 | 0.949 | 0.93516
WB | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 7328_Bundaberg - ISIS No 2 132 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | 7328_Bundaberg - ISIS No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0178 | 1.0053 | 1.0425 | 1.0163 | 1.0031 | 1.0416 | 1.0155 | 1.0101 | 1.041 | 1.0157 | 1.0102 | 1.0412 | 1.0137 | 1.0098 | 1.0395
WB | 7329_Maryborough 132 kV | % of Rated A | 47.85% | 54.66% | 36.74% | 48.4% | 55.29% | 37.13% | 48.72% | 55.6% | 37.33% | 48.79% | 55.7% | 37.39% | 50.08% | 57.1% | 38.33%
WB | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 156753_1
WB | 7329_Maryborough 132 kV | Loading (A) | 269.8473 | 327.9778 | 199.1188 | 272.961 | 331.7257 | 201.2325 | 274.7695 | 333.6006 | 202.3501 | 275.1693 | 334.2179 | 202.6511 | 282.4683 | 342.6036 | 207.7745
WB | 7329_Maryborough 132 kV | Loading (MVA) | 63.0273 | 75.8539 | 47.6091 | 63.6482 | 76.5693 | 48.0667 | 64.0253 | 77.1859 | 48.3228 | 64.1179 | 77.3323 | 48.3951 | 65.691 | 79.1994 | 49.5384
WB | 7329_Maryborough 132 kV | Loading (MW) | 62.4492 | 74.1871 | 47.581 | 62.9991 | 74.8338 | 48.0282 | 63.3417 | 75.3177 | 48.2866 | 63.4249 | 75.4402 | 48.3573 | 64.9129 | 77.2028 | 49.4798
WB | 7329_Maryborough 132 kV | Power Factor | 0.99083 | 0.97803 | 0.99924 | 0.9898 | 0.97733 | 0.99903 | 0.98932 | 0.9758 | 0.9991 | 0.98919 | 0.97553 | 0.99907 | 0.98816 | 0.97479 | 0.99871
WB | 7329_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 7329_Maryborough 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | 7329_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 1.006 | 0.98964 | 1.0359 | 1.004 | 0.98721 | 1.0348 | 1.0031 | 0.98929 | 1.0344 | 1.003 | 0.98925 | 1.0344 | 1.0003 | 0.98747 | 1.0324
WB | 7330_Maryborough 132 kV | % of Rated A | 47.82% | 54.64% | 36.72% | 48.38% | 55.26% | 37.11% | 48.7% | 55.58% | 37.32% | 48.77% | 55.68% | 37.37% | 50.06% | 57.08% | 38.32%
WB | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 156755_1
WB | 7330_Maryborough 132 kV | Loading (A) | 269.7271 | 327.8316 | 199.03 | 272.8394 | 331.5779 | 201.1429 | 274.6471 | 333.4519 | 202.2599 | 275.0467 | 334.069 | 202.5608 | 282.3424 | 342.4509 | 207.6819
WB | 7330_Maryborough 132 kV | Loading (MVA) | 62.9991 | 75.8199 | 47.5877 | 63.6197 | 76.535 | 48.0452 | 63.9967 | 77.1513 | 48.3012 | 64.0892 | 77.2976 | 48.3734 | 65.6615 | 79.1639 | 49.5162
WB | 7330_Maryborough 132 kV | Loading (MW) | 62.4207 | 74.1529 | 47.5596 | 62.9703 | 74.7992 | 48.0065 | 63.3128 | 75.2829 | 48.2649 | 63.3958 | 75.4052 | 48.3355 | 64.8832 | 77.1671 | 49.4575
WB | 7330_Maryborough 132 kV | Power Factor | 0.99082 | 0.97801 | 0.99923 | 0.98979 | 0.97732 | 0.99902 | 0.98931 | 0.97578 | 0.9991 | 0.98918 | 0.97552 | 0.99907 | 0.98815 | 0.97478 | 0.99871
WB | 7330_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 7330_Maryborough 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | 7330_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 1.006 | 0.98964 | 1.0359 | 1.004 | 0.98721 | 1.0348 | 1.0031 | 0.98929 | 1.0344 | 1.003 | 0.98925 | 1.0344 | 1.0003 | 0.98747 | 1.0324
WB | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 18.82% | 13.99% | 8.63% | 18.89% | 14.05% | 8.656% | 18.89% | 14.05% | 8.656% | 18.81% | 13.99% | 8.624% | 19.26% | 14.33% | 8.805%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 46.6841 | 55.4031 | 33.914 | 46.852 | 55.6288 | 34.0183 | 46.8519 | 55.6286 | 34.0182 | 46.655 | 55.4056 | 33.8905 | 47.7729 | 56.7599 | 34.6038
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 11.2477 | 13.3361 | 8.1902 | 11.288 | 13.3901 | 8.2154 | 11.288 | 13.3901 | 8.2154 | 11.2408 | 13.3368 | 8.1846 | 11.5088 | 13.6607 | 8.3567
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 11.1759 | 13.1675 | 8.1412 | 11.2147 | 13.2187 | 8.1675 | 11.2147 | 13.2187 | 8.1675 | 11.1696 | 13.1687 | 8.135 | 11.4264 | 13.4735 | 8.3151
WB | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.99197 | 0.98541 | 0.99402 | 0.99186 | 0.98524 | 0.99417 | 0.99186 | 0.98524 | 0.99417 | 0.99203 | 0.98544 | 0.99395 | 0.99116 | 0.9843 | 0.99503
WB | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 764_Woolooga-Kilkivan No 1 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | 764_Woolooga-Kilkivan No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0538 | 1.0528 | 1.0552 | 1.0538 | 1.0528 | 1.0552 | 1.0538 | 1.0528 | 1.0552 | 1.0538 | 1.0528 | 1.0552 | 1.0537 | 1.0527 | 1.0551
WB | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 18.82% | 13.99% | 8.629% | 18.89% | 14.05% | 8.656% | 18.89% | 14.05% | 8.656% | 18.81% | 13.99% | 8.623% | 19.26% | 14.33% | 8.805%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 46.6838 | 55.4028 | 33.9139 | 46.8518 | 55.6285 | 34.0181 | 46.8516 | 55.6283 | 34.018 | 46.6547 | 55.4052 | 33.8903 | 47.7726 | 56.7595 | 34.6036
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 11.2476 | 13.336 | 8.1901 | 11.2879 | 13.39 | 8.2153 | 11.2879 | 13.39 | 8.2153 | 11.2407 | 13.3367 | 8.1845 | 11.5087 | 13.6606 | 8.3566
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 11.1758 | 13.1675 | 8.1411 | 11.2146 | 13.2186 | 8.1674 | 11.2146 | 13.2186 | 8.1674 | 11.1696 | 13.1686 | 8.135 | 11.4264 | 13.4735 | 8.3151
WB | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.99197 | 0.98541 | 0.99402 | 0.99186 | 0.98524 | 0.99417 | 0.99186 | 0.98524 | 0.99417 | 0.99203 | 0.98544 | 0.99395 | 0.99116 | 0.9843 | 0.99503
WB | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 765_Woolooga-Kilkivan No 2 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | 765_Woolooga-Kilkivan No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0538 | 1.0528 | 1.0552 | 1.0538 | 1.0528 | 1.0552 | 1.0538 | 1.0528 | 1.0552 | 1.0538 | 1.0528 | 1.0552 | 1.0537 | 1.0527 | 1.0551
WB | 784_ISIS 132 kV | % of Rated A | 32.21% | 21.69% | 18.61% | 32.18% | 22.18% | 18.43% | 32.28% | 21.9% | 18.35% | 32.41% | 21.78% | 18.4% | 32.3% | 22.14% | 18.31%
WB | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB | 784_ISIS 132 kV | Loading (A) | 79.8743 | 85.9036 | 73.15 | 79.8014 | 87.8513 | 72.4185 | 80.0523 | 86.7106 | 72.1315 | 80.3813 | 86.233 | 72.3273 | 80.0922 | 87.6814 | 71.9712
WB | 784_ISIS 132 kV | Loading (MVA) | 19.2468 | 19.7997 | 17.5207 | 19.2268 | 20.2018 | 17.3358 | 19.3005 | 20.0079 | 17.2642 | 19.3818 | 19.9006 | 17.3122 | 19.3069 | 20.178 | 17.2128
WB | 784_ISIS 132 kV | Loading (MW) | 17.0223 | 1.3656 | 14.0698 | 17.0165 | 0.59739 | 13.7845 | 17.0017 | 0.84723 | 13.6313 | 17.1112 | 1.0254 | 13.7191 | 16.9869 | 0.54723 | 13.5032
WB | 784_ISIS 132 kV | Power Factor | 0.88442 | 0.06895 | 0.80304 | 0.88504 | 0.029176 | 0.79514 | 0.8809 | 0.042078 | 0.78957 | 0.88285 | 0.051344 | 0.79245 | 0.87983 | 0.026707 | 0.78449
WB | 784_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 784_ISIS 132 kV | Time | 10:30:00 | 18:30:00 | 03:00:00 | 10:30:00 | 18:30:00 | 03:00:00 | 10:30:00 | 19:00:00 | 03:00:00 | 10:30:00 | 19:00:00 | 03:00:00 | 10:30:00 | 19:00:00 | 03:00:00
WB | 784_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0539 | 1.0081 | 1.0476 | 1.0538 | 1.0058 | 1.047 | 1.0545 | 1.0092 | 1.0469 | 1.0546 | 1.0094 | 1.0469 | 1.0544 | 1.0066 | 1.0461
WB | 785_ISIS 132 kV | % of Rated A | 32.67% | 22% | 18.88% | 32.64% | 22.5% | 18.69% | 32.74% | 22.2% | 18.61% | 32.87% | 22.08% | 18.66% | 32.76% | 22.45% | 18.57%
WB | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB | 785_ISIS 132 kV | Loading (A) | 81.0156 | 87.1106 | 74.1868 | 80.9418 | 89.0869 | 73.4442 | 81.196 | 87.9294 | 73.1526 | 81.5299 | 87.4448 | 73.3515 | 81.2363 | 88.9145 | 72.9897
WB | 785_ISIS 132 kV | Loading (MVA) | 19.5213 | 20.0749 | 17.7682 | 19.501 | 20.4828 | 17.5805 | 19.5756 | 20.286 | 17.5077 | 19.6581 | 20.1773 | 17.5565 | 19.5821 | 20.4587 | 17.4556
WB | 785_ISIS 132 kV | Loading (MW) | 17.2765 | 1.3974 | 14.2816 | 17.2706 | 0.61819 | 13.9921 | 17.2557 | 0.87154 | 13.8368 | 17.3667 | 1.0522 | 13.9258 | 17.2406 | 0.56728 | 13.7068
WB | 785_ISIS 132 kV | Power Factor | 0.88501 | 0.069606 | 0.80377 | 0.88563 | 0.030165 | 0.79588 | 0.88149 | 0.042952 | 0.79032 | 0.88344 | 0.052139 | 0.7932 | 0.88043 | 0.027712 | 0.78524
WB | 785_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 785_ISIS 132 kV | Time | 10:30:00 | 18:30:00 | 03:00:00 | 10:30:00 | 18:30:00 | 03:00:00 | 10:30:00 | 19:00:00 | 03:00:00 | 10:30:00 | 19:00:00 | 03:00:00 | 10:30:00 | 19:00:00 | 03:00:00
WB | 785_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0539 | 1.008 | 1.0476 | 1.0538 | 1.0056 | 1.047 | 1.0545 | 1.0091 | 1.0468 | 1.0546 | 1.0092 | 1.0469 | 1.0543 | 1.0064 | 1.046
WB | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 150.2% | 97.58% | 74.79% | 151.5% | 98.62% | 75.36% | 152.3% | 99.4% | 75.74% | 152.1% | 99.27% | 75.67% | 154.3% | 100.8% | 76.6%
WB | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 112961_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 6770_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 6770_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 6770_1 | TR_LINE 112963_1
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 425.043 | 469.3667 | 360.5119 | 428.6344 | 474.3779 | 363.2176 | 431.0734 | 478.1199 | 365.0836 | 430.3949 | 477.5064 | 364.725 | 436.6298 | 485.0549 | 369.2069
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 101.5658 | 110.9044 | 87.0111 | 101.8712 | 111.9605 | 87.6354 | 102.4118 | 113.1094 | 88.0655 | 102.2578 | 112.9886 | 87.984 | 103.6351 | 114.8491 | 89.0095
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 101.5542 | 110.8024 | 86.6226 | 101.8678 | 111.8153 | 87.2822 | 102.4056 | 112.9156 | 87.7365 | 102.2521 | 112.8027 | 87.6488 | 103.6195 | 114.586 | 88.7342
WB | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99989 | 0.99908 | 0.99458 | 0.99997 | 0.9987 | 0.99505 | 0.99994 | 0.99829 | 0.99536 | 0.99994 | 0.99835 | 0.99528 | 0.99985 | 0.99771 | 0.99606
WB | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482
WB | 786_Gin Gin - Bundaberg 132 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | 786_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0403 | 1.0271 | 1.0532 | 1.0342 | 1.0257 | 1.0527 | 1.0337 | 1.0097 | 1.0524 | 1.0338 | 1.0101 | 1.0525 | 1.0326 | 1.0096 | 1.0517
WB | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 37.05% | 35.94% | 27.36% | 36.89% | 35.77% | 27.24% | 36.8% | 35.68% | 27.17% | 36.61% | 35.5% | 27.05% | 37.13% | 35.77% | 27.41%
WB | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1
WB | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 203.014 | 208.0911 | 142.5419 | 202.1508 | 207.0808 | 141.898 | 201.6491 | 206.5773 | 141.5767 | 200.6338 | 205.5558 | 140.9284 | 203.4687 | 207.0905 | 142.7958
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 23.8265 | 24.4154 | 16.848 | 23.7251 | 24.2986 | 16.7725 | 23.667 | 24.2402 | 16.7347 | 23.5507 | 24.1233 | 16.6592 | 23.8768 | 24.6056 | 16.8768
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 22.5622 | 23.1023 | 16.233 | 22.4635 | 23.0008 | 16.1646 | 22.413 | 22.9501 | 16.1304 | 22.312 | 22.8485 | 16.062 | 22.6146 | 23.3099 | 16.2637
WB | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.94694 | 0.94622 | 0.9635 | 0.94683 | 0.94659 | 0.96376 | 0.94702 | 0.94678 | 0.96389 | 0.9474 | 0.94715 | 0.96415 | 0.94714 | 0.94734 | 0.96367
WB | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M001_Tarong-Kingaroy East 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M001_Tarong-Kingaroy East 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99515 | 0.99377 | 1.016 | 0.99531 | 0.99409 | 1.0162 | 0.99547 | 0.99424 | 1.0163 | 0.99583 | 0.9946 | 1.0165 | 0.99495 | 1.0072 | 1.0159
WB | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 37.07% | 35.96% | 27.38% | 36.91% | 35.79% | 27.25% | 36.82% | 35.7% | 27.19% | 36.63% | 35.52% | 27.07% | 37.15% | 35.79% | 27.42%
WB | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1
WB | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 203.1343 | 208.2145 | 142.626 | 202.2706 | 207.2036 | 141.9816 | 201.7686 | 206.6998 | 141.6602 | 200.7527 | 205.6777 | 141.0115 | 203.5893 | 207.2132 | 142.88
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 23.1105 | 23.6557 | 16.5667 | 23.0158 | 23.5482 | 16.4948 | 22.9623 | 23.4945 | 16.4588 | 22.8551 | 23.3869 | 16.3869 | 23.1575 | 23.8597 | 16.5942
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 22.1024 | 22.6188 | 16.0097 | 22.0077 | 22.522 | 15.9433 | 21.9595 | 22.4737 | 15.9102 | 21.8631 | 22.3769 | 15.8438 | 22.1526 | 22.8313 | 16.0396
WB | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.95638 | 0.95617 | 0.96638 | 0.9562 | 0.95642 | 0.96657 | 0.95633 | 0.95655 | 0.96666 | 0.9566 | 0.95681 | 0.96686 | 0.95661 | 0.95689 | 0.96658
WB | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M002_Tarong-Kingaroy West 66 kV | Time | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M002_Tarong-Kingaroy West 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99515 | 0.99377 | 1.016 | 0.99531 | 0.99409 | 1.0162 | 0.99547 | 0.99424 | 1.0163 | 0.99583 | 0.9946 | 1.0165 | 0.99495 | 1.0072 | 1.0159
WB | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 85.64% | 75.12% | 46.58% | 85.62% | 75.09% | 46.57% | 85.61% | 75.09% | 46.56% | 85.57% | 75.06% | 46.55% | 87.68% | 76.93% | 47.65%
WB | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1
WB | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 113.0425 | 125.4438 | 74.0546 | 113.0221 | 125.4014 | 74.0401 | 113.0021 | 125.4031 | 74.0332 | 112.9545 | 125.351 | 74.0161 | 115.739 | 128.4796 | 75.7624
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 12.4071 | 13.8862 | 8.4124 | 12.407 | 13.8859 | 8.4123 | 12.4069 | 13.8859 | 8.4123 | 12.4066 | 13.8856 | 8.4122 | 12.6886 | 14.2026 | 8.6006
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 12.234 | 13.6711 | 8.3314 | 12.2339 | 13.671 | 8.3314 | 12.2339 | 13.671 | 8.3314 | 12.2337 | 13.6708 | 8.3313 | 12.5075 | 13.9776 | 8.5157
WB | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.98605 | 0.98451 | 0.99037 | 0.98605 | 0.98452 | 0.99037 | 0.98605 | 0.98452 | 0.99037 | 0.98606 | 0.98453 | 0.99038 | 0.98573 | 0.98415 | 0.99013
WB | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M003_Kingaroy- Yarraman 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M003_Kingaroy- Yarraman 66 kV | Min Voltage at Constrained Conductor (pu) | 0.96008 | 0.9683 | 0.9937 | 0.96024 | 0.9686 | 0.99388 | 0.9604 | 0.96859 | 0.99397 | 0.96079 | 0.96897 | 0.99419 | 0.95898 | 0.96696 | 0.99302
WB | M004_Murgon-Kingaroy 66 kV | % of Rated A | 7.921% | 6.591% | 5.348% | 7.921% | 6.591% | 5.348% | 7.921% | 6.591% | 5.348% | 7.921% | 6.591% | 5.348% | 7.922% | 6.594% | 5.347%
WB | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB | M004_Murgon-Kingaroy 66 kV | Loading (A) | 13.3867 | 15.7529 | 12.46 | 13.3868 | 15.7536 | 12.4599 | 13.3868 | 15.7536 | 12.4599 | 13.3866 | 15.7519 | 12.4602 | 13.3876 | 15.7593 | 12.4593
WB | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 1.9222 | 2.2474 | 1.8072 | 1.922 | 2.2473 | 1.8071 | 1.922 | 2.2473 | 1.8071 | 1.9224 | 2.2476 | 1.8074 | 1.9208 | 2.2461 | 1.8062
WB | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 1.5453 | 2.0073 | 1.3315 | 1.5453 | 2.0073 | 1.3315 | 1.5453 | 2.0073 | 1.3315 | 1.5453 | 2.0073 | 1.3315 | 1.5454 | 2.0074 | 1.3315
WB | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.80396 | 0.89316 | 0.73677 | 0.80402 | 0.89322 | 0.7368 | 0.80402 | 0.89322 | 0.7368 | 0.80385 | 0.89307 | 0.73667 | 0.80454 | 0.8937 | 0.73716
WB | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | M004_Murgon-Kingaroy 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M004_Murgon-Kingaroy 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2561 | 1.248 | 1.2688 | 1.256 | 1.2479 | 1.2687 | 1.256 | 1.2479 | 1.2687 | 1.2563 | 1.2482 | 1.2689 | 1.2551 | 1.2468 | 1.2682
WB | M005 KINGAROY-BOONDOOMA | % of Rated A | 19.7% | 13.69% | 12.02% | 19.69% | 13.69% | 12.02% | 19.69% | 13.69% | 12.02% | 19.68% | 13.68% | 12.02% | 19.7% | 13.7% | 12.02%
WB | M005 KINGAROY-BOONDOOMA | Limiting Line Name | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1
WB | M005 KINGAROY-BOONDOOMA | Loading (A) | 26.396 | 24.7833 | 21.0374 | 26.3885 | 24.7763 | 21.0348 | 26.3849 | 24.7729 | 21.0336 | 26.3768 | 24.7641 | 21.0306 | 26.3957 | 24.7896 | 21.0386
WB | M005 KINGAROY-BOONDOOMA | Loading (MVA) | 3.0252 | 2.8428 | 2.4622 | 3.0251 | 2.8427 | 2.4622 | 3.0251 | 2.8427 | 2.4622 | 3.0251 | 2.8427 | 2.4622 | 3.0252 | 2.8428 | 2.4622
WB | M005 KINGAROY-BOONDOOMA | Loading (MW) | 2.843 | 2.6725 | 2.3166 | 2.843 | 2.6725 | 2.3166 | 2.843 | 2.6725 | 2.3166 | 2.843 | 2.6725 | 2.3166 | 2.843 | 2.6725 | 2.3166
WB | M005 KINGAROY-BOONDOOMA | Power Factor | 0.93946 | 0.93981 | 0.94059 | 0.93946 | 0.93981 | 0.94059 | 0.93946 | 0.93981 | 0.94059 | 0.93947 | 0.93982 | 0.94059 | 0.93946 | 0.93981 | 0.94059
WB | M005 KINGAROY-BOONDOOMA | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
WB | M005 KINGAROY-BOONDOOMA | Time | 15:00:00 | 18:00:00 | 01:00:00 | 15:00:00 | 18:00:00 | 01:00:00 | 15:00:00 | 18:00:00 | 01:00:00 | 15:00:00 | 18:00:00 | 01:00:00 | 15:00:00 | 18:00:00 | 01:00:00
WB | M005 KINGAROY-BOONDOOMA | Min Voltage at Constrained Conductor (pu) | 1.0025 | 1.0034 | 1.0238 | 1.0028 | 1.0037 | 1.024 | 1.003 | 1.0038 | 1.024 | 1.0033 | 1.0042 | 1.0242 | 1.0026 | 1.0032 | 1.0238
WB | M007_Proston 66 kV | % of Rated A | 11.18% | 11.3% | 7.985% | 11.18% | 11.3% | 7.985% | 11.18% | 11.3% | 7.985% | 11.18% | 11.3% | 7.984% | 11.19% | 11.31% | 7.987%
WB | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1
WB | M007_Proston 66 kV | Loading (A) | 11.0717 | 14.3488 | 9.6617 | 11.0724 | 14.3504 | 9.662 | 11.0724 | 14.3504 | 9.6619 | 11.0704 | 14.3465 | 9.661 | 11.0785 | 14.3635 | 9.6648
WB | M007_Proston 66 kV | Loading (MVA) | 1.5898 | 2.0275 | 1.4014 | 1.5898 | 2.0275 | 1.4013 | 1.5898 | 2.0275 | 1.4014 | 1.5898 | 2.0275 | 1.4014 | 1.5895 | 2.0276 | 1.4012
WB | M007_Proston 66 kV | Loading (MW) | 1.5448 | 2.0065 | 1.331 | 1.5448 | 2.0065 | 1.331 | 1.5448 | 2.0065 | 1.331 | 1.5448 | 2.0065 | 1.331 | 1.5448 | 2.0066 | 1.331
WB | M007_Proston 66 kV | Power Factor | 0.97171 | 0.98045 | 0.94976 | 0.97172 | 0.98044 | 0.94977 | 0.97172 | 0.98044 | 0.94977 | 0.97167 | 0.98045 | 0.94972 | 0.97187 | 0.98043 | 0.9499
WB | M007_Proston 66 kV | Rating (A) | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121
WB | M007_Proston 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M007_Proston 66 kV | Min Voltage at Constrained Conductor (pu) | 1.256 | 1.2361 | 1.2688 | 1.2559 | 1.2359 | 1.2687 | 1.2559 | 1.2359 | 1.2687 | 1.2562 | 1.2363 | 1.2689 | 1.2551 | 1.2348 | 1.2682
WB | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 27.25% | 22.58% | 15.36% | 27.25% | 22.58% | 15.36% | 27.25% | 22.58% | 15.36% | 27.08% | 22.44% | 15.27% | 27.61% | 22.87% | 15.55%
WB | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 49.3247 | 56.8938 | 37.6381 | 49.3285 | 56.9003 | 37.6396 | 49.3283 | 56.9002 | 37.6395 | 49.0105 | 56.5394 | 37.4193 | 49.9773 | 57.6434 | 38.0856
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 7.1638 | 8.228 | 5.5006 | 7.1638 | 8.2281 | 5.5006 | 7.1638 | 8.2281 | 5.5006 | 7.1185 | 8.177 | 5.4688 | 7.2548 | 8.3306 | 5.5643
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 7.1501 | 8.1907 | 5.4993 | 7.1501 | 8.1908 | 5.4994 | 7.1501 | 8.1908 | 5.4994 | 7.1057 | 8.1412 | 5.4673 | 7.2392 | 8.29 | 5.5635
WB | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.99787 | 0.99519 | 0.99977 | 0.99786 | 0.99518 | 0.99977 | 0.99786 | 0.99518 | 0.99977 | 0.99798 | 0.99534 | 0.99973 | 0.99761 | 0.99484 | 0.99985
WB | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245
WB | M008_Kilkivan-Murgon No 1 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M008_Kilkivan-Murgon No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2703 | 1.2649 | 1.278 | 1.2702 | 1.2647 | 1.278 | 1.2702 | 1.2647 | 1.278 | 1.2703 | 1.2649 | 1.2781 | 1.2696 | 1.264 | 1.2777
WB | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 25.58% | 20.72% | 13.57% | 25.58% | 20.72% | 13.57% | 25.58% | 20.72% | 13.57% | 25.39% | 20.57% | 13.48% | 25.98% | 21.04% | 13.77%
WB | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 43.2348 | 49.5168 | 31.6282 | 43.2382 | 49.5226 | 31.6294 | 43.2381 | 49.5225 | 31.6293 | 42.909 | 49.1508 | 31.4115 | 43.9082 | 50.2851 | 32.0806
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 6.2117 | 7.0701 | 4.6223 | 6.2117 | 7.0702 | 4.6223 | 6.2117 | 7.0702 | 4.6223 | 6.1661 | 7.0187 | 4.5907 | 6.303 | 7.1734 | 4.6854
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 6.2107 | 7.0585 | 4.6027 | 6.2107 | 7.0585 | 4.6027 | 6.2107 | 7.0585 | 4.6027 | 6.1654 | 7.008 | 4.57 | 6.3014 | 7.1597 | 4.668
WB | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.98998 | 0.98711 | 0.99575 | 0.98997 | 0.98711 | 0.99576 | 0.98997 | 0.98711 | 0.99576 | 0.99015 | 0.98729 | 0.99548 | 0.98961 | 0.98673 | 0.99597
WB | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | M009_Kilkivan-Murgon No 2 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M009_Kilkivan-Murgon No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2561 | 1.248 | 1.2688 | 1.256 | 1.2479 | 1.2687 | 1.256 | 1.2479 | 1.2687 | 1.2563 | 1.2482 | 1.2689 | 1.2551 | 1.2468 | 1.2682
WB | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 16% | 13.83% | 9.542% | 17.65% | 15.07% | 10.51% | 17.94% | 15.49% | 10.53% | 17.67% | 15.26% | 10.38% | 18% | 15.31% | 10.56%
WB | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1
WB | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 39.8314 | 52.8357 | 35.3061 | 43.945 | 57.5568 | 38.8829 | 44.6672 | 59.1665 | 38.979 | 44.001 | 58.2863 | 38.3985 | 44.8201 | 58.5013 | 39.0722
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 4.6643 | 6.1303 | 4.1217 | 5.1327 | 6.7474 | 4.5332 | 5.2112 | 6.8562 | 4.6001 | 5.133 | 6.7523 | 4.5314 | 5.2119 | 6.8516 | 4.6005
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 4.6563 | 6.0934 | 4.1201 | 5.1175 | 6.697 | 4.5281 | 5.1945 | 6.7994 | 4.5954 | 5.1176 | 6.6985 | 4.5274 | 5.1947 | 6.798 | 4.5955
WB | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.99824 | 0.99395 | 0.9996 | 0.997 | 0.99249 | 0.99885 | 0.99676 | 0.99168 | 0.99894 | 0.99697 | 0.99199 | 0.99907 | 0.99667 | 0.99214 | 0.9989
WB | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | M010_Maryborough - Owanyilla 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M010_Maryborough - Owanyilla 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0244 | 1.015 | 1.0212 | 1.0217 | 1.0255 | 1.0198 | 1.0206 | 1.0137 | 1.0323 | 1.0205 | 1.0134 | 1.0323 | 1.0172 | 1.0245 | 1.03
WB | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 47.3% | 47.05% | 26.7% | 47.72% | 47.49% | 26.93% | 47.72% | 47.49% | 26.93% | 47.71% | 47.48% | 26.93% | 49.04% | 48.84% | 27.66%
WB | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1
WB | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 62.4332 | 78.5669 | 42.4501 | 62.9872 | 79.3073 | 42.8185 | 62.987 | 79.3071 | 42.8184 | 62.9799 | 79.2962 | 42.8153 | 64.7367 | 81.5709 | 43.9853
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 8.9733 | 11.2097 | 6.1606 | 9.0514 | 11.3125 | 6.2134 | 9.0514 | 11.3125 | 6.2134 | 9.0513 | 11.3125 | 6.2134 | 9.2956 | 11.6234 | 6.3797
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 8.868 | 11.0362 | 6.1211 | 8.9438 | 11.1355 | 6.1728 | 8.9438 | 11.1355 | 6.1728 | 8.9438 | 11.1354 | 6.1728 | 9.1812 | 11.4356 | 6.3358
WB | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.98824 | 0.98451 | 0.99356 | 0.9881 | 0.98434 | 0.99344 | 0.9881 | 0.98434 | 0.99344 | 0.98811 | 0.98434 | 0.99344 | 0.98768 | 0.98383 | 0.99309
WB | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M011_Kilkivan-Maryborough 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M011_Kilkivan-Maryborough 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2573 | 1.2481 | 1.2695 | 1.257 | 1.2477 | 1.2694 | 1.257 | 1.2477 | 1.2694 | 1.2572 | 1.2479 | 1.2695 | 1.2561 | 1.2465 | 1.2688
WB | M012_Maryborough-Rocky St 66 kV | % of Rated A | 41.95% | 43.46% | 31.78% | 42.21% | 43.17% | 31.93% | 42.28% | 43.72% | 31.57% | 42.2% | 43.66% | 31.52% | 43.14% | 43.99% | 32.18%
WB | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB | M012_Maryborough-Rocky St 66 kV | Loading (A) | 229.8743 | 251.6335 | 165.5906 | 231.3154 | 249.9774 | 166.3688 | 231.684 | 253.1431 | 164.4803 | 231.2832 | 252.7659 | 164.2278 | 236.4005 | 254.6991 | 167.6428
WB | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 26.9344 | 29.2192 | 19.3316 | 27.035 | 29.3275 | 19.3968 | 27.0479 | 29.3591 | 19.4119 | 26.9982 | 29.3113 | 19.3813 | 27.5086 | 29.8584 | 19.7394
WB | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 26.9264 | 29.1741 | 19.2813 | 27.0207 | 29.275 | 19.3557 | 27.0326 | 29.3012 | 19.3664 | 26.9831 | 29.2537 | 19.3355 | 27.4946 | 29.8089 | 19.6989
WB | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.9997 | 0.99846 | 0.99704 | 0.99947 | 0.99821 | 0.99755 | 0.99943 | 0.99803 | 0.99733 | 0.99944 | 0.99804 | 0.99731 | 0.99949 | 0.99834 | 0.99762
WB | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M012_Maryborough-Rocky St 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M012_Maryborough-Rocky St 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0205 | 1.0105 | 1.0188 | 1.0178 | 1.021 | 1.0173 | 1.0166 | 1.0092 | 1.0299 | 1.0165 | 1.0091 | 1.0299 | 1.0132 | 1.0202 | 1.0274
WB | M014_Torquay-Pialba 66 kV | % of Rated A | 17.55% | 17.34% | 13.7% | 17.69% | 17.32% | 13.81%
WB | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB | M014_Torquay-Pialba 66 kV | Loading (A) | 106.6823 | 116.5262 | 75.4957 | 107.5362 | 116.3716 | 76.0785
WB | M014_Torquay-Pialba 66 kV | Loading (MVA) | 12.1641 | 12.9959 | 8.6485 | 12.2245 | 13.0491 | 8.7019
WB | M014_Torquay-Pialba 66 kV | Loading (MW) | 11.3738 | 12.1726 | 7.3197 | 11.4534 | 12.265 | 7.3709
WB | M014_Torquay-Pialba 66 kV | Power Factor | 0.93503 | 0.93665 | 0.84635 | 0.93692 | 0.93991 | 0.84704
WB | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551
WB | M014_Torquay-Pialba 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M014_Torquay-Pialba 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99743 | 0.97561 | 1.0021 | 0.99442 | 0.98091 | 1.0006
WB | M014_Torquay-SOPI 66 kV | % of Rated A | [6 empty] | 17.81% | 17.54% | 13.72% | 17.86% | 17.58% | 13.75% | 18.35% | 17.92% | 14.03%
WB | M014_Torquay-SOPI 66 kV | Limiting Line Name | [6 empty] | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB | M014_Torquay-SOPI 66 kV | Loading (A) | [6 empty] | 108.2829 | 117.8803 | 75.5943 | 108.5714 | 118.1662 | 75.7454 | 111.5476 | 120.4105 | 77.3069
WB | M014_Torquay-SOPI 66 kV | Loading (MVA) | [6 empty] | 12.2893 | 13.1124 | 8.7554 | 12.3176 | 13.1375 | 8.7711 | 12.5968 | 13.4205 | 8.922
WB | M014_Torquay-SOPI 66 kV | Loading (MW) | [6 empty] | 11.5485 | 12.3593 | 7.4336 | 11.5822 | 12.3903 | 7.4534 | 11.8779 | 12.713 | 7.6441
WB | M014_Torquay-SOPI 66 kV | Power Factor | [6 empty] | 0.93972 | 0.94256 | 0.84904 | 0.9403 | 0.94312 | 0.84977 | 0.94293 | 0.94728 | 0.85677
WB | M014_Torquay-SOPI 66 kV | Rating (A) | [6 empty] | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | M014_Torquay-SOPI 66 kV | Time | [6 empty] | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M014_Torquay-SOPI 66 kV | Min Voltage at Constrained Conductor (pu) | [6 empty] | 0.9928 | 0.97305 | 1.0132 | 0.99244 | 0.97256 | 1.013 | 0.98786 | 0.97499 | 1.0096
WB | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.892% | 1.487% | 1.572% | 1.891% | 1.486% | 1.57% | 1.894% | 1.484% | 1.57% | 1.894% | 1.483% | 1.57% | 1.894% | 1.488% | 1.569%
WB | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1
WB | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.4972 | 2.4832 | 2.4991 | 2.4957 | 2.4813 | 2.497 | 2.5004 | 2.4776 | 2.497 | 2.5005 | 2.4773 | 2.4969 | 2.4997 | 2.4849 | 2.494
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 0.29494 | 0.29164 | 0.29537 | 0.29459 | 0.29118 | 0.29489 | 0.29569 | 0.29031 | 0.29488 | 0.29572 | 0.29024 | 0.29487 | 0.29551 | 0.29204 | 0.29417
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 0.0011273 | 0.0011147 | 0.001129 | 0.001126 | 0.001113 | 0.0011272 | 0.0011302 | 0.0011097 | 0.0011271 | 0.0011304 | 0.0011094 | 0.0011271 | 0.0011296 | 0.0011163 | 0.0011244
WB | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224
WB | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M015_Maryborough-Howard No 1 66 kV | Time | 14:00:00 | 21:30:00 | 03:00:00 | 14:00:00 | 18:30:00 | 03:00:00 | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 19:00:00 | 03:30:00
WB | M015_Maryborough-Howard No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0332 | 1.0274 | 1.0339 | 1.0325 | 1.0266 | 1.0331 | 1.0345 | 1.025 | 1.0331 | 1.0345 | 1.0249 | 1.033 | 1.0342 | 1.0281 | 1.0318
WB | M016_Maryborough-Howard No 2 66 kV | % of Rated A | 1.935% | 1.521% | 1.607% | 1.934% | 1.519% | 1.606% | 1.937% | 1.517% | 1.606% | 1.937% | 1.517% | 1.606% | 1.937% | 1.522% | 1.604%
WB | M016_Maryborough-Howard No 2 66 kV | Limiting Line Name | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2
WB | M016_Maryborough-Howard No 2 66 kV | Loading (A) | 2.5538 | 2.5395 | 2.5557 | 2.5523 | 2.5375 | 2.5537 | 2.5571 | 2.5337 | 2.5536 | 2.5572 | 2.5334 | 2.5535 | 2.5563 | 2.5413 | 2.5505
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MVA) | 0.30162 | 0.29825 | 0.30206 | 0.30127 | 0.29778 | 0.30158 | 0.30239 | 0.29689 | 0.30156 | 0.30242 | 0.29682 | 0.30155 | 0.30221 | 0.29866 | 0.30084
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MW) | 0.0010189 | 0.0010075 | 0.0010204 | 0.0010177 | 0.0010059 | 0.0010187 | 0.0010215 | 0.0010029 | 0.0010187 | 0.0010216 | 0.0010027 | 0.0010187 | 0.0010209 | 0.0010089 | 0.0010163
WB | M016_Maryborough-Howard No 2 66 kV | Power Factor | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731 | 0.0033731
WB | M016_Maryborough-Howard No 2 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M016_Maryborough-Howard No 2 66 kV | Time | 14:00:00 | 21:30:00 | 03:00:00 | 14:00:00 | 18:30:00 | 03:00:00 | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 21:30:00 | 03:00:00 | 09:30:00 | 19:00:00 | 03:30:00
WB | M016_Maryborough-Howard No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0332 | 1.0274 | 1.0339 | 1.0325 | 1.0266 | 1.0331 | 1.0345 | 1.025 | 1.0331 | 1.0345 | 1.0249 | 1.033 | 1.0342 | 1.0281 | 1.0318
WB | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 12.84% | 3.07% | 4.341% | 12.92% | 3.142% | 4.404% | 12.8% | 3.059% | 4.345% | 12.75% | 3.008% | 4.305% | 12.76% | 2.904% | 4.283%
WB | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1
WB | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 70.3548 | 17.7781 | 22.6164 | 70.7891 | 18.1927 | 22.9462 | 70.1296 | 17.713 | 22.6363 | 69.8477 | 17.4174 | 22.4267 | 69.9185 | 16.8132 | 22.3136
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 8.2398 | 2.0575 | 2.6568 | 8.287 | 2.1024 | 2.693 | 8.2263 | 2.0446 | 2.6557 | 8.1939 | 2.01 | 2.6311 | 8.1996 | 1.96 | 2.6144
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 7.619 | 1.973 | 2.5603 | 7.6285 | 1.9861 | 2.5737 | 7.585 | 1.9285 | 2.5352 | 7.5518 | 1.8935 | 2.5103 | 7.5876 | 1.8726 | 2.5105
WB | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.92465 | 0.95892 | 0.96367 | 0.92053 | 0.94471 | 0.95569 | 0.92203 | 0.94321 | 0.95461 | 0.92163 | 0.94202 | 0.95409 | 0.92535 | 0.95538 | 0.96023
WB | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M017_Rocky St - Maryborough City 66 kV | Time | 10:30:00 | 21:00:00 | 05:30:00 | 10:30:00 | 21:00:00 | 05:30:00 | 10:30:00 | 21:00:00 | 05:30:00 | 10:30:00 | 21:00:00 | 05:30:00 | 10:30:00 | 21:00:00 | 05:30:00
WB | M017_Rocky St - Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0245 | 1.0124 | 1.0276 | 1.0241 | 1.0109 | 1.0267 | 1.0261 | 1.0098 | 1.0263 | 1.0262 | 1.0095 | 1.0263 | 1.0259 | 1.0198 | 1.025
WB | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 28.37% | 28.64% | 21.5% | 28.55% | 28.46% | 21.61% | 28.55% | 28.77% | 21.33% | 28.47% | 28.71% | 21.28% | 29.05% | 28.87% | 21.69%
WB | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1
WB | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 155.4537 | 165.835 | 112.0341 | 156.4543 | 164.7587 | 112.5854 | 156.4291 | 166.5935 | 111.1305 | 156.0012 | 166.2156 | 110.8641 | 159.2063 | 167.1752 | 113.0202
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 18.129 | 19.1533 | 13.0792 | 18.1969 | 19.2289 | 13.1262 | 18.1736 | 19.2165 | 13.1156 | 18.1222 | 19.1675 | 13.0836 | 18.4347 | 19.4921 | 13.3077
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 18.1247 | 19.1277 | 13.059 | 18.1873 | 19.1973 | 13.1123 | 18.1634 | 19.1802 | 13.098 | 18.1122 | 19.1315 | 13.0658 | 18.4266 | 19.4643 | 13.2909
WB | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.99976 | 0.99866 | 0.99845 | 0.99947 | 0.99835 | 0.99893 | 0.99944 | 0.99811 | 0.99866 | 0.99945 | 0.99812 | 0.99864 | 0.99956 | 0.99858 | 0.99873
WB | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M018_Maryborough-Maryborough City 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M018_Maryborough-Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0201 | 1.0103 | 1.0196 | 1.0174 | 1.0209 | 1.0182 | 1.0163 | 1.009 | 1.0307 | 1.0162 | 1.0087 | 1.0307 | 1.0129 | 1.0199 | 1.0283
WB | M020_Maryborough-Torquay 66 kV | % of Rated A | [6 empty] | 57.05% | 66.1% | 49.1% | 57.34% | 66.45% | 49.34% | 59.14% | 67.5% | 50.82%
WB | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1
WB | M020_Maryborough-Torquay 66 kV | Loading (A) | 340.4466 | 436.7652 | 269.7505 | 343.506 | 434.5208 | 271.7392 | 346.8827 | 444.2043 | 270.5573 | 348.6327 | 446.5353 | 271.8896 | 359.5468 | 453.6311 | 279.9988
WB | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 38.8199 | 48.714 | 31.1703 | 39.0506 | 48.9974 | 31.3547 | 39.3701 | 49.4139 | 31.6071 | 39.5544 | 49.6479 | 31.7584 | 40.6043 | 50.9627 | 32.6113
WB | M020_Maryborough-Torquay 66 kV | Loading (MW) | 38.8199 | 48.679 | 31.1685 | 39.0504 | 48.9607 | 31.3531 | 39.3694 | 49.367 | 31.6055 | 39.5535 | 49.5984 | 31.7572 | 40.602 | 50.9061 | 32.6112
WB | M020_Maryborough-Torquay 66 kV | Power Factor | 1 | 0.99928 | 0.99994 | 0.99999 | 0.99925 | 0.99995 | 0.99998 | 0.99905 | 0.99995 | 0.99998 | 0.999 | 0.99996 | 0.99994 | 0.99889 | 1
WB | M020_Maryborough-Torquay 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | M020_Maryborough-Torquay 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M020_Maryborough-Torquay 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99743 | 0.97561 | 1.0108 | 0.99442 | 0.98636 | 1.0093 | 0.9928 | 0.97305 | 1.0219 | 0.99244 | 0.97256 | 1.0218 | 0.98786 | 0.9827 | 1.0188
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | % of Rated A | 44.21% | 50.8% | 38.28% | 44.61% | 50.54% | 38.56% | 45.05% | 51.66% | 38.4% | 45.27% | 51.92% | 38.58% | 46.68% | 52.74% | 39.72%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Limiting Line Name | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 43935_1
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (A) | 267.4934 | 339.3189 | 209.3866 | 269.9012 | 337.594 | 210.9409 | 272.5384 | 345.0813 | 210.0234 | 273.8722 | 346.838 | 211.0258 | 282.3926 | 352.3035 | 217.268
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MVA) | 30.5065 | 37.8521 | 24.0112 | 30.6872 | 38.0738 | 24.1523 | 30.9349 | 38.3894 | 24.3492 | 31.0748 | 38.5648 | 24.4602 | 31.892 | 39.5789 | 25.099
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MW) | 30.472 | 37.7237 | 24.0099 | 30.6494 | 37.9411 | 24.1508 | 30.8929 | 38.2388 | 24.3474 | 31.0308 | 38.4096 | 24.4581 | 31.8402 | 39.4097 | 25.0944
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Power Factor | 0.99887 | 0.99661 | 0.99994 | 0.99877 | 0.99652 | 0.99994 | 0.99864 | 0.99608 | 0.99993 | 0.99859 | 0.99598 | 0.99991 | 0.99838 | 0.99573 | 0.99982
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99755 | 0.97571 | 1.0031 | 0.99451 | 0.98644 | 1.0015 | 0.99283 | 0.97303 | 1.0141 | 0.99246 | 0.97253 | 1.0139 | 0.98783 | 0.98261 | 1.0105
WB | M022_Howard - ISIS 66 kV | % of Rated A | 14.69% | 20.47% | 13.48% | 16.45% | 22.98% | 15.05% | 16.58% | 23.06% | 15.16% | 16.57% | 23.05% | 15.16% | 16.95% | 23.57% | 15.5%
WB | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB | M022_Howard - ISIS 66 kV | Loading (A) | 80.5196 | 118.5122 | 70.2052 | 90.151 | 133.07 | 78.4153 | 90.847 | 133.5057 | 79.0044 | 90.8264 | 133.4451 | 78.9905 | 92.8682 | 136.484 | 80.7679
WB | M022_Howard - ISIS 66 kV | Loading (MVA) | 9.35 | 13.7421 | 8.1814 | 10.4397 | 15.3654 | 9.125 | 10.513 | 15.4846 | 9.1885 | 10.5129 | 15.4839 | 9.1885 | 10.7263 | 15.8159 | 9.3794
WB | M022_Howard - ISIS 66 kV | Loading (MW) | 9.2136 | 13.4198 | 8.0791 | 10.2628 | 14.9554 | 8.9967 | 10.333 | 15.0587 | 9.0581 | 10.3329 | 15.0585 | 9.058 | 10.5423 | 15.3672 | 9.2421
WB | M022_Howard - ISIS 66 kV | Power Factor | 0.98349 | 0.97655 | 0.98486 | 0.98172 | 0.97331 | 0.98388 | 0.98158 | 0.9725 | 0.98377 | 0.98159 | 0.97253 | 0.98377 | 0.98171 | 0.97163 | 0.98344
WB | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M022_Howard - ISIS 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M022_Howard - ISIS 66 kV | Min Voltage at Constrained Conductor (pu) | 1.013 | 1.0069 | 1.018 | 1.009 | 1.0009 | 1.0154 | 1.0082 | 1.0054 | 1.0148 | 1.0085 | 1.0058 | 1.015 | 1.006 | 1.0041 | 1.013
WB | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 31.64% | 35.17% | 26.12% | 31.84% | 34.92% | 26.25% | 32.01% | 35.53% | 26.02% | 32.02% | 35.55% | 26.02% | 32.91% | 35.97% | 26.65%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 191.4095 | 234.9521 | 142.8854 | 192.6599 | 233.2409 | 143.5801 | 193.6737 | 237.3499 | 142.3167 | 193.7399 | 237.468 | 142.3421 | 199.0885 | 240.2901 | 145.7881
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 21.8274 | 26.2062 | 16.3842 | 21.903 | 26.3015 | 16.4385 | 21.9811 | 26.4011 | 16.4985 | 21.9805 | 26.4004 | 16.4979 | 22.4818 | 26.9913 | 16.8404
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 21.4891 | 25.9887 | 15.8296 | 21.5736 | 26.0871 | 15.8914 | 21.6578 | 26.1926 | 15.9517 | 21.6579 | 26.1928 | 15.9517 | 22.1611 | 26.7986 | 16.3217
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.98449 | 0.99168 | 0.96614 | 0.98495 | 0.99183 | 0.96671 | 0.98527 | 0.99209 | 0.96685 | 0.98531 | 0.99212 | 0.96688 | 0.98572 | 0.99285 | 0.96919
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99753 | 0.97568 | 1.0031 | 0.99449 | 0.98641 | 1.0015 | 0.99281 | 0.973 | 1.0141 | 0.99244 | 0.97249 | 1.0139 | 0.98781 | 0.98258 | 1.0105
WB | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 59.46% | 45.33% | 29.81% | 59.75% | 45.61% | 29.66% | 58.78% | 44.91% | 29.27% | 58.53% | 44.71% | 29.1% | 58.03% | 44.32% | 29.43%
WB | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 78.4833 | 80.2315 | 50.6748 | 78.8648 | 80.7225 | 50.4265 | 77.587 | 79.4823 | 49.7631 | 77.2642 | 79.1416 | 49.4734 | 76.5962 | 78.4414 | 50.0328
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 9.0008 | 9.2267 | 5.7946 | 9.0132 | 9.2503 | 5.8445 | 8.869 | 9.0994 | 5.7647 | 8.8361 | 9.067 | 5.7325 | 8.8676 | 8.969 | 5.789
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 8.8785 | 9.1256 | 5.3559 | 8.8882 | 9.1361 | 5.3585 | 8.7052 | 8.9494 | 5.2505 | 8.6897 | 8.9335 | 5.2412 | 8.6977 | 8.8119 | 5.2516
WB | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.98641 | 0.98905 | 0.9243 | 0.98613 | 0.98766 | 0.91684 | 0.98153 | 0.98351 | 0.9108 | 0.98344 | 0.98528 | 0.91429 | 0.98084 | 0.98249 | 0.90716
WB | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | M024_Gayndah - Mundubbera 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:00:00 | 22:00:00
WB | M024_Gayndah - Mundubbera 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98269 | 0.98455 | 0.9911 | 0.97917 | 0.98112 | 1.0051 | 0.98041 | 0.98116 | 1.005 | 0.98065 | 0.98169 | 1.0051 | 0.99352 | 0.98032 | 1.0039
WB | M025_Eidsvold 66 kV | % of Rated A | 15.5% | 12.56% | 7.769% | 15.56% | 12.61% | 7.659% | 15.54% | 12.61% | 7.659% | 15.53% | 12.6% | 7.658% | 15.32% | 12.41% | 7.666%
WB | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1
WB | M025_Eidsvold 66 kV | Loading (A) | 16.5877 | 17.3394 | 10.2554 | 16.6506 | 17.4026 | 10.1096 | 16.6242 | 17.3976 | 10.1097 | 16.6208 | 17.3887 | 10.1088 | 16.3926 | 17.1262 | 10.1196
WB | M025_Eidsvold 66 kV | Loading (MVA) | 1.8402 | 1.9261 | 1.1541 | 1.8404 | 1.9264 | 1.1592 | 1.8403 | 1.9263 | 1.1592 | 1.8403 | 1.9263 | 1.1592 | 1.8396 | 1.9019 | 1.1591
WB | M025_Eidsvold 66 kV | Loading (MW) | 1.8245 | 1.9092 | 1.1465 | 1.8247 | 1.9094 | 1.1502 | 1.8246 | 1.9094 | 1.1502 | 1.8246 | 1.9093 | 1.1502 | 1.8242 | 1.8854 | 1.1502
WB | M025_Eidsvold 66 kV | Power Factor | 0.98975 | 0.98941 | 0.99232 | 0.98969 | 0.98935 | 0.99224 | 0.98972 | 0.98935 | 0.99224 | 0.98972 | 0.98936 | 0.99223 | 0.98993 | 0.98951 | 0.99231
WB | M025_Eidsvold 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | M025_Eidsvold 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M025_Eidsvold 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97046 | 0.97174 | 0.98447 | 0.9669 | 0.96832 | 1.003 | 0.96839 | 0.96859 | 1.003 | 0.96858 | 0.96907 | 1.0031 | 0.98168 | 0.97146 | 1.0019
WB | M026_ISIS - Bundaberg 66 kV | % of Rated A | 18.91% | 30.38% | 19.03% | 18.95% | 30.48% | 19.05% | 18.94% | 30.27% | 19.03% | 18.93% | 30.26% | 19.03% | 19.52% | 31.17% | 19.61%
WB | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1
WB | M026_ISIS - Bundaberg 66 kV | Loading (A) | 18.9075 | 30.378 | 19.0298 | 18.9523 | 30.4759 | 19.0539 | 18.9352 | 30.2671 | 19.0339 | 18.9311 | 30.2607 | 19.0307 | 19.5191 | 31.1727 | 19.6117
WB | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 2.2042 | 3.528 | 2.2257 | 2.2043 | 3.5282 | 2.2257 | 2.2008 | 3.5198 | 2.2222 | 2.2008 | 3.5198 | 2.2222 | 2.264 | 3.6212 | 2.286
WB | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 2.1913 | 3.4992 | 2.2127 | 2.1913 | 3.4992 | 2.2127 | 2.1877 | 3.49 | 2.209 | 2.1877 | 3.49 | 2.209 | 2.2502 | 3.5897 | 2.2721
WB | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.99395 | 0.9917 | 0.99394 | 0.99393 | 0.99166 | 0.99393 | 0.99382 | 0.99139 | 0.99382 | 0.99383 | 0.99139 | 0.99382 | 0.9937 | 0.99116 | 0.9937
WB | M026_ISIS - Bundaberg 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
WB | M026_ISIS - Bundaberg 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M026_ISIS - Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0198 | 1.0159 | 1.0231 | 1.0174 | 1.0127 | 1.0218 | 1.0167 | 1.0173 | 1.0213 | 1.017 | 1.0175 | 1.0215 | 1.0146 | 1.0162 | 1.0197
WB | M026b_FORMER_ISIS - Bundaberg 66kV | % of Rated A | 0.2748% | 0.2223% | 0.2748% | 0.2747% | 0.2224% | 0.2747% | 0.2748% | 0.2228% | 0.2745% | 0.2738% | 0.2228% | 0.2746% | 0.2747% | 0.2226% | 0.2747%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Limiting Line Name | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (A) | 1.0689 | 1.067 | 1.069 | 1.0687 | 1.0676 | 1.0685 | 1.0691 | 1.0692 | 1.0678 | 1.0651 | 1.0694 | 1.068 | 1.0687 | 1.0685 | 1.0684
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MVA) | 0.12332 | 0.1229 | 0.12336 | 0.12329 | 0.12304 | 0.12325 | 0.12338 | 0.12341 | 0.12309 | 0.12246 | 0.12345 | 0.12313 | 0.12328 | 0.12325 | 0.12322
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MW) | 1.935e-06 | 1.9284e-06 | 1.9356e-06 | 1.9345e-06 | 1.9306e-06 | 1.9338e-06 | 1.9358e-06 | 1.9364e-06 | 1.9313e-06 | 1.9214e-06 | 1.937e-06 | 1.932e-06 | 1.9344e-06 | 1.9338e-06 | 1.9334e-06
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Power Factor | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Rating (A) | 389 | 480 | 389 | 389 | 480 | 389 | 389 | 480 | 389 | 389 | 480 | 389 | 389 | 480 | 389
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Time | 08:30:00 | 20:30:00 | 23:00:00 | 08:30:00 | 17:30:00 | 00:00:00 | 08:30:00 | 21:30:00 | 00:00:00 | 08:00:00 | 17:00:00 | 00:00:00 | 06:30:00 | 18:30:00 | 00:30:00
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Min Voltage at Constrained Conductor (pu) | 1.0093 | 1.0076 | 1.0095 | 1.0092 | 1.0081 | 1.009 | 1.0095 | 1.0097 | 1.0083 | 1.0058 | 1.0098 | 1.0085 | 1.0091 | 1.009 | 1.0089
WB | M027_ISIS - Childers 66 kV | % of Rated A | 63.55% | 65.74% | 55.62% | 63.61% | 65.06% | 55.67% | 63.65% | 65.09% | 55.7% | 63.33% | 64.79% | 55.38% | 64.36% | 65.99% | 56.25%
WB | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1
WB | M027_ISIS - Childers 66 kV | Loading (A) | 163.959 | 174.2035 | 130.1424 | 164.116 | 172.4217 | 130.2783 | 164.2243 | 172.4999 | 130.3264 | 163.3852 | 171.6977 | 129.5814 | 166.0606 | 174.8857 | 131.6263
WB | M027_ISIS - Childers 66 kV | Loading (MVA) | 18.8648 | 19.9389 | 15.1376 | 18.8521 | 19.9348 | 15.139 | 18.8533 | 19.9198 | 15.1395 | 18.7633 | 19.8324 | 15.056 | 19.0326 | 20.1311 | 15.2783
WB | M027_ISIS - Childers 66 kV | Loading (MW) | 18.4946 | 19.5008 | 14.925 | 18.4944 | 19.4978 | 14.9252 | 18.4946 | 19.4973 | 14.9253 | 18.4117 | 19.4022 | 14.8476 | 18.6613 | 19.6904 | 15.056
WB | M027_ISIS - Childers 66 kV | Power Factor | 0.98037 | 0.97803 | 0.98596 | 0.98102 | 0.97808 | 0.98588 | 0.98097 | 0.97879 | 0.98585 | 0.98126 | 0.97831 | 0.98615 | 0.98049 | 0.97811 | 0.98545
WB | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | M027_ISIS - Childers 66 kV | Time | 16:00:00 | 19:00:00 | 00:30:00 | 16:00:00 | 19:00:00 | 00:30:00 | 16:00:00 | 19:00:00 | 00:30:00 | 16:00:00 | 19:00:00 | 00:30:00 | 16:00:00 | 19:00:00 | 00:30:00
WB | M027_ISIS - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0047 | 0.99931 | 1.0161 | 1.0031 | 1.0095 | 1.0152 | 1.0025 | 1.0083 | 1.0148 | 1.0028 | 1.0085 | 1.015 | 1.0008 | 1.005 | 1.014
WB | M028_GAYN TEE DEGI FDR 66kV | % of Rated A | 20.82% | 20.56% | 15.73% | 21.54% | 21.03% | 16.26% | 21.96% | 21.52% | 16.63% | 21.85% | 21.4% | 16.57% | 21.98% | 21.41% | 16.66%
WB | M028_GAYN TEE DEGI FDR 66kV | Limiting Line Name | TR_LINE 160969_1 | TR_LINE 160969_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 160969_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 160969_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 160969_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 160969_1 | TR_LINE 12103276_2(New M028)
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (A) | 114.1076 | 119.0408 | 81.9459 | 118.0407 | 121.7495 | 84.6926 | 120.3214 | 124.5933 | 86.6173 | 119.7124 | 123.9112 | 86.3204 | 120.4556 | 123.9481 | 86.8003
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MVA) | 13.0079 | 13.4289 | 9.6255 | 13.4072 | 13.8687 | 9.9358 | 13.6524 | 14.1618 | 10.1564 | 13.5912 | 14.0965 | 10.1232 | 13.6454 | 14.1465 | 10.1632
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MW) | 12.9489 | 13.3522 | 9.6186 | 13.3414 | 13.7913 | 9.9304 | 13.5916 | 14.0877 | 10.1525 | 13.535 | 14.0297 | 10.1185 | 13.5925 | 14.0839 | 10.1574
WB | M028_GAYN TEE DEGI FDR 66kV | Power Factor | 0.99546 | 0.99429 | 0.99929 | 0.99509 | 0.99442 | 0.99945 | 0.99554 | 0.99477 | 0.99962 | 0.99587 | 0.99527 | 0.99954 | 0.99612 | 0.99558 | 0.99943
WB | M028_GAYN TEE DEGI FDR 66kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M028_GAYN TEE DEGI FDR 66kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M028_GAYN TEE DEGI FDR 66kV | Min Voltage at Constrained Conductor (pu) | 0.9972 | 0.98681 | 1.0168 | 0.99357 | 0.99645 | 1.0151 | 0.99256 | 0.99429 | 1.0141 | 0.99313 | 0.99515 | 1.0144 | 0.99094 | 0.99838 | 1.0129
WB | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 16.16% | 8.866% | 10.41% | 16.11% | 8.775% | 10.41% | 16.12% | 8.797% | 10.42% | 16.11% | 8.792% | 10.42% | 16.15% | 8.861% | 10.43%
WB | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 31.1919 | 24.2941 | 27.7849 | 31.0959 | 24.0447 | 27.8046 | 31.107 | 24.1036 | 27.8182 | 31.0899 | 24.0902 | 27.815 | 31.1648 | 24.2805 | 27.8466
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 3.5368 | 2.7617 | 3.1641 | 3.5583 | 2.7619 | 3.1641 | 3.5568 | 2.762 | 3.1642 | 3.5567 | 2.762 | 3.1642 | 3.557 | 2.7616 | 3.1643
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 3.1104 | 2.4366 | 2.7871 | 3.1285 | 2.4366 | 2.7871 | 3.1284 | 2.4366 | 2.7872 | 3.1284 | 2.4366 | 2.7871 | 3.1284 | 2.4366 | 2.7872
WB | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.87896 | 0.88193 | 0.88047 | 0.87877 | 0.88187 | 0.88045 | 0.8791 | 0.88182 | 0.88044 | 0.87912 | 0.88184 | 0.88044 | 0.87905 | 0.88194 | 0.88041
WB | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267
WB | M029_Bundaberg - Farnsfield 66 kV | Time | 16:00:00 | 17:30:00 | 05:00:00 | 15:30:00 | 17:30:00 | 05:00:00 | 15:30:00 | 17:30:00 | 05:00:00 | 15:30:00 | 17:30:00 | 05:00:00 | 15:30:00 | 17:30:00 | 05:00:00
WB | M029_Bundaberg - Farnsfield 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9919 | 0.99441 | 0.99616 | 1.001 | 1.0048 | 0.99548 | 1.0002 | 1.0024 | 0.99501 | 1.0008 | 1.0029 | 0.99512 | 0.99843 | 0.99496 | 0.99402
WB | M030_Farnsfield - Childers 66 kV | % of Rated A | 53.61% | 49.62% | 42.26% | 53.65% | 49.12% | 42.26% | 53.68% | 49.11% | 42.06% | 53.09% | 48.64% | 41.82% | 54.36% | 49.83% | 42.57%
WB | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB | M030_Farnsfield - Childers 66 kV | Loading (A) | 70.7657 | 82.8642 | 67.1894 | 70.8126 | 82.0303 | 67.1888 | 70.8601 | 82.0218 | 66.8751 | 70.0778 | 81.228 | 66.491 | 71.7511 | 83.2178 | 67.6819
WB | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 8.0945 | 9.4169 | 7.7687 | 8.0874 | 9.4176 | 7.7622 | 8.0878 | 9.406 | 7.7658 | 8.002 | 9.3174 | 7.6807 | 8.1749 | 9.5111 | 7.8487
WB | M030_Farnsfield - Childers 66 kV | Loading (MW) | 8.0479 | 9.3031 | 7.7351 | 8.0476 | 9.302 | 7.7347 | 8.0476 | 9.3014 | 7.7346 | 7.9656 | 9.2072 | 7.656 | 8.1299 | 9.397 | 7.8135
WB | M030_Farnsfield - Childers 66 kV | Power Factor | 0.99401 | 0.98774 | 0.99544 | 0.99487 | 0.98752 | 0.99625 | 0.99483 | 0.98869 | 0.99576 | 0.99525 | 0.98797 | 0.99658 | 0.99429 | 0.98781 | 0.99529
WB | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M030_Farnsfield - Childers 66 kV | Time | 16:00:00 | 19:00:00 | 23:30:00 | 16:00:00 | 19:00:00 | 23:30:00 | 16:00:00 | 19:00:00 | 23:30:00 | 16:00:00 | 19:00:00 | 23:30:00 | 16:00:00 | 19:00:00 | 23:30:00
WB | M030_Farnsfield - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99816 | 0.99115 | 1.0092 | 0.99659 | 1.0014 | 1.0083 | 0.99598 | 1.0002 | 1.0135 | 0.99644 | 1.0005 | 1.0082 | 0.99417 | 0.99682 | 1.0121
WB | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 70.41% | 62.32% | 46.2% | 70.55% | 62.49% | 46.25% | 69.68% | 62.92% | 46.3% | 69.67% | 62.88% | 46.29% | 71.58% | 63.73% | 47.45%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 7401_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 7401_1 | TR_LINE 138990_1
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 92.9379 | 110.3072 | 78.5452 | 93.1279 | 110.5992 | 78.6293 | 91.9797 | 111.3668 | 78.7081 | 91.9654 | 111.2927 | 78.6881 | 94.4833 | 112.7983 | 80.6725
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 10.5538 | 12.5807 | 8.9865 | 10.5553 | 12.5765 | 8.9868 | 10.5485 | 12.5866 | 8.9871 | 10.5484 | 12.5856 | 8.9871 | 10.8088 | 12.8976 | 9.1911
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 10.5518 | 12.5312 | 8.9849 | 10.5529 | 12.5325 | 8.9853 | 10.5465 | 12.5378 | 8.9858 | 10.5464 | 12.5373 | 8.9857 | 10.8059 | 12.8391 | 9.1909
WB | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.99978 | 0.99607 | 0.99981 | 0.99975 | 0.99651 | 0.99983 | 0.99977 | 0.99612 | 0.99985 | 0.99977 | 0.99616 | 0.99985 | 0.9997 | 0.99546 | 0.99998
WB | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | M032_Bundaberg-South Kolan No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M032_Bundaberg-South Kolan No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97982 | 0.98134 | 1.0008 | 0.9779 | 0.97833 | 0.9998 | 0.98981 | 0.97212 | 0.99884 | 0.98996 | 0.97271 | 0.99909 | 0.98695 | 0.98345 | 0.99663
WB | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 12.45% | 14.4% | 11.36% | 12.47% | 14.44% | 11.37% | 12.32% | 14.54% | 11.38% | 12.32% | 14.53% | 11.38% | 12.68% | 14.76% | 11.71%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 68.2201 | 83.3935 | 59.185 | 68.3612 | 83.6157 | 59.2516 | 67.5288 | 84.1773 | 59.3101 | 67.5182 | 84.1221 | 59.2942 | 69.495 | 85.4527 | 60.9874
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 7.7614 | 9.5419 | 6.7797 | 7.7629 | 9.5387 | 6.7803 | 7.7584 | 9.5452 | 6.7805 | 7.7582 | 9.5445 | 6.7804 | 7.9656 | 9.804 | 6.957
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 7.7329 | 9.4485 | 6.7673 | 7.7336 | 9.4492 | 6.7676 | 7.73 | 9.452 | 6.7677 | 7.73 | 9.4517 | 6.7677 | 7.9344 | 9.7008 | 6.94
WB | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.99553 | 0.98949 | 0.99738 | 0.99543 | 0.98993 | 0.99734 | 0.99552 | 0.98957 | 0.99732 | 0.99553 | 0.98961 | 0.99733 | 0.99529 | 0.98879 | 0.99672
WB | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M035_Bundaberg-South Kolan No 2 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M035_Bundaberg-South Kolan No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9938 | 0.99892 | 1.0009 | 0.99194 | 0.99588 | 0.99989 | 1.0037 | 0.98986 | 0.99893 | 1.0038 | 0.99043 | 0.99918 | 1.0012 | 1.0015 | 0.99673
WB | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 61.1% | 67.35% | 57.29% | 61.52% | 67.95% | 57.67% | 61.23% | 68.93% | 58.14% | 61.22% | 68.95% | 58.16% | 62.85% | 69.91% | 59.71%
WB | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 268.2106 | 323.2602 | 222.8422 | 270.0646 | 326.171 | 224.3284 | 268.8163 | 330.8694 | 226.169 | 268.7471 | 330.9549 | 226.2616 | 275.9031 | 335.5484 | 232.2544
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 30.6224 | 37.1625 | 25.6018 | 30.7773 | 37.3832 | 25.7461 | 30.9929 | 37.6969 | 25.9327 | 30.9893 | 37.7281 | 25.9497 | 31.7384 | 38.6841 | 26.5771
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 30.3502 | 37.0599 | 25.1047 | 30.5028 | 37.2903 | 25.2425 | 30.7151 | 37.6117 | 25.4424 | 30.7182 | 37.6427 | 25.4599 | 31.4853 | 38.6079 | 26.1317
WB | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.98624 | 0.99348 | 0.97524 | 0.98615 | 0.99386 | 0.97501 | 0.98621 | 0.99411 | 0.97568 | 0.98648 | 0.99411 | 0.97571 | 0.98726 | 0.99458 | 0.97791
WB | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB | M036_Bundaberg-South Bundaberg 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M036_Bundaberg-South Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98308 | 0.98429 | 0.99389 | 0.98115 | 0.98088 | 0.99281 | 0.99286 | 0.9745 | 0.99166 | 0.99295 | 0.97506 | 0.9919 | 0.98991 | 0.98582 | 0.98899
WB | M037_South - East Bundaberg 66 kV | % of Rated A | 17.52% | 10.57% | 10.38% | 17.51% | 10.55% | 10.23% | 17.69% | 10.77% | 10.28% | 17.39% | 10.78% | 10.29% | 17.45% | 10.72% | 10.42%
WB | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB | M037_South - East Bundaberg 66 kV | Loading (A) | 39.5929 | 32.8792 | 26.7822 | 39.5669 | 32.8167 | 26.4009 | 39.9852 | 33.4938 | 26.5275 | 39.301 | 33.5271 | 26.557 | 39.4396 | 33.3484 | 26.8857
WB | M037_South - East Bundaberg 66 kV | Loading (MVA) | 4.5438 | 3.6764 | 3.0446 | 4.5381 | 3.7085 | 2.998 | 4.5839 | 3.7384 | 3.0089 | 4.5076 | 3.7397 | 3.013 | 4.5152 | 3.7261 | 3.0414
WB | M037_South - East Bundaberg 66 kV | Loading (MW) | 3.999 | 1.2039 | 0.38087 | 3.9883 | 1.2024 | 0.38348 | 4.0396 | 0.47009 | 0.44605 | 3.9439 | 0.61563 | 0.3335 | 3.9498 | 0.98994 | 0.23368
WB | M037_South - East Bundaberg 66 kV | Power Factor | 0.88009 | 0.32748 | 0.12509 | 0.87885 | 0.32424 | 0.12791 | 0.88125 | 0.12575 | 0.14824 | 0.87494 | 0.16462 | 0.11069 | 0.87478 | 0.26568 | 0.076833
WB | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | M037_South - East Bundaberg 66 kV | Time | 14:30:00 | 17:30:00 | 22:00:00 | 14:30:00 | 17:30:00 | 22:00:00 | 14:30:00 | 18:30:00 | 22:00:00 | 14:30:00 | 18:00:00 | 22:00:00 | 14:30:00 | 17:30:00 | 22:00:00
WB | M037_South - East Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0037 | 0.97814 | 0.99446 | 1.0031 | 0.98855 | 0.99337 | 1.0027 | 0.97639 | 0.99222 | 1.0031 | 0.97575 | 0.99247 | 1.0013 | 0.9774 | 0.98957
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 43.84% | 42.94% | 35.88% | 44.34% | 43.58% | 36.29% | 44.39% | 44.51% | 36.82% | 44.14% | 44.28% | 36.65% | 45.04% | 44.6% | 37.39%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 353.3713 | 387.7831 | 267.2907 | 357.3695 | 393.5323 | 270.3895 | 357.7478 | 401.9175 | 274.3383 | 355.7525 | 399.8198 | 273.0739 | 363.0261 | 402.7001 | 278.5924
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 40.2366 | 44.4355 | 30.7084 | 40.6133 | 44.9502 | 31.0325 | 41.1312 | 45.6274 | 31.4558 | 40.9081 | 45.4174 | 31.3185 | 41.6418 | 46.2611 | 31.8796
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 40.2352 | 44.4138 | 30.5855 | 40.6102 | 44.9168 | 30.9213 | 41.1267 | 45.58 | 31.3619 | 40.9035 | 45.3752 | 31.2194 | 41.6367 | 46.2139 | 31.8003
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.99997 | 0.99951 | 0.99598 | 0.99992 | 0.99926 | 0.99639 | 0.99989 | 0.99896 | 0.99699 | 0.99989 | 0.99907 | 0.99682 | 0.99988 | 0.99898 | 0.99749
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99273 | 0.99842 | 1.005 | 0.99072 | 0.99505 | 1.0039 | 1.0023 | 0.98876 | 1.003 | 1.0025 | 0.98943 | 1.0032 | 0.99991 | 1.0006 | 1.001
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 42.21% | 41.35% | 34.54% | 42.69% | 41.96% | 34.94% | 42.73% | 42.85% | 35.45% | 42.5% | 42.63% | 35.29% | 43.37% | 42.94% | 36%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 7295_1 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_1 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_2 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_2 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_2 | TR_LINE 7295_2 | TR_LINE 169764_1
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 340.2301 | 373.3627 | 257.3537 | 344.0795 | 378.8984 | 260.3371 | 344.4438 | 386.9719 | 264.1388 | 342.5228 | 384.9522 | 262.9215 | 349.5259 | 387.7255 | 268.2345
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 38.7461 | 42.6266 | 29.5667 | 39.1091 | 43.1133 | 29.8788 | 39.4759 | 43.7541 | 30.2863 | 39.2624 | 43.5552 | 30.1541 | 39.9635 | 44.3638 | 30.6944
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 38.7447 | 42.6195 | 29.4477 | 39.1059 | 43.0995 | 29.771 | 39.4757 | 43.7318 | 30.1953 | 39.2622 | 43.5362 | 30.0581 | 39.9632 | 44.3415 | 30.6174
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.99996 | 0.99983 | 0.99538 | 0.99992 | 0.99968 | 0.99582 | 1 | 0.99949 | 0.99646 | 0.99999 | 0.99956 | 0.99627 | 0.99999 | 0.9995 | 0.99699
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99298 | 0.99842 | 1.0039 | 0.99098 | 0.99505 | 1.0028 | 1.0023 | 0.98876 | 1.0018 | 1.0025 | 0.98943 | 1.0021 | 0.99991 | 1.0006 | 0.99972
WB | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 58.47% | 51.25% | 43.62% | 63.18% | 55.57% | 46.84% | 67.07% | 60.15% | 50.12% | 66.7% | 59.76% | 49.86% | 67.92% | 60.02% | 50.75%
WB | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 132.134 | 159.3988 | 112.5285 | 142.7898 | 172.8234 | 120.8525 | 151.5709 | 187.0683 | 129.3093 | 150.7418 | 185.8394 | 128.6283 | 153.4982 | 186.6499 | 130.9423
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 14.7005 | 17.7733 | 12.6746 | 15.8316 | 19.1686 | 13.5828 | 16.9859 | 20.573 | 14.5014 | 16.8977 | 20.4562 | 14.4307 | 17.1558 | 20.7807 | 14.6489
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 13.3924 | 16.2992 | 11.4334 | 14.4826 | 17.6091 | 12.3242 | 15.5707 | 18.9222 | 13.2163 | 15.4866 | 18.8231 | 13.1476 | 15.7326 | 19.1182 | 13.3587
WB | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.91102 | 0.91706 | 0.90197 | 0.9148 | 0.91864 | 0.90734 | 0.91668 | 0.91976 | 0.91138 | 0.91649 | 0.92016 | 0.91108 | 0.91705 | 0.91999 | 0.91193
WB | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | M041_West Bundaberg-Meadowvale 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | M041_West Bundaberg-Meadowvale 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97034 | 0.97163 | 0.98314 | 0.96665 | 0.96606 | 0.9807 | 0.97681 | 0.95741 | 0.97825 | 0.97712 | 0.95831 | 0.97866 | 0.97412 | 0.96933 | 0.9758
WB | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 30.84% | 29.79% | 26.97% | 30.96% | 29.97% | 27.03% | 30.63% | 30.24% | 27.1% | 30.62% | 30.23% | 27.09% | 31.39% | 30.53% | 27.76%
WB | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 34.2275 | 43.4935 | 32.0927 | 34.3638 | 43.7498 | 32.1663 | 34.0003 | 44.1457 | 32.2503 | 33.9893 | 44.1338 | 32.2363 | 34.8399 | 44.5765 | 33.0365
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 3.756 | 4.785 | 3.5711 | 3.7563 | 4.7865 | 3.5702 | 3.7565 | 4.7872 | 3.5704 | 3.7565 | 4.7871 | 3.5704 | 3.8375 | 4.8905 | 3.6473
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 3.5496 | 4.5059 | 3.3741 | 3.5498 | 4.5064 | 3.3739 | 3.5494 | 4.507 | 3.3741 | 3.5494 | 4.507 | 3.374 | 3.6256 | 4.6031 | 3.4465
WB | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.93919 | 0.9369 | 0.93941 | 0.93912 | 0.93677 | 0.93958 | 0.93908 | 0.93687 | 0.93953 | 0.93909 | 0.93687 | 0.93954 | 0.93884 | 0.9366 | 0.93932
WB | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119
WB | M042_Meadowvale-Gooburrum 66 kV | Time | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00 | 16:30:00 | 18:30:00 | 22:00:00
WB | M042_Meadowvale-Gooburrum 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95995 | 0.95966 | 0.9734 | 0.95621 | 0.95419 | 0.97094 | 0.96649 | 0.94552 | 0.96846 | 0.96679 | 0.94577 | 0.96887 | 0.96354 | 0.95663 | 0.96577
WB | M046_Tarong-Caboonbah 66 kV | % of Rated A | 18.89% | 11.16% | 6.515% | 18.88% | 11.16% | 6.515% | 18.88% | 11.16% | 6.515% | 18.88% | 11.16% | 6.514% | 18.88% | 11.16% | 6.515%
WB | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1
WB | M046_Tarong-Caboonbah 66 kV | Loading (A) | 47.0241 | 42.6366 | 24.1053 | 47.0218 | 42.635 | 24.1047 | 47.0207 | 42.6368 | 24.1044 | 47.0179 | 42.6322 | 24.1033 | 47.0234 | 42.6445 | 24.1066
WB | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 5.5438 | 5.0606 | 2.8657 | 5.5438 | 5.0606 | 2.8657 | 5.5438 | 5.0606 | 2.8657 | 5.5437 | 5.0605 | 2.8657 | 5.5438 | 5.0605 | 2.8657
WB | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 5.0508 | 4.6463 | 2.7379 | 5.0508 | 4.6463 | 2.7379 | 5.0508 | 4.6463 | 2.7379 | 5.0508 | 4.6463 | 2.7379 | 5.0508 | 4.6462 | 2.7379
WB | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.91106 | 0.91813 | 0.95539 | 0.91106 | 0.91813 | 0.95539 | 0.91107 | 0.91813 | 0.95539 | 0.91107 | 0.91814 | 0.9554 | 0.91106 | 0.91814 | 0.95538
WB | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | M046_Tarong-Caboonbah 66 kV | Time | 12:30:00 | 17:30:00 | 05:30:00 | 12:30:00 | 17:30:00 | 05:30:00 | 12:30:00 | 17:30:00 | 05:30:00 | 12:30:00 | 17:30:00 | 05:30:00 | 12:30:00 | 17:30:00 | 05:30:00
WB | M046_Tarong-Caboonbah 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0313 | 1.0383 | 1.0399 | 1.0313 | 1.0383 | 1.04 | 1.0314 | 1.0383 | 1.04 | 1.0314 | 1.0384 | 1.04 | 1.0313 | 1.0381 | 1.0399
WB | M049_ISIS - Gayndah 66 kV | % of Rated A | 32.93% | 32.42% | 27.3% | 33.33% | 32.37% | 27.58% | 33.3% | 32.4% | 27.63% | 33.16% | 32.25% | 27.54% | 33.35% | 32.25% | 27.67%
WB | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB | M049_ISIS - Gayndah 66 kV | Loading (A) | 131.3963 | 134.5252 | 101.0127 | 133.0019 | 134.3392 | 102.0288 | 132.8534 | 134.4584 | 102.2163 | 132.29 | 133.8362 | 101.9039 | 133.0551 | 133.8208 | 102.3772
WB | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 15.3692 | 15.6003 | 11.8597 | 15.5194 | 15.7385 | 11.9641 | 15.4951 | 15.7306 | 11.9799 | 15.4326 | 15.664 | 11.9453 | 15.4897 | 15.7106 | 11.9816
WB | M049_ISIS - Gayndah 66 kV | Loading (MW) | 15.3679 | 15.5957 | 11.818 | 15.5174 | 15.7353 | 11.9203 | 15.4943 | 15.7288 | 11.9354 | 15.4318 | 15.6623 | 11.9011 | 15.4891 | 15.7097 | 11.9342
WB | M049_ISIS - Gayndah 66 kV | Power Factor | 0.99991 | 0.99971 | 0.99648 | 0.99987 | 0.9998 | 0.99634 | 0.99995 | 0.99988 | 0.99629 | 0.99995 | 0.99989 | 0.9963 | 0.99993 | 0.99994 | 0.99604
WB | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
WB | M049_ISIS - Gayndah 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M049_ISIS - Gayndah 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99136 | 0.98163 | 1.0061 | 0.98845 | 0.99216 | 1.0047 | 0.98814 | 0.9908 | 1.0041 | 0.98848 | 0.99136 | 1.0044 | 0.98625 | 0.9946 | 1.0028
WB | M051_Tarong Tie 66 kV | % of Rated A | 41.48% | 35.5% | 23.56% | 41.47% | 35.49% | 23.56% | 41.46% | 35.49% | 23.56% | 41.44% | 35.47% | 23.55% | 42.36% | 36.27% | 24.05%
WB | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1
WB | M051_Tarong Tie 66 kV | Loading (A) | 44.3817 | 48.9898 | 31.1022 | 44.3734 | 48.9727 | 31.096 | 44.3653 | 48.9733 | 31.0931 | 44.3461 | 48.9523 | 31.0858 | 45.3288 | 50.0544 | 31.7407
WB | M051_Tarong Tie 66 kV | Loading (MVA) | 4.7861 | 5.3208 | 3.4865 | 4.7861 | 5.3207 | 3.4864 | 4.786 | 5.3207 | 3.4864 | 4.7859 | 5.3206 | 3.4864 | 4.8811 | 5.4269 | 3.5547
WB | M051_Tarong Tie 66 kV | Loading (MW) | 4.6791 | 5.1919 | 3.4228 | 4.679 | 5.1919 | 3.4228 | 4.679 | 5.1919 | 3.4228 | 4.679 | 5.1918 | 3.4228 | 4.7702 | 5.2932 | 3.4892
WB | M051_Tarong Tie 66 kV | Power Factor | 0.97568 | 0.97399 | 0.97886 | 0.97568 | 0.974 | 0.97886 | 0.97569 | 0.974 | 0.97886 | 0.9757 | 0.97401 | 0.97887 | 0.97538 | 0.97363 | 0.97866
WB | M051_Tarong Tie 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | M051_Tarong Tie 66 kV | Time | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00 | 16:30:00 | 17:30:00 | 22:00:00
WB | M051_Tarong Tie 66 kV | Min Voltage at Constrained Conductor (pu) | 0.94111 | 0.94727 | 0.9806 | 0.94128 | 0.94759 | 0.98078 | 0.94145 | 0.94758 | 0.98088 | 0.94184 | 0.94797 | 0.9811 | 0.93959 | 0.94546 | 0.97964
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 30.23% | 27.39% | 20.36% | 30.61% | 27.78% | 20.6% | 30.57% | 28.26% | 20.84% | 30.88% | 28.54% | 21.05% | 32.09% | 29.24% | 21.87%
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 123.9594 | 173.4001 | 109.7518 | 125.5207 | 175.8773 | 111.0308 | 125.3214 | 178.8808 | 112.3212 | 126.6061 | 180.6363 | 113.453 | 131.558 | 185.0958 | 117.8664
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 13.8719 | 19.3898 | 12.424 | 14.018 | 19.5961 | 12.5545 | 14.1636 | 19.7982 | 12.6851 | 14.3093 | 20.0025 | 12.8154 | 14.8204 | 20.7197 | 13.2725
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 13.7882 | 19.2281 | 12.3558 | 13.9323 | 19.4296 | 12.4849 | 14.0762 | 19.63 | 12.6139 | 14.2202 | 19.831 | 12.7429 | 14.7246 | 20.5347 | 13.1947
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.99397 | 0.99166 | 0.99451 | 0.99389 | 0.9915 | 0.99445 | 0.99383 | 0.99151 | 0.99439 | 0.99378 | 0.99142 | 0.99434 | 0.99353 | 0.99107 | 0.99414
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00 | 16:30:00 | 18:00:00 | 22:00:00
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9786 | 0.97763 | 0.98999 | 0.9766 | 0.9741 | 0.98886 | 0.98832 | 0.9676 | 0.98766 | 0.98835 | 0.96808 | 0.98784 | 0.98509 | 0.97862 | 0.98475