## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extend that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
The Network Modeling Team makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be taken into account when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modeling Team obtain these forecast values as populated by the Strategic Forecasting Team, the accuracy of these values are as per their quality assurance processes.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The studies results contained are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using PowerFactory 2024 SP5. The reported studies were calculated in PowerFactory 2024 SP5
· For the Energex network the model is running from External Grids representing the Powerlink Network at the common coupling points.
· For the Ergon network the model is running using the current years Powerlink Transmission TAPR model connected to the Ergon Subtransmission Model at the points of connection between the two utilities.
· The Mount Isa North West Power System network is running self contained within the Ergon Subtransmission model and is supplied by the large required generators in the system
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model as required by the study (most generation is excluded due to current settings)
· The Forecasts are extracted from SIFT or Tableau depending on where the current data is stored. 10PoE and 50PoE Forecasts from SIFT the Minimum Forecasts and Ergon Energy Daily Load Profiles are from Tableau
· Python automation was used to pull demand forecasts into PowerFactory model
· Load Flow studies were run for each of the following senarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLF_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Export Packaged Master Model
2. Import and Activate Extracted Model
3. Activate Load Characterstic Application Study Case
4. Run appropraite Forecast Load script for the given study
5. Run the DAPR Feeder Association Script to identify elements required for the new Feeder Voltage Attributes
6. Run The Setup Task Automation Script to create the command required for each individual year/Time Combination
7. Run the Task Automation Command with Parallel Computing turned on to calculate multiple studies at once
7. Repeat 4-6 for other characterstic combinations (such as SEQ Night Forecasts after running SEQ Day forecasts) required in the report.
8. Run a Python Interpreter that reads the output files and produces the formatted document
This entire process is completed with the RunExternalPowerFactoryGooey custom tool to run PowerFactory in external mode to minimise failed calculations due to momentary license outages.
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.
NNC | Normal Network Configuration
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor at the constrained conductor. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## Important Info 50POE_EE_N-1
2. Important Information
2.1 Study Information - 50PoE_EE_N-1 - Known Issues and Limitations
· The List of Subtransmission Projects to be stored as Variations has been produced manually from Copperleaf for the next 10 years.
· This report does not offer details of active Generators considered for each project
· Time Periods are based on Day (6am-6pm), Evening (6pm-10pm) and Night. This means that SN sift forecasts run at 7:30pm will be labelled as SE. This is unlikely to change
3. Additional Information
3.1 Information About Variables
The Values for a given timeslot shown are calculated as follows. All of the values will be for the line element in PowerFactory with the Loading Constraint.
This means that the Power Factor and Voltage values are recorded at the line that is considered the most "limited" not the minimum voltage on the feeder or the minimum Power Factor on the feeder
For each Contingency Event the values for each line are recorded with them eventually ending up in the following fields
% of Rated A: The % Utilisation called "loading" in PowerFactory [c:loading]
Limiting Line Name: The name of the line the results come from. It is nominally the most constrainted line. See later information for more details
Loading (A): Absolute Maximum Current for Both Ends in kA
Loading (MVA): Absolute Maximum Apparent Power for Both Ends in MVA
Loading (MW): Absolute Maximum Real Power for Both Ends in MW
Power Factor: Absolute Min PowerFactor for Both Ends
Rating (A): Line Nominal Rating using [e:Inom_a]
Time: The time at which the limiting study was completed
Min Voltage at Constrained Conductor: Min Voltage seen on both sides of line for the constrained line
Min Feeder Voltage: The minimum voltage seen on the ElmFeeder object associated with the line. Includes Open End Branch voltages and Feeder End Terminals
Min Feeder End Terminal Voltage: The Feeder voltage at the end terminals of a feeder. Does not include Open End Branches
Min Feeder Associated Sift-Load or Customer Terminal Voltage: The minimum voltage at terminals connected to a SIFT-load that the ElmFeeder can get to without traversing another feeder or at the Terminal Connected to a Customer site with an ElmOwner association starting with NMI_
Min Feeder Voltage at MV Connected TXs: The Minimum Voltage at any MV Terminals of Transformers within the ElmFeeder object
Once they are calculated for each feeder and Timeslot the Limiting entry is determined. This will be the values for a single line limited in the following order.
At each step all lines that share the "limiting" value will be recorded, provided their float representative is identical.
Minor differences in the float representation will result in the Min or Max value being utilised even if the value when considering real life significant figures are otherwise identical
1. % of Rated A - Max
2. Rating (A) - Min
3. Loading (MVA) - Max
The following limit calculations are applied to ensure only 1 line's values are recorded even if all entries have the same electrical loading characteristics
4. For N-1 results. Contingency Outage: Alphabetical Max
Note that "_NNC" is used with is a "Normal Network Configuration" contingency where nothing is taken out of service. If it is displayed then taking a feeder out of service did not make a recordable difference to the feeder loading.
If multiple feeder outage contingencies have the same affect on the feeder then the higher alphabetical name will be recorded.
5. Limiting Line Name: Alphabetical Min: This is to ensure there is a unique value
6. Current Study Case Time: Alphabetical Min: This is a stopgap to ensure there is a unique value

## 50PoE_EE_N-1_2025
Region | PF Feeder Obj Name | Variable | 2026 SD | 2026 SE | 2026 SN | 2027 SD | 2027 SE | 2027 SN | 2028 SD | 2028 SE | 2028 SN | 2029 SD | 2029 SE | 2029 SN | 2030 SD | 2030 SE | 2030 SN
CA | 6011_Blackwater - Comet 66 kV | % of Rated A | 68.21% | 61.08% | 88.94% | 68.37% | 61.21% | 89.12% | 68.37% | 61.22% | 89.12% | 68.22% | 61.09% | 88.93% | 69.64% | 62.29% | 90.68%
CA | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1
CA | 6011_Blackwater - Comet 66 kV | Loading (A) | 188.9517 | 180.1804 | 233.9067 | 189.388 | 180.5755 | 234.3884 | 189.3946 | 180.6044 | 234.391 | 188.9699 | 180.2288 | 233.8981 | 192.9145 | 183.7612 | 238.4849
CA | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 22.8445 | 21.8624 | 28.1192 | 22.8971 | 21.9103 | 28.1768 | 22.8978 | 21.9126 | 28.1768 | 22.8497 | 21.8702 | 28.1192 | 23.3114 | 22.2845 | 28.6584
CA | 6011_Blackwater - Comet 66 kV | Loading (MW) | 22.7054 | 21.6415 | 27.8383 | 22.76 | 21.6915 | 27.9013 | 22.7607 | 21.6945 | 27.9013 | 22.7094 | 21.6483 | 27.838 | 23.1967 | 22.0931 | 28.4313
CA | 6011_Blackwater - Comet 66 kV | Power Factor | 0.9939 | 0.98988 | 0.98998 | 0.994 | 0.99 | 0.99019 | 0.994 | 0.99003 | 0.9902 | 0.99384 | 0.98984 | 0.98997 | 0.99507 | 0.99139 | 0.99205
CA | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 6011_Blackwater - Comet 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6011_Blackwater - Comet 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0575 | 1.0613 | 1.0515 | 1.0575 | 1.0613 | 1.0515 | 1.0575 | 1.0613 | 1.0515 | 1.0576 | 1.0614 | 1.0515 | 1.0569 | 1.0607 | 1.0511
CA | 6011_Blackwater - Comet 66 kV | Contingency Outage | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 41.88% | 38.21% | 30.24% | 41.89% | 38.22% | 30.24% | 41.89% | 38.22% | 30.24% | 41.88% | 38.21% | 30.24% | 42.52% | 38.83% | 30.7%
CA | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 116.4395 | 113.1129 | 79.842 | 116.4438 | 113.1164 | 79.843 | 116.4446 | 113.1235 | 79.844 | 116.4245 | 113.104 | 79.8387 | 118.21 | 114.938 | 81.0362
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 13.5792 | 13.2573 | 9.4571 | 13.5792 | 13.2573 | 9.4571 | 13.5792 | 13.2574 | 9.4571 | 13.5791 | 13.2572 | 9.4571 | 13.773 | 13.4595 | 9.5926
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 12.9056 | 12.613 | 9.0093 | 12.9056 | 12.613 | 9.0094 | 12.9056 | 12.613 | 9.0094 | 12.9055 | 12.613 | 9.0093 | 13.0895 | 12.8051 | 9.1389
CA | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.95039 | 0.9514 | 0.95262 | 0.95039 | 0.95139 | 0.95262 | 0.95039 | 0.95139 | 0.95262 | 0.9504 | 0.9514 | 0.95263 | 0.95037 | 0.95137 | 0.95267
CA | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 6012_Blackwater - Bedford Weir 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6012_Blackwater - Bedford Weir 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0201 | 1.0252 | 1.0361 | 1.02 | 1.0251 | 1.0361 | 1.02 | 1.0251 | 1.0361 | 1.0202 | 1.0252 | 1.0361 | 1.0191 | 1.0243 | 1.0355
CA | 6012_Blackwater - Bedford Weir 66 kV | Contingency Outage | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6014_Blackwater - South Blackwater 66 kV | % of Rated A | 22.23% | 18.18% | 21.46% | 22.23% | 18.18% | 21.46% | 22.23% | 18.18% | 21.46% | 22.23% | 18.18% | 21.46% | 22.25% | 18.19% | 21.46%
CA | 6014_Blackwater - South Blackwater 66 kV | Limiting Line Name | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1 | TR_LINE 201131_1
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (A) | 110.2787 | 99.7978 | 106.8645 | 110.2829 | 99.798 | 106.8625 | 110.2837 | 99.8046 | 106.8638 | 110.2641 | 99.7861 | 106.8602 | 110.3488 | 99.8661 | 106.8806
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MVA) | 12.9651 | 11.7807 | 12.6935 | 12.9652 | 11.7807 | 12.6934 | 12.9652 | 11.7808 | 12.6935 | 12.9649 | 11.7805 | 12.6934 | 12.9663 | 11.7818 | 12.6937
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MW) | 11.9251 | 11.0014 | 11.7966 | 11.9251 | 11.0014 | 11.7966 | 11.9251 | 11.0015 | 11.7966 | 11.9251 | 11.0014 | 11.7966 | 11.9254 | 11.0017 | 11.7967
CA | 6014_Blackwater - South Blackwater 66 kV | Power Factor | 0.91757 | 0.92959 | 0.92638 | 0.91757 | 0.92959 | 0.92638 | 0.91757 | 0.92958 | 0.92638 | 0.91758 | 0.92959 | 0.92639 | 0.91753 | 0.92955 | 0.92637
CA | 6014_Blackwater - South Blackwater 66 kV | Rating (A) | 496 | 549 | 498 | 496 | 549 | 498 | 496 | 549 | 498 | 496 | 549 | 498 | 496 | 549 | 498
CA | 6014_Blackwater - South Blackwater 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6014_Blackwater - South Blackwater 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0199 | 1.0276 | 1.0318 | 1.0199 | 1.0276 | 1.0319 | 1.0199 | 1.0275 | 1.0318 | 1.0201 | 1.0277 | 1.0319 | 1.0193 | 1.0269 | 1.0317
CA | 6014_Blackwater - South Blackwater 66 kV | Contingency Outage | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV
CA | 6056_Comet - Emerald 66 kV | % of Rated A | 60.7% | 54.42% | 81.99% | 60.85% | 54.55% | 82.16% | 60.85% | 54.56% | 82.16% | 60.71% | 54.44% | 81.98% | 61.84% | 55.38% | 83.43%
CA | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1
CA | 6056_Comet - Emerald 66 kV | Loading (A) | 168.1315 | 160.5518 | 215.6262 | 168.5508 | 160.9314 | 216.0821 | 168.557 | 160.9549 | 216.0842 | 168.1613 | 160.6073 | 215.619 | 171.2856 | 163.3763 | 219.4221
CA | 6056_Comet - Emerald 66 kV | Loading (MVA) | 19.6577 | 18.9088 | 24.9505 | 19.704 | 18.9512 | 24.9978 | 19.7046 | 18.9525 | 24.9977 | 19.6645 | 18.9173 | 24.9508 | 19.9867 | 19.2053 | 25.3264
CA | 6056_Comet - Emerald 66 kV | Loading (MW) | 18.95 | 18.0539 | 23.8781 | 19.0002 | 18.1001 | 23.9351 | 19.0009 | 18.1028 | 23.9351 | 18.9538 | 18.0603 | 23.878 | 19.3157 | 18.3877 | 24.337
CA | 6056_Comet - Emerald 66 kV | Power Factor | 0.96399 | 0.95478 | 0.957 | 0.96427 | 0.95508 | 0.95747 | 0.96427 | 0.95515 | 0.95747 | 0.96385 | 0.95468 | 0.95698 | 0.96642 | 0.95742 | 0.96091
CA | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 6056_Comet - Emerald 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6056_Comet - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0227 | 1.0302 | 1.0122 | 1.0226 | 1.0301 | 1.012 | 1.0226 | 1.03 | 1.012 | 1.0229 | 1.0303 | 1.0122 | 1.0207 | 1.0283 | 1.0097
CA | 6056_Comet - Emerald 66 kV | Contingency Outage | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6271_Curragh Mine 66 kV | 6271_Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 13.27% | 12.75% | 12.85% | 13.27% | 12.75% | 12.85% | 13.27% | 12.75% | 12.85% | 13.27% | 12.75% | 12.85% | 13.56% | 13.06% | 13.1%
CA | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 36.8875 | 37.7386 | 33.9304 | 36.889 | 37.7398 | 33.9308 | 36.8892 | 37.7423 | 33.9313 | 36.8826 | 37.7356 | 33.9289 | 37.6918 | 38.6519 | 34.5756
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 4.2532 | 4.3725 | 3.9781 | 4.2532 | 4.3725 | 3.9781 | 4.2532 | 4.3726 | 3.9781 | 4.2531 | 4.3725 | 3.9781 | 4.3408 | 4.4732 | 4.0505
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 3.8917 | 4.0196 | 3.6335 | 3.8917 | 4.0196 | 3.6335 | 3.8917 | 4.0196 | 3.6335 | 3.8917 | 4.0196 | 3.6335 | 3.9772 | 4.1177 | 3.7043
CA | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.91496 | 0.91924 | 0.91332 | 0.91495 | 0.91924 | 0.91332 | 0.91495 | 0.91923 | 0.91332 | 0.91497 | 0.91924 | 0.91333 | 0.91619 | 0.92046 | 0.91449
CA | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 6058_Bedford Weir - Bingegang 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6058_Bedford Weir - Bingegang 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0086 | 1.0135 | 1.0256 | 1.0086 | 1.0135 | 1.0256 | 1.0086 | 1.0135 | 1.0256 | 1.0087 | 1.0136 | 1.0257 | 1.0074 | 1.0124 | 1.0248
CA | 6058_Bedford Weir - Bingegang 66 kV | Contingency Outage | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6059_Leichardt - Cook Colliery 66 kV | % of Rated A | 67.6% | 46.52% | 50.13% | 67.6% | 46.52% | 50.13% | 67.6% | 46.53% | 50.13% | 67.59% | 46.52% | 50.13% | 67.64% | 46.56% | 50.14%
CA | 6059_Leichardt - Cook Colliery 66 kV | Limiting Line Name | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (A) | 96.6645 | 98.166 | 104.2697 | 96.6683 | 98.1661 | 104.2678 | 96.669 | 98.1728 | 104.2691 | 96.6515 | 98.1542 | 104.2654 | 96.7272 | 98.2352 | 104.286
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MVA) | 11.2365 | 11.4846 | 12.2551 | 11.2365 | 11.4846 | 12.255 | 11.2365 | 11.4847 | 12.255 | 11.2363 | 11.4844 | 12.255 | 11.2373 | 11.4855 | 12.2553
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MW) | 10.5504 | 10.7595 | 11.4492 | 10.5504 | 10.7595 | 11.4492 | 10.5504 | 10.7596 | 11.4492 | 10.5504 | 10.7595 | 11.4492 | 10.5507 | 10.7598 | 11.4493
CA | 6059_Leichardt - Cook Colliery 66 kV | Power Factor | 0.93711 | 0.93506 | 0.93289 | 0.9371 | 0.93506 | 0.9329 | 0.9371 | 0.93506 | 0.9329 | 0.93711 | 0.93507 | 0.9329 | 0.93707 | 0.93502 | 0.93289
CA | 6059_Leichardt - Cook Colliery 66 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
CA | 6059_Leichardt - Cook Colliery 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6059_Leichardt - Cook Colliery 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0084 | 1.0147 | 1.0183 | 1.0083 | 1.0147 | 1.0183 | 1.0083 | 1.0147 | 1.0183 | 1.0085 | 1.0148 | 1.0183 | 1.0078 | 1.0141 | 1.0181
CA | 6059_Leichardt - Cook Colliery 66 kV | Contingency Outage | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV
CA | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 45.37% | 39.26% | 28.78% | 45.37% | 39.26% | 28.78% | 45.37% | 39.27% | 28.78% | 45.35% | 39.25% | 28.78% | 45.81% | 39.63% | 28.93%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 110.2404 | 106.7748 | 71.3773 | 110.2473 | 106.7867 | 71.3759 | 110.2488 | 106.801 | 71.3765 | 110.2091 | 106.7635 | 71.3757 | 111.3166 | 107.8037 | 71.75
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 13.0554 | 12.6777 | 8.4738 | 13.0555 | 12.6779 | 8.4737 | 13.0555 | 12.6781 | 8.4737 | 13.0549 | 12.6776 | 8.4737 | 13.1672 | 12.7847 | 8.5181
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 12.6964 | 12.3191 | 8.2055 | 12.6964 | 12.3192 | 8.2055 | 12.6964 | 12.3193 | 8.2055 | 12.6962 | 12.319 | 8.2055 | 12.8044 | 12.422 | 8.2492
CA | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.97237 | 0.97146 | 0.96657 | 0.97236 | 0.97145 | 0.96657 | 0.97236 | 0.97144 | 0.96657 | 0.97238 | 0.97146 | 0.96657 | 0.97235 | 0.97141 | 0.96669
CA | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 6065_Lilyvale - Tieri Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6065_Lilyvale - Tieri Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0303 | 1.0333 | 1.0366 | 1.0302 | 1.0332 | 1.0366 | 1.0302 | 1.033 | 1.0366 | 1.0305 | 1.0334 | 1.0366 | 1.029 | 1.0319 | 1.0366
CA | 6065_Lilyvale - Tieri Tee 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 122.2% | 84.64% | 46.95% | 122.6% | 84.87% | 47.04% | 122.6% | 84.89% | 47.04% | 122.2% | 84.63% | 46.95% | 125.2% | 86.56% | 47.65%
CA | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 416.8574 | 381.7273 | 202.8288 | 418.0561 | 382.7741 | 203.2038 | 418.0635 | 382.8345 | 203.2048 | 416.7008 | 381.6794 | 202.8262 | 427.0538 | 390.4029 | 205.8595
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 49.4868 | 45.4388 | 24.2217 | 49.6249 | 45.5589 | 24.2666 | 49.6252 | 45.5607 | 24.2666 | 49.481 | 45.4373 | 24.2218 | 50.6238 | 46.416 | 24.5813
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 49.1305 | 45.3129 | 23.1033 | 49.2553 | 45.4261 | 23.1564 | 49.2555 | 45.4272 | 23.1564 | 49.1272 | 45.312 | 23.1033 | 50.144 | 46.2256 | 23.529
CA | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.99214 | 0.98927 | 0.92323 | 0.9923 | 0.98945 | 0.92365 | 0.9923 | 0.98946 | 0.92365 | 0.99211 | 0.98926 | 0.92322 | 0.99052 | 0.99069 | 0.9266
CA | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432
CA | 6067 Lilyvale - Emerald 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6067 Lilyvale - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9612 | 0.97872 | 1.0446 | 0.96048 | 0.97806 | 1.0447 | 0.96046 | 0.97789 | 1.0446 | 0.96158 | 0.97886 | 1.0447 | 0.95418 | 0.97275 | 1.0446
CA | 6067 Lilyvale - Emerald 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV
CA | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 22.73% | 21.91% | 11.62% | 22.84% | 21.95% | 11.62% | 22.84% | 21.96% | 11.62% | 22.51% | 21.62% | 11.51% | 22.73% | 21.9% | 11.62%
CA | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_LINE 38978_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38978_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38978_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38978_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38978_1 | TR_LINE 38974_1 | TR_LINE 38974_1
CA | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 78.4107 | 86.754 | 41.2571 | 78.8104 | 86.9286 | 41.2438 | 78.8118 | 86.9474 | 41.2441 | 77.6495 | 85.63 | 40.8478 | 78.4347 | 86.7315 | 41.2462
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 9.3104 | 10.3221 | 4.9351 | 9.3131 | 10.3241 | 4.9355 | 9.3131 | 10.3243 | 4.9355 | 9.2137 | 10.2103 | 4.8912 | 9.3106 | 10.3218 | 4.9354
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 9.3029 | 10.3203 | 4.7318 | 9.3063 | 10.3225 | 4.7317 | 9.3063 | 10.3227 | 4.7317 | 9.2053 | 10.2075 | 4.6827 | 9.3032 | 10.32 | 4.7317
CA | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.99919 | 0.99983 | 0.9588 | 0.99927 | 0.99985 | 0.95871 | 0.99927 | 0.99985 | 0.95871 | 0.99909 | 0.99972 | 0.95737 | 0.9992 | 0.99982 | 0.95873
CA | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 345 | 396 | 355 | 345 | 396 | 355 | 345 | 396 | 355 | 345 | 396 | 355 | 345 | 396 | 355
CA | 6079_Barcaldine - Longreach 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6079_Barcaldine - Longreach 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0123 | 1.0408 | 1.0464 | 1.0072 | 1.0389 | 1.0468 | 1.0071 | 1.0387 | 1.0468 | 1.012 | 1.043 | 1.0475 | 1.012 | 1.041 | 1.0467
CA | 6079_Barcaldine - Longreach 66 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6067 Lilyvale - Emerald 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6075_Keppel - Farnborough 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6075_Keppel - Farnborough 66 kV | 6080_Barcaldine - Blackall 66 kV | 6067 Lilyvale - Emerald 66 kV | 6016_Blackwater - Utah 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 11.02% | 11.6% | 6.538% | 11% | 11.6% | 6.537% | 11% | 11.6% | 6.537% | 10.74% | 11.33% | 6.448% | 11.01% | 11.6% | 6.538%
CA | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 41.2065 | 45.1204 | 22.0971 | 41.1476 | 45.128 | 22.0963 | 41.1484 | 45.136 | 22.0963 | 40.1691 | 44.0846 | 21.7936 | 41.1865 | 45.1211 | 22.0969
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 4.7107 | 5.2165 | 2.5766 | 4.7107 | 5.2164 | 2.5768 | 4.7107 | 5.2164 | 2.5767 | 4.6185 | 5.1175 | 2.5419 | 4.7107 | 5.2165 | 2.5766
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 4.694 | 5.1578 | 2.2212 | 4.6937 | 5.1579 | 2.2212 | 4.6937 | 5.1579 | 2.2212 | 4.5989 | 5.0516 | 2.1771 | 4.6939 | 5.1578 | 2.2212
CA | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.99644 | 0.98876 | 0.86208 | 0.99638 | 0.98878 | 0.86203 | 0.99638 | 0.9888 | 0.86203 | 0.99574 | 0.98713 | 0.85649 | 0.99642 | 0.98876 | 0.86207
CA | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338
CA | 6080_Barcaldine - Blackall 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6080_Barcaldine - Blackall 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99499 | 1.0113 | 1.02 | 0.99644 | 1.0111 | 1.0201 | 0.99642 | 1.011 | 1.0201 | 1.0009 | 1.0155 | 1.0203 | 0.99548 | 1.0113 | 1.02
CA | 6080_Barcaldine - Blackall 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV
CA | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 7.685% | 6.14% | 2.854% | 7.685% | 6.14% | 2.854% | 7.685% | 6.141% | 2.854% | 7.683% | 6.139% | 2.854% | 7.695% | 6.147% | 2.854%
CA | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 18.6739 | 16.6994 | 7.0781 | 18.6749 | 16.7011 | 7.078 | 18.6752 | 16.7032 | 7.0781 | 18.669 | 16.6978 | 7.078 | 18.6981 | 16.7211 | 7.0784
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 2.1963 | 1.9701 | 0.83837 | 2.1963 | 1.9701 | 0.83837 | 2.1963 | 1.9701 | 0.83837 | 2.1963 | 1.9701 | 0.83837 | 2.1964 | 1.9701 | 0.83837
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 2.1634 | 1.9409 | 0.82693 | 2.1634 | 1.9409 | 0.82693 | 2.1634 | 1.9409 | 0.82693 | 2.1634 | 1.9409 | 0.82693 | 2.1634 | 1.9409 | 0.82693
CA | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.98391 | 0.98422 | 0.98596 | 0.98391 | 0.98422 | 0.98596 | 0.98391 | 0.98422 | 0.98596 | 0.98391 | 0.98422 | 0.98596 | 0.9839 | 0.98421 | 0.98596
CA | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 6085_Tieri Tee - Tieri 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6085_Tieri Tee - Tieri 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0289 | 1.032 | 1.0361 | 1.0288 | 1.0319 | 1.0361 | 1.0288 | 1.0318 | 1.0361 | 1.0291 | 1.0321 | 1.0361 | 1.0275 | 1.0307 | 1.0361
CA | 6085_Tieri Tee - Tieri 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 38.35% | 33.73% | 26.68% | 38.35% | 33.73% | 26.68% | 38.35% | 33.73% | 26.68% | 38.34% | 33.72% | 26.68% | 38.78% | 34.09% | 26.83%
CA | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_LINE 17095_1
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 93.1888 | 91.7337 | 66.1749 | 93.1947 | 91.7439 | 66.1736 | 93.1959 | 91.7561 | 66.1742 | 93.1624 | 91.7239 | 66.1734 | 94.2349 | 92.7363 | 66.5416
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 10.7032 | 10.5688 | 7.6771 | 10.7032 | 10.5689 | 7.6771 | 10.7032 | 10.569 | 7.6771 | 10.703 | 10.5688 | 7.6771 | 10.8071 | 10.6684 | 7.7191
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 10.2848 | 10.1399 | 7.2593 | 10.2848 | 10.1399 | 7.2593 | 10.2848 | 10.14 | 7.2593 | 10.2847 | 10.1399 | 7.2593 | 10.3875 | 10.2377 | 7.3017
CA | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.95988 | 0.95826 | 0.94203 | 0.95988 | 0.95826 | 0.94203 | 0.95988 | 0.95826 | 0.94203 | 0.95989 | 0.95827 | 0.94203 | 0.96022 | 0.95855 | 0.94242
CA | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 6086_Tieri Tee - Middlemount 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6086_Tieri Tee - Middlemount 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99906 | 1.0024 | 1.0138 | 0.999 | 1.0023 | 1.0138 | 0.99898 | 1.0022 | 1.0138 | 0.99933 | 1.0025 | 1.0138 | 0.9974 | 1.0008 | 1.0137
CA | 6086_Tieri Tee - Middlemount 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 27.12% | 27.57% | 21.93% | 27.01% | 27.46% | 21.89% | 27.01% | 27.47% | 21.89% | 26.85% | 27.28% | 21.83% | 27.09% | 27.54% | 21.91%
CA | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 192.0011 | 199.629 | 139.6914 | 191.2442 | 198.8435 | 139.4685 | 191.2457 | 198.8613 | 139.4684 | 190.0765 | 197.5384 | 139.0703 | 191.8056 | 199.3614 | 139.5961
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 46.0533 | 47.9604 | 33.8575 | 45.8718 | 47.7694 | 33.7974 | 45.8717 | 47.7686 | 33.7972 | 45.6019 | 47.4622 | 33.7147 | 45.9766 | 47.8608 | 33.8276
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 45.1235 | 47.3204 | 27.3349 | 44.9035 | 47.1272 | 27.2387 | 44.9036 | 47.1283 | 27.2387 | 44.5459 | 46.7425 | 27.0884 | 45.0092 | 47.2108 | 27.2859
CA | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.97981 | 0.98665 | 0.80735 | 0.97889 | 0.98656 | 0.80594 | 0.9789 | 0.98659 | 0.80595 | 0.97684 | 0.98484 | 0.80346 | 0.97896 | 0.98642 | 0.80662
CA | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637
CA | 7153_Lilyvale - Clermont 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 7153_Lilyvale - Clermont 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0477 | 1.0484 | 1.0601 | 1.0479 | 1.0484 | 1.0599 | 1.0478 | 1.0483 | 1.0599 | 1.0483 | 1.0488 | 1.0604 | 1.0472 | 1.0477 | 1.0599
CA | 7153_Lilyvale - Clermont 132 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV
CA | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 29.75% | 28.36% | 23.41% | 29.66% | 28.26% | 23.4% | 29.66% | 28.26% | 23.4% | 29.39% | 27.97% | 23.37% | 29.67% | 28.29% | 23.4%
CA | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 107.1036 | 110.899 | 82.1744 | 106.774 | 110.4825 | 82.1471 | 106.7745 | 110.4897 | 82.1467 | 105.7959 | 109.3541 | 82.0217 | 106.8002 | 110.6069 | 82.1436
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 25.5408 | 26.3952 | 20.5764 | 25.4727 | 26.2962 | 20.5721 | 25.4725 | 26.2946 | 20.5718 | 25.2673 | 26.0568 | 20.5446 | 25.462 | 26.3099 | 20.57
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 23.8884 | 25.1058 | 11.439 | 23.7734 | 25.0201 | 11.391 | 23.7735 | 25.0209 | 11.391 | 23.4298 | 24.6517 | 11.2458 | 23.7768 | 24.9995 | 11.391
CA | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.9353 | 0.95115 | 0.55593 | 0.93329 | 0.95147 | 0.55371 | 0.9333 | 0.95156 | 0.55372 | 0.92728 | 0.94607 | 0.54739 | 0.93382 | 0.95019 | 0.55377
CA | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351
CA | 7154_Clermont - Barcaldine 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 7154_Clermont - Barcaldine 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0426 | 1.0404 | 1.0952 | 1.0431 | 1.0404 | 1.0953 | 1.0431 | 1.0402 | 1.0953 | 1.0443 | 1.0416 | 1.0956 | 1.0424 | 1.0398 | 1.0953
CA | 7154_Clermont - Barcaldine 132 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6073_Clermont - Blair Athol 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6073_Clermont - Blair Athol 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6073_Clermont - Blair Athol 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6073_Clermont - Blair Athol 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6073_Clermont - Blair Athol 66 kV
CA | 7286_Blackwater - Memooloo 132 kV | % of Rated A | 17.23% | 13.21% | 13.05% | 17.23% | 13.21% | 13.05% | 17.23% | 13.21% | 13.05% | 17.23% | 13.21% | 13.05% | 17.29% | 13.27% | 13.09%
CA | 7286_Blackwater - Memooloo 132 kV | Limiting Line Name | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2 | TR_LINE 200594_2
CA | 7286_Blackwater - Memooloo 132 kV | Loading (A) | 121.467 | 97.0843 | 85.0893 | 121.47 | 97.0838 | 85.0888 | 121.4708 | 97.0896 | 85.0898 | 121.4544 | 97.0756 | 85.0866 | 121.9185 | 97.5686 | 85.3234
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MVA) | 28.7395 | 23.0965 | 20.3499 | 28.7396 | 23.0965 | 20.3499 | 28.7396 | 23.0966 | 20.3499 | 28.7394 | 23.0964 | 20.3498 | 28.833 | 23.1994 | 20.4014
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MW) | 28.5798 | 22.9392 | 20.2464 | 28.5798 | 22.9392 | 20.2464 | 28.5798 | 22.9392 | 20.2464 | 28.5798 | 22.9392 | 20.2464 | 28.6718 | 23.0403 | 20.2974
CA | 7286_Blackwater - Memooloo 132 kV | Power Factor | 0.9944 | 0.99315 | 0.99488 | 0.9944 | 0.99315 | 0.99488 | 0.9944 | 0.99315 | 0.99488 | 0.9944 | 0.99316 | 0.99489 | 0.99436 | 0.99311 | 0.99487
CA | 7286_Blackwater - Memooloo 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
CA | 7286_Blackwater - Memooloo 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 7286_Blackwater - Memooloo 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0349 | 1.0405 | 1.046 | 1.0348 | 1.0406 | 1.0461 | 1.0348 | 1.0405 | 1.046 | 1.035 | 1.0406 | 1.0461 | 1.0344 | 1.04 | 1.0458
CA | 7286_Blackwater - Memooloo 132 kV | Contingency Outage | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 12.33% | 12.23% | 10.86% | 12.33% | 12.23% | 10.86% | 12.33% | 12.23% | 10.86% | 12.33% | 12.23% | 10.86% | 12.39% | 12.3% | 10.9%
CA | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1
CA | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 86.9198 | 89.9089 | 70.8111 | 86.922 | 89.9085 | 70.8108 | 86.9225 | 89.9138 | 70.8115 | 86.9108 | 89.901 | 70.8089 | 87.3524 | 90.3865 | 71.0389
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 20.3709 | 21.187 | 16.8062 | 20.3709 | 21.187 | 16.8062 | 20.3709 | 21.187 | 16.8062 | 20.3709 | 21.187 | 16.8062 | 20.4618 | 21.2871 | 16.8562
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 19.7808 | 20.5947 | 16.2083 | 19.7808 | 20.5947 | 16.2083 | 19.7808 | 20.5947 | 16.2083 | 19.7808 | 20.5947 | 16.2083 | 19.8716 | 20.6947 | 16.2588
CA | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.97103 | 0.97204 | 0.96442 | 0.97103 | 0.97204 | 0.96442 | 0.97103 | 0.97204 | 0.96442 | 0.97103 | 0.97204 | 0.96442 | 0.97115 | 0.97217 | 0.96456
CA | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
CA | 7450_Memooloo - Rolleston 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 7450_Memooloo - Rolleston 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0251 | 1.0307 | 1.0381 | 1.0251 | 1.0307 | 1.0381 | 1.025 | 1.0306 | 1.0381 | 1.0252 | 1.0308 | 1.0381 | 1.0246 | 1.0301 | 1.0378
CA | 7450_Memooloo - Rolleston 132 kV | Contingency Outage | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV | 6013_Blackwater - Leichardt 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 34.34% | 36.8% | 20.06% | 34.61% | 37.11% | 20.18% | 35.09% | 37.46% | 20.42% | 35.28% | 37.68% | 20.51% | 36.37% | 38.86% | 21.03%
CA | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 137.7004 | 153.8233 | 74.6242 | 138.7855 | 155.1318 | 75.0655 | 140.7053 | 156.6017 | 75.9562 | 141.4653 | 157.5081 | 76.2991 | 145.8444 | 162.4521 | 78.2415
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 16.3003 | 18.1761 | 8.8709 | 16.423 | 18.3219 | 8.9298 | 16.6388 | 18.5645 | 9.0306 | 16.7298 | 18.6709 | 9.0748 | 17.2647 | 19.2861 | 9.3318
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 16.2727 | 18.1099 | 8.8366 | 16.3927 | 18.2507 | 8.8967 | 16.6019 | 18.4861 | 9.0018 | 16.691 | 18.5891 | 9.0469 | 17.2098 | 19.1797 | 9.3107
CA | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.9983 | 0.99635 | 0.99614 | 0.99816 | 0.99612 | 0.99629 | 0.99778 | 0.99578 | 0.99681 | 0.99768 | 0.99562 | 0.99692 | 0.99682 | 0.99448 | 0.99774
CA | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6001_Glenmore - Parkhurst 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6001_Glenmore - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0268 | 1.0236 | 1.0399 | 1.0263 | 1.023 | 1.0406 | 1.0255 | 1.0267 | 1.04 | 1.0255 | 1.0266 | 1.0404 | 1.0261 | 1.0277 | 1.0433
CA | 6001_Glenmore - Parkhurst 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA | 6003_Glenmore - Berserker 66 kV | % of Rated A | 109.8% | 111.3% | 61.8% | 110.6% | 112.4% | 61.9% | 111.9% | 115.8% | 62.28% | 112.2% | 116.3% | 62.24% | 115.7% | 121.2% | 63.27%
CA | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 102404_1 | TR_LINE 200510_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 200510_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 200510_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 200510_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 200510_1 | TR_LINE 22137_1
CA | 6003_Glenmore - Berserker 66 kV | Loading (A) | 440.2927 | 465.3182 | 229.9132 | 443.4977 | 469.9723 | 230.265 | 448.5908 | 483.842 | 231.6931 | 449.7831 | 486.3044 | 231.5256 | 464.053 | 506.4333 | 235.3689
CA | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 51.631 | 54.9094 | 27.319 | 51.9073 | 55.4097 | 27.3811 | 52.4753 | 56.5627 | 27.5363 | 52.6087 | 56.8328 | 27.5268 | 54.4164 | 59.1719 | 27.996
CA | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 51.6263 | 54.7571 | 25.863 | 51.8987 | 55.2252 | 25.9331 | 52.4648 | 56.2545 | 26.1233 | 52.5946 | 56.4928 | 26.1158 | 54.3153 | 58.567 | 26.8387
CA | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.99991 | 0.99723 | 0.94664 | 0.99983 | 0.99667 | 0.94705 | 0.9998 | 0.99455 | 0.94862 | 0.99973 | 0.99402 | 0.94867 | 0.99814 | 0.98978 | 0.9586
CA | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6003_Glenmore - Berserker 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6003_Glenmore - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0254 | 1.0318 | 1.0394 | 1.0235 | 1.0309 | 1.0402 | 1.0229 | 1.0222 | 1.0396 | 1.0228 | 1.0219 | 1.04 | 1.0254 | 1.0216 | 1.0404
CA | 6003_Glenmore - Berserker 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 41.56% | 34.14% | 22.76% | 41.49% | 34.15% | 22.69% | 41.61% | 34.12% | 22.75% | 41.29% | 33.94% | 22.57% | 42.35% | 34.64% | 22.78%
CA | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 152.5099 | 129.7336 | 76.9159 | 152.2637 | 129.7763 | 76.6795 | 152.7141 | 129.6643 | 76.8882 | 151.5492 | 128.9687 | 76.2947 | 155.4097 | 131.641 | 77.0037
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 18.0783 | 15.4054 | 9.1343 | 18.0445 | 15.4049 | 9.113 | 18.089 | 15.4497 | 9.1331 | 17.953 | 15.3667 | 9.0662 | 18.4854 | 15.7182 | 9.1562
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 18.0528 | 15.3132 | 9.1023 | 18.0184 | 15.3134 | 9.0798 | 18.064 | 15.3533 | 9.1004 | 17.9252 | 15.2673 | 9.0312 | 18.4843 | 15.6494 | 9.0796
CA | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.99858 | 0.994 | 0.9965 | 0.99854 | 0.99405 | 0.99635 | 0.99861 | 0.99375 | 0.99642 | 0.99845 | 0.99352 | 0.99614 | 0.99994 | 0.99561 | 0.99164
CA | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 380 | 338 | 367 | 380 | 338 | 367 | 380 | 338 | 367 | 380 | 338 | 367 | 380 | 338
CA | 6004_Glenmore - Rockhampton South 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6004_Glenmore - Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0367 | 1.0386 | 1.0388 | 1.0365 | 1.0382 | 1.0395 | 1.036 | 1.0422 | 1.039 | 1.0361 | 1.0422 | 1.0394 | 1.0403 | 1.0443 | 1.0401
CA | 6004_Glenmore - Rockhampton South 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 53.55% | 52.46% | 30.98% | 53.63% | 52.56% | 30.98% | 53.74% | 52.43% | 31.03% | 53.6% | 52.31% | 30.95% | 54.63% | 53.36% | 31.54%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 213.6791 | 217.6997 | 114.6128 | 213.9919 | 218.1242 | 114.6346 | 214.4225 | 217.5755 | 114.8259 | 213.8662 | 217.0728 | 114.5198 | 217.9737 | 221.4364 | 116.7146
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 25.3766 | 25.8877 | 13.6229 | 25.4072 | 25.9288 | 13.6357 | 25.4461 | 25.9608 | 13.6515 | 25.3822 | 25.9003 | 13.6203 | 25.9804 | 26.479 | 13.889
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 24.9999 | 25.6191 | 12.9153 | 25.0348 | 25.665 | 12.9271 | 25.0787 | 25.7012 | 12.9468 | 25.0126 | 25.6396 | 12.9116 | 25.7509 | 26.2662 | 13.0705
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.985 | 0.98949 | 0.948 | 0.98519 | 0.98969 | 0.94798 | 0.98541 | 0.98987 | 0.94833 | 0.98528 | 0.98981 | 0.94792 | 0.99104 | 0.99185 | 0.941
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0384 | 1.0397 | 1.0396 | 1.0381 | 1.0393 | 1.0404 | 1.0376 | 1.0432 | 1.0398 | 1.0377 | 1.0432 | 1.0402 | 1.0421 | 1.0455 | 1.0408
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 46.36% | 50.93% | 24.91% | 46.59% | 51.2% | 25.01% | 47.09% | 51.52% | 25.26% | 47.24% | 51.7% | 25.33% | 48.49% | 53.05% | 25.91%
CA | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1
CA | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 185.8864 | 212.8884 | 92.6787 | 186.8137 | 214.0171 | 93.0268 | 188.8146 | 215.3348 | 93.9503 | 189.4406 | 216.0917 | 94.2262 | 194.4304 | 221.7556 | 96.3847
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 21.8606 | 24.9625 | 11.0171 | 21.961 | 25.0814 | 11.0665 | 22.1793 | 25.3293 | 11.1699 | 22.2538 | 25.416 | 11.207 | 22.8581 | 26.1153 | 11.4957
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 21.8323 | 24.9016 | 11.0022 | 21.931 | 25.0172 | 11.0522 | 22.1445 | 25.2604 | 11.1577 | 22.2177 | 25.3449 | 11.1951 | 22.8108 | 26.0275 | 11.4873
CA | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.9987 | 0.99756 | 0.99865 | 0.99863 | 0.99744 | 0.9987 | 0.99843 | 0.99728 | 0.9989 | 0.99838 | 0.9972 | 0.99894 | 0.99793 | 0.99664 | 0.99927
CA | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6006_Glenmore - Frenchville 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6006_Glenmore - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0287 | 1.0256 | 1.0398 | 1.0283 | 1.0251 | 1.0406 | 1.0275 | 1.0289 | 1.04 | 1.0275 | 1.0288 | 1.0404 | 1.0283 | 1.0301 | 1.0433
CA | 6006_Glenmore - Frenchville 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 56.79% | 52.35% | 27.99% | 56.06% | 51.71% | 27.63% | 56.06% | 51.72% | 27.63% | 56.04% | 51.71% | 27.62% | 57.28% | 52.87% | 28.09%
CA | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 74.9649 | 87.4328 | 44.5067 | 73.9961 | 86.3605 | 43.9241 | 73.9965 | 86.371 | 43.9292 | 73.9789 | 86.3486 | 43.9227 | 75.6115 | 88.3004 | 44.663
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 8.9502 | 10.4456 | 5.3625 | 8.8343 | 10.3172 | 5.2953 | 8.8343 | 10.3174 | 5.2946 | 8.8341 | 10.317 | 5.2955 | 9.0245 | 10.5443 | 5.3822
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 8.915 | 10.4439 | 4.8534 | 8.8036 | 10.3164 | 4.7947 | 8.8036 | 10.3167 | 4.7947 | 8.8033 | 10.3162 | 4.7946 | 8.9959 | 10.5439 | 4.8892
CA | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.99607 | 0.99984 | 0.90505 | 0.99653 | 0.99993 | 0.90545 | 0.99653 | 0.99993 | 0.90559 | 0.99651 | 0.99992 | 0.90541 | 0.99684 | 0.99996 | 0.90841
CA | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6007_Biloela - Coominglah Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6007_Biloela - Coominglah Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0443 | 1.045 | 1.054 | 1.0443 | 1.045 | 1.0546 | 1.0443 | 1.0449 | 1.0543 | 1.0445 | 1.0451 | 1.0546 | 1.044 | 1.0445 | 1.0541
CA | 6007_Biloela - Coominglah Tee 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV
CA | 6008_Biloela - Wowan 66 kV | % of Rated A | 165.4% | 130.9% | 73.98% | 166.4% | 131.8% | 74.09% | 166.4% | 131.8% | 74.12% | 164.9% | 130.6% | 73.73% | 168.6% | 133.6% | 74.49%
CA | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1
CA | 6008_Biloela - Wowan 66 kV | Loading (A) | 218.3533 | 218.5556 | 117.629 | 219.6952 | 220.0537 | 117.799 | 219.6985 | 220.1101 | 117.8521 | 217.7042 | 218.0638 | 117.236 | 222.5637 | 223.1683 | 118.4429
CA | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 22.6813 | 22.7596 | 13.1033 | 22.7946 | 22.8864 | 13.1288 | 22.7948 | 22.8893 | 13.1305 | 22.628 | 22.7169 | 13.0718 | 23.0328 | 23.1486 | 13.1896
CA | 6008_Biloela - Wowan 66 kV | Loading (MW) | 20.5838 | 20.7804 | 12.2105 | 20.6755 | 20.8828 | 12.2356 | 20.6756 | 20.8848 | 12.2366 | 20.5332 | 20.7372 | 12.1814 | 20.8667 | 21.0936 | 12.2914
CA | 6008_Biloela - Wowan 66 kV | Power Factor | 0.90753 | 0.91304 | 0.93184 | 0.90704 | 0.91246 | 0.93195 | 0.90704 | 0.91242 | 0.93191 | 0.90742 | 0.91285 | 0.93185 | 0.90595 | 0.91122 | 0.9319
CA | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6008_Biloela - Wowan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6008_Biloela - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 0.88634 | 0.8887 | 0.96409 | 0.88515 | 0.88736 | 0.96456 | 0.88514 | 0.88723 | 0.96424 | 0.88699 | 0.88909 | 0.96506 | 0.88247 | 0.88457 | 0.96367
CA | 6008_Biloela - Wowan 66 kV | Contingency Outage | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV
CA | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 63.99% | 44.04% | 32.34% | 63.99% | 44.04% | 32.64% | 63.99% | 44.05% | 32.32% | 63.67% | 43.83% | 32.51% | 64.67% | 44.52% | 32.59%
CA | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1
CA | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 156.7671 | 150.6068 | 92.1725 | 156.7815 | 150.6244 | 93.0381 | 156.7847 | 150.6389 | 92.1018 | 155.9922 | 149.8845 | 92.6571 | 158.4529 | 152.2528 | 92.8827
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 18.8846 | 18.0905 | 11.1078 | 18.8845 | 18.0904 | 11.1292 | 18.8845 | 18.0902 | 11.1139 | 18.7891 | 17.9996 | 11.0834 | 19.0749 | 18.2709 | 11.2042
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 18.8054 | 17.9871 | 10.3956 | 18.8054 | 17.9871 | 10.396 | 18.8054 | 17.9871 | 10.3956 | 18.7069 | 17.8929 | 10.3417 | 19.0026 | 18.1757 | 10.5041
CA | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.99579 | 0.99427 | 0.93588 | 0.9958 | 0.99428 | 0.93412 | 0.9958 | 0.99429 | 0.93537 | 0.99561 | 0.99406 | 0.93309 | 0.9962 | 0.99478 | 0.93752
CA | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285
CA | 6019_Gladstone South - Friend St 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6019_Gladstone South - Friend St 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0537 | 1.0507 | 1.0542 | 1.0536 | 1.0505 | 1.0464 | 1.0535 | 1.0504 | 1.0556 | 1.0535 | 1.0504 | 1.0464 | 1.053 | 1.0497 | 1.0552
CA | 6019_Gladstone South - Friend St 66 kV | Contingency Outage | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV
CA | 6020_Gladstone South - BORE 66 kV | % of Rated A | 150.9% | 127.1% | 87.29% | 151.6% | 127.9% | 88% | 151.6% | 127.9% | 87.47% | 151.6% | 127.9% | 88.01% | 154.8% | 130.7% | 88.9%
CA | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1
CA | 6020_Gladstone South - BORE 66 kV | Loading (A) | 318.3892 | 375.0695 | 213.855 | 319.9787 | 377.1665 | 215.6092 | 319.9725 | 377.2128 | 214.2974 | 319.9752 | 377.2233 | 215.6162 | 326.5911 | 385.5226 | 217.8067
CA | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 37.234 | 43.5463 | 25.1807 | 37.4124 | 43.7775 | 25.2869 | 37.4111 | 43.7786 | 25.2657 | 37.4112 | 43.7788 | 25.287 | 38.1461 | 44.6844 | 25.6644
CA | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 36.1038 | 42.0986 | 24.5516 | 36.2764 | 42.3174 | 24.648 | 36.2763 | 42.318 | 24.6377 | 36.2763 | 42.3181 | 24.648 | 36.965 | 43.1661 | 25.018
CA | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.96965 | 0.96676 | 0.97502 | 0.96964 | 0.96665 | 0.97473 | 0.96966 | 0.96664 | 0.97515 | 0.96966 | 0.96664 | 0.97473 | 0.96904 | 0.96602 | 0.97481
CA | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 6020_Gladstone South - BORE 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6020_Gladstone South - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0207 | 1.0129 | 1.0286 | 1.0205 | 1.0126 | 1.0245 | 1.0205 | 1.0125 | 1.0299 | 1.0205 | 1.0125 | 1.0245 | 1.0194 | 1.0111 | 1.0293
CA | 6020_Gladstone South - BORE 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 34.44% | 36.83% | 26.87% | 34.55% | 36.97% | 27.05% | 34.55% | 36.98% | 26.89% | 34.55% | 36.98% | 27.05% | 35.14% | 37.66% | 27.25%
CA | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1
CA | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 214.5307 | 244.5828 | 160.969 | 215.2516 | 245.5062 | 162.0325 | 215.2561 | 245.534 | 161.0945 | 215.2578 | 245.5379 | 162.0374 | 218.9415 | 250.0528 | 163.2446
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 25.1728 | 28.5497 | 18.953 | 25.254 | 28.6524 | 19.003 | 25.254 | 28.6527 | 18.9931 | 25.254 | 28.6528 | 19.003 | 25.6649 | 29.1493 | 19.2362
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 24.4505 | 27.7211 | 18.4576 | 24.5295 | 27.8207 | 18.5009 | 24.5295 | 27.8208 | 18.4987 | 24.5296 | 27.8208 | 18.5009 | 24.9182 | 28.2906 | 18.7304
CA | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.97131 | 0.97098 | 0.97386 | 0.97131 | 0.97097 | 0.97358 | 0.97131 | 0.97096 | 0.97397 | 0.97131 | 0.97096 | 0.97358 | 0.97091 | 0.97054 | 0.97371
CA | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599
CA | 6022_Gladstone South - Calliope 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6022_Gladstone South - Calliope 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0264 | 1.021 | 1.0299 | 1.0262 | 1.0208 | 1.0259 | 1.0262 | 1.0207 | 1.0313 | 1.0262 | 1.0207 | 1.0259 | 1.0254 | 1.0197 | 1.0308
CA | 6022_Gladstone South - Calliope 66 kV | Contingency Outage | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV | 6034_Boyne Residential Tee - BORE 66 kV
CA | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 46.72% | 46.47% | 39.04% | 46.77% | 46.54% | 34.39% | 46.81% | 46.59% | 39.08% | 46.79% | 46.57% | 34.4% | 47.52% | 47.39% | 39.41%
CA | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 205.091 | 223.0641 | 151.8842 | 205.3223 | 223.3957 | 133.7852 | 205.502 | 223.6255 | 152.0124 | 205.4007 | 223.5596 | 133.8159 | 208.6047 | 227.4858 | 153.291
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 24.3744 | 26.4433 | 18.0696 | 24.3997 | 26.4799 | 15.8907 | 24.4207 | 26.5047 | 18.1084 | 24.4091 | 26.4971 | 15.8942 | 24.7786 | 26.947 | 18.2553
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 20.7595 | 23.2132 | 11.8547 | 20.8056 | 23.2721 | 13.2068 | 20.8311 | 23.3032 | 11.8814 | 20.8105 | 23.2896 | 13.2068 | 21.2741 | 23.8415 | 12.1114
CA | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.85163 | 0.87778 | 0.656 | 0.85264 | 0.87879 | 0.83107 | 0.85294 | 0.87915 | 0.65607 | 0.85251 | 0.87888 | 0.83089 | 0.8585 | 0.88469 | 0.66339
CA | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
CA | 6023_Friend St-Clinton Industrial 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6023_Friend St-Clinton Industrial 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0396 | 1.037 | 1.0407 | 1.0395 | 1.0369 | 1.039 | 1.0395 | 1.0368 | 1.0421 | 1.0395 | 1.0368 | 1.039 | 1.0391 | 1.0362 | 1.0418
CA | 6023_Friend St-Clinton Industrial 66 kV | Contingency Outage | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV
CA | 6024_Awoonga - Calliope 66kV | % of Rated A | 102% | 84.1% | 51.22% | 102.5% | 84.57% | 51.64% | 102.5% | 84.58% | 51.31% | 102.5% | 84.58% | 51.64% | 104.6% | 86.44% | 52.02%
CA | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1 | TR_LINE 18905_1
CA | 6024_Awoonga - Calliope 66kV | Loading (A) | 172.4596 | 201.8423 | 119.8642 | 173.274 | 202.9639 | 120.8425 | 173.2639 | 202.9911 | 120.058 | 173.2656 | 202.9973 | 120.8468 | 176.7145 | 207.4496 | 121.7166
CA | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 18.8863 | 21.6703 | 13.5011 | 18.9658 | 21.7745 | 13.5495 | 18.9647 | 21.7748 | 13.5408 | 18.9647 | 21.7749 | 13.5495 | 19.2922 | 22.1785 | 13.7095
CA | 6024_Awoonga - Calliope 66kV | Loading (MW) | 18.2984 | 20.9819 | 13.128 | 18.3771 | 21.082 | 13.1709 | 18.3771 | 21.0821 | 13.1691 | 18.3771 | 21.0821 | 13.1709 | 18.6834 | 21.4614 | 13.3285
CA | 6024_Awoonga - Calliope 66kV | Power Factor | 0.96888 | 0.96824 | 0.97237 | 0.96896 | 0.9682 | 0.97206 | 0.96902 | 0.96819 | 0.97255 | 0.96902 | 0.96819 | 0.97206 | 0.96844 | 0.96767 | 0.97221
CA | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 6024_Awoonga - Calliope 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6024_Awoonga - Calliope 66kV | Min Voltage at Constrained Conductor (pu) | 0.95788 | 0.93907 | 0.98526 | 0.9574 | 0.93837 | 0.98078 | 0.95739 | 0.93826 | 0.98656 | 0.95739 | 0.93823 | 0.98075 | 0.95491 | 0.93511 | 0.98524
CA | 6024_Awoonga - Calliope 66kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 13.33% | 13.64% | 6.714% | 13.34% | 13.65% | 6.743% | 13.34% | 13.65% | 6.705% | 13.34% | 13.65% | 6.744% | 13.39% | 13.71% | 6.716%
CA | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16031_1 | TR_LINE 16162_1
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 17.5977 | 22.7744 | 10.675 | 17.6072 | 22.7927 | 10.7221 | 17.6072 | 22.7956 | 10.6613 | 17.6074 | 22.7963 | 10.7224 | 17.6699 | 22.8977 | 10.6789
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 1.9028 | 2.397 | 1.2028 | 1.9028 | 2.397 | 1.2025 | 1.9028 | 2.397 | 1.2029 | 1.9028 | 2.397 | 1.2025 | 1.9028 | 2.3968 | 1.2028
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 1.8936 | 2.3841 | 1.1933 | 1.8936 | 2.3841 | 1.1934 | 1.8936 | 2.3841 | 1.1933 | 1.8936 | 2.3841 | 1.1934 | 1.8936 | 2.3841 | 1.1934
CA | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.99517 | 0.9946 | 0.99215 | 0.99517 | 0.99459 | 0.99242 | 0.99517 | 0.99459 | 0.99207 | 0.99517 | 0.99459 | 0.99242 | 0.99516 | 0.99464 | 0.99217
CA | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6029_Littlemore - Miriam Vale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6029_Littlemore - Miriam Vale 66 kV | Min Voltage at Constrained Conductor (pu) | 0.94586 | 0.92071 | 0.98563 | 0.94535 | 0.91997 | 0.98107 | 0.94535 | 0.91986 | 0.98696 | 0.94534 | 0.91983 | 0.98104 | 0.94202 | 0.91568 | 0.98525
CA | 6029_Littlemore - Miriam Vale 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6030_Littlemore - Monto 66 kV | % of Rated A | 42.61% | 38.82% | 19.45% | 41.89% | 38.23% | 19.13% | 41.89% | 38.24% | 19.07% | 41.89% | 38.24% | 19.13% | 42.7% | 38.95% | 19.44%
CA | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 22120_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 22120_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 22120_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 22120_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 22120_1 | TR_LINE 19505_1
CA | 6030_Littlemore - Monto 66 kV | Loading (A) | 56.2445 | 64.8366 | 30.92 | 55.2931 | 63.8463 | 30.4214 | 55.2945 | 63.856 | 30.319 | 55.295 | 63.8574 | 30.4219 | 56.3683 | 65.0524 | 30.9086
CA | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 6.2882 | 6.7053 | 3.5986 | 6.1817 | 6.605 | 3.5257 | 6.1817 | 6.605 | 3.5337 | 6.1817 | 6.605 | 3.5257 | 6.289 | 6.7059 | 3.599
CA | 6030_Littlemore - Monto 66 kV | Loading (MW) | 6.2753 | 6.701 | 3.3248 | 6.1726 | 6.5969 | 3.27 | 6.1726 | 6.597 | 3.2694 | 6.1726 | 6.597 | 3.27 | 6.2768 | 6.7012 | 3.3249
CA | 6030_Littlemore - Monto 66 kV | Power Factor | 0.99795 | 0.99934 | 0.92392 | 0.99853 | 0.99877 | 0.92748 | 0.99853 | 0.99876 | 0.92521 | 0.99853 | 0.99876 | 0.92749 | 0.99805 | 0.99929 | 0.92382
CA | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6030_Littlemore - Monto 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6030_Littlemore - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97729 | 0.90432 | 1.0179 | 0.97727 | 0.90461 | 1.0136 | 0.97724 | 0.90448 | 1.0193 | 0.97724 | 0.90446 | 1.0136 | 0.97527 | 0.90139 | 1.0184
CA | 6030_Littlemore - Monto 66 kV | Contingency Outage | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 48.57% | 44.85% | 24.44% | 47.82% | 44.19% | 24.07% | 47.82% | 44.2% | 24.08% | 47.81% | 44.19% | 24.07% | 49.03% | 45.34% | 24.54%
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 64.1085 | 74.8945 | 38.8587 | 63.1252 | 73.805 | 38.2761 | 63.1255 | 73.8139 | 38.2809 | 63.1106 | 73.7949 | 38.2748 | 64.7222 | 75.7187 | 39.015
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 7.3572 | 8.515 | 4.6193 | 7.246 | 8.3934 | 4.5532 | 7.246 | 8.3935 | 4.5525 | 7.2461 | 8.3934 | 4.5534 | 7.4197 | 8.5963 | 4.6372
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 7.257 | 8.474 | 4.1205 | 7.1551 | 8.3588 | 4.0651 | 7.1551 | 8.359 | 4.0651 | 7.1549 | 8.3587 | 4.0651 | 7.3312 | 8.5636 | 4.1553
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.98637 | 0.99518 | 0.89201 | 0.98746 | 0.99588 | 0.8928 | 0.98746 | 0.99589 | 0.89294 | 0.98742 | 0.99587 | 0.89277 | 0.98808 | 0.99619 | 0.89608
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0038 | 0.99447 | 1.0399 | 1.0041 | 0.99475 | 1.0406 | 1.0041 | 0.99463 | 1.0403 | 1.0043 | 0.99488 | 1.0407 | 1.0028 | 0.99303 | 1.0397
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV
CA | 6031_Calliope - Littlemore 66 kV | % of Rated A | 57.92% | 54% | 28.13% | 57.18% | 53.37% | 27.82% | 57.18% | 53.38% | 27.75% | 57.18% | 53.38% | 27.82% | 58.45% | 54.6% | 28.23%
CA | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 19492_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 19492_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 19492_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 19492_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 19492_1 | TR_LINE 13872_1
CA | 6031_Calliope - Littlemore 66 kV | Loading (A) | 76.4577 | 90.1734 | 44.7289 | 75.4799 | 89.1302 | 44.2375 | 75.4816 | 89.1431 | 44.117 | 75.4822 | 89.1449 | 44.2381 | 77.1529 | 91.1757 | 44.8818
CA | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 8.9373 | 9.9096 | 5.2744 | 8.8213 | 9.7946 | 5.1957 | 8.8213 | 9.7948 | 5.209 | 8.8213 | 9.7948 | 5.1956 | 9.0088 | 9.9922 | 5.2966
CA | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 8.9197 | 9.9065 | 4.8171 | 8.8067 | 9.7894 | 4.7595 | 8.8068 | 9.7896 | 4.758 | 8.8068 | 9.7896 | 4.7595 | 8.9956 | 9.9871 | 4.8519
CA | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.99803 | 0.99969 | 0.9133 | 0.99835 | 0.99947 | 0.91606 | 0.99835 | 0.99947 | 0.91342 | 0.99835 | 0.99947 | 0.91607 | 0.99854 | 0.99948 | 0.91604
CA | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6031_Calliope - Littlemore 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6031_Calliope - Littlemore 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0217 | 0.95911 | 1.0313 | 1.0215 | 0.9591 | 1.0271 | 1.0215 | 0.95898 | 1.0326 | 1.0215 | 0.95896 | 1.0271 | 1.0206 | 0.95644 | 1.0321
CA | 6031_Calliope - Littlemore 66 kV | Contingency Outage | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 108.7% | 89.9% | 68.54% | 109.1% | 90.29% | 69.03% | 109.1% | 90.3% | 68.59% | 109.1% | 90.3% | 69.03% | 111.1% | 92.16% | 69.56%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 22220_1
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 229.3412 | 265.1943 | 167.9184 | 230.1788 | 266.3529 | 169.1119 | 230.1692 | 266.3874 | 168.0469 | 230.1713 | 266.3953 | 169.1176 | 234.5132 | 271.8802 | 170.417
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 25.7116 | 29.2825 | 19.2118 | 25.7954 | 29.3938 | 19.2647 | 25.7941 | 29.3943 | 19.2518 | 25.7942 | 29.3945 | 19.2648 | 26.2281 | 29.9229 | 19.5022
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 24.7815 | 28.1809 | 18.6092 | 24.8634 | 28.286 | 18.6548 | 24.8633 | 28.2862 | 18.6507 | 24.8633 | 28.2863 | 18.6548 | 25.2659 | 28.7769 | 18.8866
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.96383 | 0.96238 | 0.96863 | 0.96387 | 0.96231 | 0.96834 | 0.96391 | 0.9623 | 0.96878 | 0.96391 | 0.9623 | 0.96834 | 0.96332 | 0.9617 | 0.96844
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98061 | 0.96579 | 1.0008 | 0.98022 | 0.96524 | 0.99644 | 0.98022 | 0.96514 | 1.0021 | 0.98021 | 0.96511 | 0.99641 | 0.97824 | 0.96264 | 1.001
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 55.02% | 50.13% | 25.65% | 55.47% | 50.56% | 25.96% | 55.47% | 50.56% | 25.82% | 55.47% | 50.56% | 25.96% | 56.88% | 51.86% | 26.45%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 90.7778 | 111.7996 | 47.1929 | 91.5304 | 112.7446 | 47.766 | 91.5315 | 112.7568 | 47.5042 | 91.5322 | 112.7595 | 47.7674 | 93.8497 | 115.6408 | 48.6649
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 10.3669 | 12.6121 | 5.4752 | 10.4493 | 12.7127 | 5.5186 | 10.4493 | 12.7127 | 5.5184 | 10.4493 | 12.7127 | 5.5186 | 10.6966 | 13.0109 | 5.6483
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 10.3068 | 12.5253 | 5.4548 | 10.3882 | 12.6244 | 5.4979 | 10.3882 | 12.6244 | 5.4978 | 10.3882 | 12.6244 | 5.4979 | 10.6327 | 12.9204 | 5.6269
CA | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.99419 | 0.99311 | 0.99625 | 0.99415 | 0.99305 | 0.99622 | 0.99415 | 0.99305 | 0.99624 | 0.99415 | 0.99305 | 0.99622 | 0.99402 | 0.99304 | 0.99619
CA | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184
CA | 6034_Boyne Residential Tee - BORE 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6034_Boyne Residential Tee - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99886 | 0.98666 | 1.0148 | 0.99852 | 0.98618 | 1.0106 | 0.99851 | 0.98608 | 1.0161 | 0.9985 | 0.98606 | 1.0106 | 0.99689 | 0.98404 | 1.0153
CA | 6034_Boyne Residential Tee - BORE 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 1.808% | 1.663% | 1.986% | 1.808% | 1.663% | 1.978% | 1.808% | 1.663% | 1.979% | 1.808% | 1.663% | 1.978% | 1.807% | 1.663% | 1.978%
CA | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 4.5924 | 4.5911 | 4.6079 | 4.5922 | 4.5909 | 4.5892 | 4.5921 | 4.5905 | 4.5907 | 4.5922 | 4.5905 | 4.5892 | 4.5907 | 4.5889 | 4.5896
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 0.5464 | 0.5461 | 0.55011 | 0.54635 | 0.54604 | 0.54565 | 0.54634 | 0.54595 | 0.54599 | 0.54635 | 0.54596 | 0.54563 | 0.546 | 0.54556 | 0.54573
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 0.00026834 | 0.00026819 | 0.00027016 | 0.00026831 | 0.00026816 | 0.00026797 | 0.00026831 | 0.00026812 | 0.00026813 | 0.00026831 | 0.00026812 | 0.00026796 | 0.00026814 | 0.00026793 | 0.00026801
CA | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527
CA | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 254 | 276 | 232 | 254 | 276 | 232 | 254 | 276 | 232 | 254 | 276 | 232 | 254 | 276 | 232
CA | 6039_Clinton Industrial - Beecher 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6039_Clinton Industrial - Beecher 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0408 | 1.0405 | 1.0443 | 1.0407 | 1.0405 | 1.0401 | 1.0407 | 1.0404 | 1.0404 | 1.0407 | 1.0404 | 1.0401 | 1.0404 | 1.04 | 1.0402
CA | 6039_Clinton Industrial - Beecher 66 kV | Contingency Outage | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV
CA | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 2.767% | 2.187% | 2.305% | 2.767% | 2.187% | 2.296% | 2.767% | 2.187% | 2.297% | 2.767% | 2.187% | 2.296% | 2.766% | 2.186% | 2.296%
CA | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 3.6531 | 3.6521 | 3.6654 | 3.6529 | 3.6519 | 3.6506 | 3.6529 | 3.6516 | 3.6517 | 3.6529 | 3.6516 | 3.6505 | 3.6517 | 3.6503 | 3.6508
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 0.43476 | 0.43452 | 0.43771 | 0.43472 | 0.43447 | 0.43416 | 0.43471 | 0.43441 | 0.43443 | 0.43472 | 0.43441 | 0.43415 | 0.43444 | 0.43409 | 0.43423
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 0.00017473 | 0.00017464 | 0.00017592 | 0.00017472 | 0.00017462 | 0.00017449 | 0.00017472 | 0.00017459 | 0.0001746 | 0.00017472 | 0.00017459 | 0.00017449 | 0.00017461 | 0.00017447 | 0.00017452
CA | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831
CA | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6041_Yarwun - Boat Creek 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6041_Yarwun - Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0411 | 1.0408 | 1.0446 | 1.041 | 1.0407 | 1.0404 | 1.041 | 1.0407 | 1.0407 | 1.041 | 1.0407 | 1.0404 | 1.0407 | 1.0403 | 1.0404
CA | 6041_Yarwun - Boat Creek 66 kV | Contingency Outage | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 11.05% | 3.491% | 1.399% | 11.06% | 3.493% | 1.4% | 11.06% | 3.498% | 1.4% | 11.06% | 3.499% | 1.4% | 11.03% | 3.498% | 1.401%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 21443_1 | TR_LINE 21443_1 | TR_LINE 22122_1 | TR_LINE 21443_1 | TR_LINE 21443_1 | TR_LINE 22122_1 | TR_LINE 21443_1 | TR_LINE 21443_1 | TR_LINE 22122_1 | TR_LINE 21443_1 | TR_LINE 21443_1 | TR_LINE 22122_1 | TR_LINE 21443_1 | TR_LINE 21443_1 | TR_LINE 22122_1
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 14.8092 | 6.3194 | 2.2248 | 14.8174 | 6.3223 | 2.2261 | 14.8241 | 6.3317 | 2.2253 | 14.8255 | 6.3333 | 2.2259 | 14.7837 | 6.3315 | 2.2274
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 1.7013 | 0.73297 | 0.2634 | 1.7014 | 0.73298 | 0.26375 | 1.7015 | 0.73301 | 0.26352 | 1.7015 | 0.73302 | 0.26369 | 1.7011 | 0.73301 | 0.2641
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 1.271 | 0.55683 | 0.19634 | 1.271 | 0.55683 | 0.19634 | 1.271 | 0.55683 | 0.19634 | 1.271 | 0.55683 | 0.19634 | 1.2709 | 0.55683 | 0.19634
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.74573 | 0.75916 | 0.74542 | 0.74571 | 0.75915 | 0.74442 | 0.74569 | 0.75912 | 0.74507 | 0.74568 | 0.75912 | 0.74458 | 0.74581 | 0.75912 | 0.74345
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 134 | 181 | 159 | 134 | 181 | 159 | 134 | 181 | 159 | 134 | 181 | 159 | 134 | 181 | 159
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 1.005 | 1.0146 | 1.0356 | 1.0045 | 1.0142 | 1.0364 | 1.004 | 1.0127 | 1.0359 | 1.004 | 1.0125 | 1.0363 | 1.0066 | 1.0128 | 1.0372
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6091_Egan's Hill - Gavial 66 kV
CA | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 31.96% | 28.35% | 14.42% | 31.36% | 27.81% | 14.1% | 31.36% | 27.82% | 14.1% | 31.35% | 27.81% | 14.1% | 31.96% | 28.35% | 14.42%
CA | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 75765_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 75765_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 75765_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 75765_1 | TR_LINE 18411_1 | TR_LINE 18411_1 | TR_LINE 75765_1
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 42.1825 | 47.3377 | 22.9343 | 41.3904 | 46.4475 | 22.4155 | 41.3905 | 46.4514 | 22.4214 | 41.3777 | 46.4392 | 22.4129 | 42.1933 | 47.3485 | 22.9313
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 4.6981 | 5.2396 | 2.6989 | 4.6112 | 5.1429 | 2.6396 | 4.6112 | 5.1429 | 2.6396 | 4.6112 | 5.1429 | 2.6396 | 4.6982 | 5.2396 | 2.699
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 4.6867 | 5.2255 | 2.6675 | 4.5935 | 5.1215 | 2.6137 | 4.5935 | 5.1215 | 2.6138 | 4.5935 | 5.1215 | 2.6137 | 4.6867 | 5.2255 | 2.6675
CA | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.99749 | 0.99725 | 0.98837 | 0.99606 | 0.99576 | 0.9902 | 0.99606 | 0.99576 | 0.99022 | 0.99606 | 0.99577 | 0.99019 | 0.99749 | 0.99725 | 0.98836
CA | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6045_Coominglah Tee - Monto 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97407 | 0.96798 | 1.0294 | 0.97437 | 0.96835 | 1.0301 | 0.97437 | 0.96827 | 1.0298 | 0.97467 | 0.96852 | 1.0302 | 0.97383 | 0.96776 | 1.0296
CA | 6045_Coominglah Tee - Monto 66 kV | Contingency Outage | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV
CA | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 120.5% | 93.63% | 58.55% | 121.4% | 94.44% | 58.66% | 121.4% | 94.47% | 58.69% | 120.8% | 94% | 58.61% | 123.4% | 96.13% | 59.04%
CA | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 22282_1 | TR_LINE 22282_1 | TR_LINE 15222_1 | TR_LINE 22282_1 | TR_LINE 22282_1 | TR_LINE 15222_1 | TR_LINE 22282_1 | TR_LINE 22282_1 | TR_LINE 15222_1 | TR_LINE 22282_1 | TR_LINE 22282_1 | TR_LINE 15222_1 | TR_LINE 22282_1 | TR_LINE 22282_1 | TR_LINE 15222_1
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 159.058 | 156.3599 | 93.0921 | 160.2758 | 157.7148 | 93.2694 | 160.2784 | 157.7599 | 93.3123 | 159.4873 | 156.9746 | 93.1844 | 162.869 | 160.5297 | 93.8695
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 14.7346 | 14.5382 | 9.1755 | 14.8162 | 14.6297 | 9.1964 | 14.8163 | 14.6312 | 9.1967 | 14.7899 | 14.6048 | 9.1959 | 14.9858 | 14.8178 | 9.2398
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 13.1973 | 13.1257 | 8.2775 | 13.2679 | 13.2045 | 8.2992 | 13.2679 | 13.2055 | 8.2993 | 13.2502 | 13.1878 | 8.299 | 13.4134 | 13.3655 | 8.3431
CA | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.89566 | 0.90284 | 0.90168 | 0.8955 | 0.90258 | 0.902 | 0.8955 | 0.90256 | 0.90199 | 0.89589 | 0.90298 | 0.90204 | 0.89507 | 0.90199 | 0.90254
CA | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6046_Mt Morgan - Wowan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6046_Mt Morgan - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 0.81022 | 0.81322 | 0.85809 | 0.80852 | 0.81131 | 0.8584 | 0.80851 | 0.81116 | 0.85802 | 0.81107 | 0.81375 | 0.85914 | 0.80475 | 0.80732 | 0.85688
CA | 6046_Mt Morgan - Wowan 66 kV | Contingency Outage | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV
CA | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 8.81% | 7.74% | 2.952% | 8.808% | 7.738% | 2.966% | 8.808% | 7.739% | 2.948% | 8.808% | 7.739% | 2.966% | 8.832% | 7.768% | 2.951%
CA | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 13.5678 | 16.0227 | 5.8753 | 13.5645 | 16.017 | 5.9016 | 13.5649 | 16.0196 | 5.8656 | 13.565 | 16.0199 | 5.9018 | 13.6018 | 16.0795 | 5.8722
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 1.4365 | 1.6393 | 0.67235 | 1.4365 | 1.6392 | 0.6724 | 1.4365 | 1.6393 | 0.67232 | 1.4365 | 1.6393 | 0.67241 | 1.4367 | 1.6396 | 0.67234
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 1.284 | 1.4594 | 0.60633 | 1.284 | 1.4594 | 0.60634 | 1.284 | 1.4594 | 0.60633 | 1.284 | 1.4594 | 0.60634 | 1.284 | 1.4595 | 0.60633
CA | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.89379 | 0.89026 | 0.90181 | 0.8938 | 0.89028 | 0.90174 | 0.8938 | 0.89027 | 0.90183 | 0.8938 | 0.89027 | 0.90174 | 0.89372 | 0.89013 | 0.90181
CA | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199
CA | 6047_Coominglah Sub Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6047_Coominglah Sub Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 0.92617 | 0.89498 | 1.0011 | 0.92639 | 0.89528 | 0.99668 | 0.92636 | 0.89514 | 1.0027 | 0.92635 | 0.89512 | 0.99665 | 0.92396 | 0.89199 | 1.0016
CA | 6047_Coominglah Sub Tee 66 kV | Contingency Outage | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV
CA | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 35.18% | 40.08% | 16.34% | 35.19% | 40.09% | 16.32% | 35.39% | 40.15% | 16.41% | 35.39% | 40.15% | 16.41% | 35.89% | 40.87% | 16.75%
CA | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 141.0698 | 167.5291 | 60.7688 | 141.1175 | 167.5889 | 60.7249 | 141.9157 | 167.8267 | 61.0631 | 141.9166 | 167.8224 | 61.0419 | 143.9178 | 170.8334 | 62.3182
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 16.5345 | 19.6245 | 7.1826 | 16.5346 | 19.6245 | 7.1825 | 16.617 | 19.7214 | 7.2182 | 16.617 | 19.7214 | 7.2182 | 16.9452 | 20.1122 | 7.3606
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 16.5137 | 19.5894 | 7.1809 | 16.5137 | 19.5894 | 7.1809 | 16.5957 | 19.6863 | 7.2165 | 16.5957 | 19.6863 | 7.2165 | 16.9231 | 20.0752 | 7.3589
CA | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.99874 | 0.99821 | 0.99977 | 0.99873 | 0.99821 | 0.99977 | 0.99872 | 0.99822 | 0.99977 | 0.99872 | 0.99822 | 0.99977 | 0.9987 | 0.99816 | 0.99976
CA | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6050_Parkhurst - Frenchville 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6050_Parkhurst - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0252 | 1.0246 | 1.0339 | 1.0249 | 1.0243 | 1.0347 | 1.0242 | 1.0279 | 1.034 | 1.0242 | 1.0279 | 1.0344 | 1.0299 | 1.0298 | 1.0332
CA | 6050_Parkhurst - Frenchville 66 kV | Contingency Outage | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV
CA | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 177% | 157.5% | 74.52% | 179.9% | 160.4% | 75.45% | 184.4% | 163.6% | 77% | 186.1% | 165.3% | 77.64% | 194.4% | 174.8% | 80.81%
CA | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 375.2875 | 466.1711 | 183.3177 | 381.4403 | 474.7258 | 185.6076 | 390.8325 | 484.1407 | 189.4298 | 394.4853 | 489.1617 | 190.9932 | 412.0687 | 517.2894 | 198.8006
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 39.9653 | 47.9397 | 20.8328 | 40.5064 | 48.6162 | 21.0933 | 41.3241 | 49.5974 | 21.4883 | 41.6632 | 50.0196 | 21.6625 | 43.2925 | 52.108 | 22.4723
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 39.5846 | 47.2308 | 20.8264 | 40.1014 | 47.8676 | 21.0854 | 40.8815 | 48.8022 | 21.4775 | 41.2227 | 49.2219 | 21.6503 | 42.7849 | 51.164 | 22.4527
CA | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.99047 | 0.98521 | 0.99969 | 0.99 | 0.9846 | 0.99962 | 0.98929 | 0.98397 | 0.9995 | 0.98943 | 0.98405 | 0.99944 | 0.98827 | 0.98188 | 0.99912
CA | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 6051_Parkhurst - Keppel 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6051_Parkhurst - Keppel 66 kV | Min Voltage at Constrained Conductor (pu) | 0.92319 | 0.88877 | 0.99056 | 0.9204 | 0.88479 | 0.99052 | 0.91612 | 0.88483 | 0.98861 | 0.915 | 0.88307 | 0.98843 | 0.90969 | 0.86894 | 0.98491
CA | 6051_Parkhurst - Keppel 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 6052_Pandoin - Kunwarara 66 kV | % of Rated A | 18.05% | 17.88% | 16.11% | 18.06% | 17.89% | 16.1% | 18.07% | 17.82% | 16.1% | 18.07% | 17.82% | 16.1% | 18.01% | 17.92% | 16.14%
CA | 6052_Pandoin - Kunwarara 66 kV | Limiting Line Name | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (A) | 62.6483 | 64.5364 | 51.8758 | 62.669 | 64.5882 | 51.8287 | 62.7076 | 64.3245 | 51.8529 | 62.7075 | 64.3356 | 51.8315 | 62.4856 | 64.7016 | 51.9715
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MVA) | 7.0883 | 7.311 | 5.9232 | 7.0886 | 7.3115 | 5.9228 | 7.089 | 7.3089 | 5.923 | 7.089 | 7.309 | 5.9228 | 7.0866 | 7.3126 | 5.924
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MW) | 5.4194 | 5.6659 | 4.5942 | 5.4195 | 5.6661 | 4.5941 | 5.4196 | 5.6654 | 4.5941 | 5.4196 | 5.6655 | 4.5941 | 5.419 | 5.6664 | 4.5944
CA | 6052_Pandoin - Kunwarara 66 kV | Power Factor | 0.75728 | 0.7675 | 0.76968 | 0.75726 | 0.76745 | 0.76973 | 0.75722 | 0.76769 | 0.7697 | 0.75722 | 0.76768 | 0.76972 | 0.75744 | 0.76735 | 0.76958
CA | 6052_Pandoin - Kunwarara 66 kV | Rating (A) | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322
CA | 6052_Pandoin - Kunwarara 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6052_Pandoin - Kunwarara 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98976 | 0.99098 | 0.99882 | 0.98947 | 0.99026 | 0.99966 | 0.98891 | 0.99397 | 0.99922 | 0.98892 | 0.99381 | 0.9996 | 0.9921 | 0.98867 | 0.99711
CA | 6052_Pandoin - Kunwarara 66 kV | Contingency Outage | 6006_Glenmore - Frenchville 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6006_Glenmore - Frenchville 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6006_Glenmore - Frenchville 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6006_Glenmore - Frenchville 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 51.48% | 48.65% | 24.26% | 51.81% | 49.08% | 24.34% | 52.38% | 49.53% | 24.52% | 52.42% | 49.65% | 24.5% | 54.12% | 49.3% | 25.06%
CA | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 269.2487 | 288.0014 | 132.45 | 270.9742 | 290.5704 | 132.8724 | 273.9237 | 293.1983 | 133.8808 | 274.1366 | 293.9486 | 133.7628 | 283.0281 | 291.8744 | 136.8525
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 31.8886 | 34.1099 | 15.7775 | 32.0781 | 34.3912 | 15.8394 | 32.4039 | 34.8236 | 15.9514 | 32.4264 | 34.9068 | 15.9428 | 33.5241 | 34.5022 | 16.2695
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 31.7631 | 33.1535 | 15.7092 | 31.9399 | 33.3901 | 15.7726 | 32.2433 | 33.7617 | 15.8908 | 32.2611 | 33.8291 | 15.8823 | 33.2745 | 34.0015 | 15.49
CA | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.99606 | 0.97196 | 0.99545 | 0.99569 | 0.97089 | 0.99556 | 0.99504 | 0.96951 | 0.99598 | 0.9949 | 0.96913 | 0.99599 | 0.99256 | 0.98549 | 0.95111
CA | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546
CA | 6053_Parkhurst - Pandoin 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6053_Parkhurst - Pandoin 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0299 | 1.0274 | 1.0404 | 1.0294 | 1.0265 | 1.0411 | 1.0284 | 1.03 | 1.0405 | 1.0283 | 1.0298 | 1.0409 | 1.0292 | 1.0262 | 1.04
CA | 6053_Parkhurst - Pandoin 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6052_Pandoin - Kunwarara 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6052_Pandoin - Kunwarara 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6052_Pandoin - Kunwarara 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6052_Pandoin - Kunwarara 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6052_Pandoin - Kunwarara 66 kV
CA | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 49.99% | 36.11% | 32.76% | 50.02% | 36.14% | 32.91% | 50.01% | 36.15% | 32.71% | 50.01% | 36.15% | 32.92% | 50.16% | 36.29% | 32.76%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 84.4857 | 86.6658 | 76.6574 | 84.5358 | 86.7416 | 77.019 | 84.5155 | 86.7538 | 76.5399 | 84.5163 | 86.7566 | 77.0217 | 84.772 | 87.0965 | 76.6592
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 9.1269 | 9.1825 | 8.5073 | 9.1278 | 9.1838 | 8.5096 | 9.1257 | 9.184 | 8.5053 | 9.1257 | 9.184 | 8.5097 | 9.1301 | 9.1899 | 8.5073
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 7.987 | 8.017 | 7.5001 | 7.9873 | 8.0174 | 7.5012 | 7.9872 | 8.0174 | 7.4995 | 7.9872 | 8.0174 | 7.5012 | 7.9884 | 8.0191 | 7.5001
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.86944 | 0.86809 | 0.87404 | 0.8694 | 0.86803 | 0.87409 | 0.8696 | 0.86802 | 0.87415 | 0.8696 | 0.86802 | 0.87409 | 0.86939 | 0.86774 | 0.87404
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Min Voltage at Constrained Conductor (pu) | 0.93725 | 0.91786 | 0.96666 | 0.93675 | 0.91714 | 0.9621 | 0.93676 | 0.91702 | 0.968 | 0.93675 | 0.917 | 0.96207 | 0.93421 | 0.91378 | 0.96664
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 96.5% | 114.6% | 49.8% | 98.13% | 116.8% | 50.42% | 100.2% | 122% | 51.44% | 101.3% | 123.5% | 51.86% | 106% | 130.5% | 53.92%
CA | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 385.0413 | 475.5996 | 184.2612 | 391.552 | 484.7363 | 186.563 | 399.7955 | 506.1918 | 190.3286 | 404.0534 | 512.6229 | 191.8931 | 422.9132 | 541.5609 | 199.4988
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 44.4561 | 55.1053 | 21.6822 | 45.1683 | 56.0917 | 21.9661 | 46.0854 | 58.0018 | 22.3941 | 46.5624 | 58.7033 | 22.5846 | 48.8093 | 61.9179 | 23.4791
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 43.0267 | 52.3881 | 21.6154 | 43.6551 | 53.2177 | 21.8926 | 44.5728 | 54.7073 | 22.3154 | 44.9931 | 55.2811 | 22.501 | 46.9115 | 57.9142 | 23.3698
CA | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.96785 | 0.95069 | 0.99692 | 0.9665 | 0.94876 | 0.99665 | 0.96718 | 0.9432 | 0.99649 | 0.9663 | 0.9417 | 0.9963 | 0.96112 | 0.93534 | 0.99535
CA | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 6074_Lakes Creek - Tanby 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6074_Lakes Creek - Tanby 66 kV | Min Voltage at Constrained Conductor (pu) | 0.94299 | 0.92576 | 1.0033 | 0.9406 | 0.92227 | 1.0035 | 0.93862 | 0.90696 | 1.0021 | 0.93733 | 0.90476 | 1.0021 | 0.9341 | 0.89607 | 1.0007
CA | 6074_Lakes Creek - Tanby 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV
CA | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.2992% | 0.2696% | 0.3451% | 0.2989% | 0.2692% | 0.3453% | 0.2984% | 0.27% | 0.3449% | 0.2982% | 0.2698% | 0.345% | 0.2991% | 0.2684% | 0.3445%
CA | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.131 | 1.1189 | 1.1631 | 1.1298 | 1.1173 | 1.1636 | 1.1278 | 1.1205 | 1.1623 | 1.1273 | 1.1197 | 1.1625 | 1.1308 | 1.114 | 1.1609
CA | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.12832 | 0.12558 | 0.13569 | 0.12805 | 0.12522 | 0.13581 | 0.12759 | 0.12595 | 0.13551 | 0.12747 | 0.12576 | 0.13556 | 0.12826 | 0.12449 | 0.13519
CA | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.1973e-06 | 3.1292e-06 | 3.3812e-06 | 3.1907e-06 | 3.1204e-06 | 3.3842e-06 | 3.1793e-06 | 3.1386e-06 | 3.3768e-06 | 3.1763e-06 | 3.1339e-06 | 3.3779e-06 | 3.1962e-06 | 3.1019e-06 | 3.3688e-06
CA | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.1858e-06 | 2.1883e-06 | 2.1892e-06 | 2.189e-06 | 2.1899e-06 | 2.1915e-06 | 2.1901e-06 | 2.1954e-06 | 2.1914e-06 | 2.1878e-06 | 2.1921e-06 | 2.1918e-06 | 2.1938e-06 | 2.1888e-06 | 2.1892e-06
CA | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 6075_Keppel - Farnborough 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6075_Keppel - Farnborough 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99245 | 0.98181 | 1.0206 | 0.99141 | 0.98042 | 1.021 | 0.98963 | 0.98325 | 1.0199 | 0.98917 | 0.98253 | 1.0201 | 0.99224 | 0.97752 | 1.0187
CA | 6075_Keppel - Farnborough 66 kV | Contingency Outage | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6097_Egan's Hill - Canning 66 kV | 6091_Egan's Hill - Gavial 66 kV
CA | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 177.1% | 157.6% | 74.53% | 180% | 160.5% | 75.47% | 184.4% | 163.6% | 77.02% | 186.2% | 165.3% | 77.66% | 194.5% | 174.8% | 80.84%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 375.4705 | 466.3885 | 183.3552 | 381.6273 | 474.9466 | 185.649 | 391.025 | 484.3659 | 189.4773 | 394.676 | 489.3856 | 191.0433 | 412.2681 | 517.5238 | 198.8624
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 39.1335 | 46.6018 | 20.6592 | 39.6436 | 47.2233 | 20.9151 | 40.4128 | 48.143 | 21.3021 | 40.7354 | 48.5353 | 21.4731 | 42.2706 | 50.4266 | 22.2658
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 38.8618 | 46.1155 | 20.654 | 39.3547 | 46.7111 | 20.9086 | 40.0976 | 47.5994 | 21.2933 | 40.4241 | 47.994 | 21.4632 | 41.9135 | 49.7908 | 22.2499
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.99306 | 0.98956 | 0.99975 | 0.99271 | 0.98915 | 0.99969 | 0.9922 | 0.98871 | 0.99959 | 0.99236 | 0.98885 | 0.99954 | 0.99155 | 0.98739 | 0.99929
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 0.91142 | 0.87368 | 0.9855 | 0.9084 | 0.86936 | 0.98538 | 0.90376 | 0.86905 | 0.98333 | 0.90254 | 0.86714 | 0.98309 | 0.89657 | 0.85191 | 0.9793
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 6087_Glenmore - QMAG Tee 66 kV | % of Rated A | 40.3% | 42.93% | 24.14% | 40.61% | 43.28% | 24.27% | 41.15% | 43.67% | 24.55% | 41.36% | 43.92% | 24.65% | 42.6% | 45.25% | 25.25%
CA | 6087_Glenmore - QMAG Tee 66 kV | Limiting Line Name | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 22128_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 22128_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 22128_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 22128_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 22128_1
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (A) | 161.6029 | 179.4292 | 89.7902 | 162.8317 | 180.9104 | 90.2885 | 165.0113 | 182.5477 | 91.3162 | 165.8694 | 183.5714 | 91.7045 | 170.8175 | 189.1479 | 93.9125
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MVA) | 19.0312 | 21.0777 | 10.6737 | 19.1682 | 21.24 | 10.7408 | 19.4098 | 21.5112 | 10.8568 | 19.5114 | 21.6297 | 10.9071 | 20.1094 | 22.3151 | 11.2008
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MW) | 18.9898 | 20.9966 | 10.6596 | 19.1239 | 21.1538 | 10.7273 | 19.3577 | 21.4173 | 10.8459 | 19.4572 | 21.5321 | 10.8967 | 20.0371 | 22.1916 | 11.1943
CA | 6087_Glenmore - QMAG Tee 66 kV | Power Factor | 0.99783 | 0.99615 | 0.99868 | 0.99769 | 0.99594 | 0.99875 | 0.99732 | 0.99563 | 0.999 | 0.99722 | 0.99549 | 0.99905 | 0.99641 | 0.99447 | 0.99942
CA | 6087_Glenmore - QMAG Tee 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6087_Glenmore - QMAG Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6087_Glenmore - QMAG Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0282 | 1.0253 | 1.0398 | 1.0277 | 1.0247 | 1.0406 | 1.0269 | 1.0285 | 1.04 | 1.0269 | 1.0283 | 1.0404 | 1.0276 | 1.0296 | 1.0433
CA | 6087_Glenmore - QMAG Tee 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA | 6088_QMAG Tee - Parkhurst 66 kV | % of Rated A | 36.63% | 40.51% | 18.94% | 36.97% | 40.91% | 19.08% | 37.56% | 41.38% | 19.34% | 37.79% | 41.65% | 19.45% | 39.17% | 43.16% | 20.07%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Limiting Line Name | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (A) | 127.1045 | 146.2581 | 60.9768 | 128.2739 | 147.6771 | 61.4393 | 130.3172 | 149.375 | 62.2869 | 131.1476 | 150.368 | 62.6439 | 135.911 | 155.8112 | 64.6247
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MVA) | 14.9332 | 17.1339 | 7.223 | 15.0641 | 17.29 | 7.2828 | 15.2915 | 17.5526 | 7.3785 | 15.3892 | 17.6671 | 7.4234 | 15.959 | 18.3274 | 7.6783
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MW) | 14.9134 | 17.1337 | 6.823 | 15.0468 | 17.29 | 6.8902 | 15.2795 | 17.5524 | 7.0078 | 15.3785 | 17.6666 | 7.0582 | 15.9556 | 18.3227 | 7.3536
CA | 6088_QMAG Tee - Parkhurst 66 kV | Power Factor | 0.99864 | 0.99999 | 0.94462 | 0.99882 | 1 | 0.94608 | 0.99919 | 0.99999 | 0.94977 | 0.99928 | 0.99997 | 0.95081 | 0.99977 | 0.99975 | 0.95772
CA | 6088_QMAG Tee - Parkhurst 66 kV | Rating (A) | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322 | 347 | 361 | 322
CA | 6088_QMAG Tee - Parkhurst 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6088_QMAG Tee - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0268 | 1.0236 | 1.036 | 1.0263 | 1.023 | 1.0367 | 1.0255 | 1.0267 | 1.036 | 1.0255 | 1.0266 | 1.0364 | 1.0261 | 1.0277 | 1.0391
CA | 6088_QMAG Tee - Parkhurst 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA | 6089_QMAG Tee - QMAG 66 kV | % of Rated A | 40.3% | 42.93% | 24.13% | 40.61% | 43.28% | 24.26% | 41.15% | 43.67% | 24.54% | 41.36% | 43.92% | 24.64% | 42.6% | 45.25% | 25.24%
CA | 6089_QMAG Tee - QMAG 66 kV | Limiting Line Name | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1 | TR_LINE 20870_1
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (A) | 161.603 | 179.4293 | 89.749 | 162.8318 | 180.9106 | 90.2484 | 165.0114 | 182.5478 | 91.2804 | 165.8695 | 183.5716 | 91.6696 | 170.8176 | 189.1481 | 93.8851
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MVA) | 18.994 | 21.0305 | 10.6321 | 19.1303 | 21.1918 | 10.6987 | 19.3707 | 21.462 | 10.814 | 19.4718 | 21.5798 | 10.864 | 20.0669 | 22.2615 | 11.156
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MW) | 18.9549 | 20.9535 | 10.6193 | 19.0884 | 21.11 | 10.6865 | 19.3213 | 21.3727 | 10.8042 | 19.4204 | 21.487 | 10.8546 | 19.998 | 22.1437 | 11.1501
CA | 6089_QMAG Tee - QMAG 66 kV | Power Factor | 0.99794 | 0.99634 | 0.99879 | 0.99781 | 0.99614 | 0.99886 | 0.99745 | 0.99584 | 0.99909 | 0.99736 | 0.9957 | 0.99914 | 0.99657 | 0.99471 | 0.99948
CA | 6089_QMAG Tee - QMAG 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6089_QMAG Tee - QMAG 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6089_QMAG Tee - QMAG 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0282 | 1.0253 | 1.0363 | 1.0277 | 1.0247 | 1.037 | 1.0269 | 1.0284 | 1.0363 | 1.0269 | 1.0283 | 1.0367 | 1.0276 | 1.0295 | 1.0395
CA | 6089_QMAG Tee - QMAG 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 30.96% | 22.28% | 13.92% | 30.98% | 22.29% | 13.91% | 30.99% | 22.32% | 13.92% | 31% | 22.33% | 13.91% | 31.48% | 22.84% | 14.23%
CA | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 40.8702 | 37.2096 | 22.1347 | 40.8921 | 37.2264 | 22.12 | 40.9101 | 37.2816 | 22.1305 | 40.9139 | 37.2904 | 22.1232 | 41.5556 | 38.1355 | 22.6271
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 4.7245 | 4.3262 | 2.6231 | 4.7247 | 4.3262 | 2.6233 | 4.7248 | 4.3264 | 2.6232 | 4.7248 | 4.3264 | 2.6232 | 4.8114 | 4.4257 | 2.6855
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 4.5945 | 4.2995 | 2.5961 | 4.5945 | 4.2995 | 2.596 | 4.5945 | 4.2996 | 2.596 | 4.5945 | 4.2996 | 2.596 | 4.6819 | 4.3982 | 2.6597
CA | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.97242 | 0.99381 | 0.98968 | 0.97239 | 0.9938 | 0.98962 | 0.97237 | 0.99377 | 0.98967 | 0.97237 | 0.99377 | 0.98963 | 0.97303 | 0.99377 | 0.99041
CA | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6090_Egan's Hill - Raglan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6090_Egan's Hill - Raglan 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0112 | 1.017 | 1.0363 | 1.0107 | 1.0166 | 1.037 | 1.0103 | 1.0151 | 1.0365 | 1.0102 | 1.0149 | 1.0369 | 1.0128 | 1.0152 | 1.0378
CA | 6090_Egan's Hill - Raglan 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV
CA | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 86.07% | 62.01% | 45.69% | 86.1% | 62.04% | 45.65% | 86.14% | 61.75% | 45.67% | 85.47% | 61.23% | 45.41% | 85.74% | 61.58% | 45.6%
CA | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2 | TR_LINE 22265_2
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 123.0792 | 119.6729 | 84.9745 | 123.1218 | 119.7289 | 84.9021 | 123.1857 | 119.1833 | 84.9512 | 122.2238 | 118.1795 | 84.4653 | 122.6046 | 118.8421 | 84.8126
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 14.4789 | 14.0848 | 10.0156 | 14.4797 | 14.0859 | 10.0145 | 14.4809 | 14.0755 | 10.0152 | 14.3705 | 13.9596 | 9.9621 | 14.47 | 14.069 | 10.0137
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 13.3507 | 13.0585 | 9.1917 | 13.3511 | 13.0591 | 9.1913 | 13.3518 | 13.0534 | 9.1916 | 13.2459 | 12.9425 | 9.1395 | 13.3459 | 13.0499 | 9.1908
CA | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.92197 | 0.92701 | 0.9171 | 0.92195 | 0.92698 | 0.91715 | 0.92192 | 0.92725 | 0.91711 | 0.92163 | 0.927 | 0.91676 | 0.9222 | 0.92742 | 0.91717
CA | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186
CA | 6091_Egan's Hill - Gavial 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6091_Egan's Hill - Gavial 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0258 | 1.0264 | 1.0294 | 1.0255 | 1.026 | 1.0302 | 1.025 | 1.03 | 1.0297 | 1.0253 | 1.0302 | 1.0301 | 1.0292 | 1.0325 | 1.0312
CA | 6091_Egan's Hill - Gavial 66 kV | Contingency Outage | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV
CA | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 93.78% | 72.08% | 53.92% | 93.82% | 72.11% | 53.87% | 93.87% | 71.78% | 53.9% | 93.14% | 71.18% | 53.6% | 93.43% | 71.58% | 53.82%
CA | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 123.7962 | 120.3684 | 85.7278 | 123.8386 | 120.4242 | 85.6558 | 123.9023 | 119.8803 | 85.7046 | 122.9422 | 118.8782 | 85.2207 | 123.3231 | 119.5403 | 85.5669
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 14.3051 | 13.9226 | 9.9557 | 14.3058 | 13.9234 | 9.9548 | 14.3067 | 13.9152 | 9.9554 | 14.1996 | 13.8027 | 9.9036 | 14.2982 | 13.9101 | 9.9543
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 13.1852 | 12.902 | 9.1128 | 13.1855 | 12.9024 | 9.1125 | 13.186 | 12.8982 | 9.1127 | 13.0826 | 12.7899 | 9.0615 | 13.1816 | 12.8956 | 9.1122
CA | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.92158 | 0.92647 | 0.9124 | 0.92157 | 0.92645 | 0.91244 | 0.92155 | 0.92664 | 0.91241 | 0.92116 | 0.92629 | 0.91198 | 0.92174 | 0.92676 | 0.91244
CA | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 6093_Gavial - Mt Morgan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6093_Gavial - Mt Morgan 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99158 | 0.99331 | 1.0056 | 0.99127 | 0.99289 | 1.0064 | 0.9908 | 0.99702 | 1.0059 | 0.99128 | 0.99752 | 1.0065 | 0.99509 | 0.99963 | 1.0074
CA | 6093_Gavial - Mt Morgan 66 kV | Contingency Outage | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV | 6008_Biloela - Wowan 66 kV
CA | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 44.47% | 34.97% | 16.1% | 44.93% | 35.33% | 16.24% | 44.94% | 35.38% | 16.25% | 44.95% | 35.39% | 16.24% | 45.68% | 36.04% | 16.54%
CA | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 75.1506 | 83.9229 | 37.6702 | 75.9235 | 84.7827 | 38.0061 | 75.9547 | 84.905 | 38.0254 | 75.9612 | 84.9244 | 38.0091 | 77.1995 | 86.5048 | 38.6962
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 8.8204 | 9.8628 | 4.4346 | 8.9065 | 9.9593 | 4.4775 | 8.9066 | 9.9598 | 4.4775 | 8.9066 | 9.9598 | 4.4775 | 9.078 | 10.1524 | 4.5634
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 8.7597 | 9.7875 | 4.4195 | 8.8446 | 9.8824 | 4.4621 | 8.8447 | 9.8827 | 4.4621 | 8.8447 | 9.8827 | 4.4621 | 9.014 | 10.0725 | 4.5474
CA | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.99223 | 0.99171 | 0.99423 | 0.99218 | 0.99165 | 0.99421 | 0.99217 | 0.99164 | 0.99421 | 0.99217 | 0.99163 | 0.99421 | 0.99211 | 0.99154 | 0.99418
CA | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 6094_Malchi Tee - Malchi 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6094_Malchi Tee - Malchi 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0225 | 1.023 | 1.0297 | 1.0219 | 1.0225 | 1.0304 | 1.0215 | 1.021 | 1.0299 | 1.0214 | 1.0208 | 1.0304 | 1.0243 | 1.0214 | 1.0314
CA | 6094_Malchi Tee - Malchi 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6008_Biloela - Wowan 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6008_Biloela - Wowan 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6008_Biloela - Wowan 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6008_Biloela - Wowan 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6008_Biloela - Wowan 66 kV
CA | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 48.34% | 44.91% | 23.71% | 48.3% | 44.91% | 23.71% | 48.53% | 45.06% | 23.93% | 48.27% | 44.89% | 23.84% | 48.06% | 46.02% | 24.85%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 119.876 | 112.2643 | 52.1627 | 119.7743 | 112.2627 | 52.1689 | 120.3557 | 112.6406 | 52.6431 | 119.7067 | 112.2225 | 52.4515 | 119.1989 | 115.042 | 54.6668
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 14.3065 | 13.4223 | 6.1729 | 14.2912 | 13.4179 | 6.2096 | 14.3545 | 13.5135 | 6.2629 | 14.2783 | 13.4632 | 6.2425 | 14.2765 | 13.8355 | 6.5126
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 13.8824 | 13.1357 | 5.7741 | 13.8673 | 13.1305 | 6.1028 | 13.9264 | 13.2118 | 6.1605 | 13.8533 | 13.163 | 6.1382 | 13.9587 | 13.5064 | 6.4974
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.97035 | 0.97865 | 0.93446 | 0.97034 | 0.97858 | 0.98281 | 0.97017 | 0.97767 | 0.98364 | 0.97024 | 0.9777 | 0.98329 | 0.97774 | 0.97621 | 0.99766
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0413 | 1.0434 | 1.035 | 1.0411 | 1.0431 | 1.0408 | 1.0406 | 1.047 | 1.0403 | 1.0408 | 1.047 | 1.0407 | 1.0451 | 1.0495 | 1.0417
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Contingency Outage | 6097_Egan's Hill - Canning 66 kV | 6097_Egan's Hill - Canning 66 kV | 6004_Glenmore - Rockhampton South 66 kV | 6097_Egan's Hill - Canning 66 kV | 6097_Egan's Hill - Canning 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6097_Egan's Hill - Canning 66 kV | 6097_Egan's Hill - Canning 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6097_Egan's Hill - Canning 66 kV | 6097_Egan's Hill - Canning 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6097_Egan's Hill - Canning 66 kV | 6097_Egan's Hill - Canning 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA | 6096_Egan's Hill - Lakes Creek 66 kV | % of Rated A | 126.4% | 120.7% | 68.74% | 126.9% | 121.3% | 68.86% | 128% | 122% | 69.32% | 127.9% | 122.1% | 69.27% | 130.7% | 125.4% | 70.52%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Limiting Line Name | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19734_1 | TR_LINE 19717_1
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (A) | 405.8142 | 411.673 | 211.0447 | 407.3415 | 413.7344 | 211.3929 | 410.7753 | 415.8835 | 212.8001 | 410.7001 | 416.3059 | 212.6636 | 419.6811 | 427.7829 | 216.4836
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MVA) | 47.4215 | 48.1049 | 24.9761 | 47.5797 | 48.3174 | 25.0352 | 47.9434 | 48.7488 | 25.186 | 47.9374 | 48.7935 | 25.1793 | 49.104 | 50.0042 | 25.641
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MW) | 47.3935 | 48.0981 | 23.8342 | 47.5553 | 48.3129 | 23.9 | 47.9248 | 48.7456 | 24.0806 | 47.9197 | 48.7911 | 24.0752 | 49.1038 | 50.0004 | 24.7643
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Power Factor | 0.99928 | 0.99979 | 0.95377 | 0.99937 | 0.99985 | 0.95415 | 0.99951 | 0.99989 | 0.9556 | 0.99953 | 0.99991 | 0.95564 | 0.99998 | 0.99992 | 0.96536
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Rating (A) | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0199 | 1.0197 | 1.0346 | 1.0194 | 1.0191 | 1.0353 | 1.0186 | 1.0229 | 1.0347 | 1.0186 | 1.0228 | 1.0351 | 1.021 | 1.0078 | 1.0353
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 76.12% | 77.4% | 45.14% | 76.14% | 77.43% | 45.11% | 76.17% | 77.13% | 45.13% | 75.84% | 76.8% | 44.94% | 77.18% | 78.26% | 45.75%
CA | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1
CA | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 188.7802 | 193.5051 | 99.3041 | 188.8273 | 193.5685 | 99.2452 | 188.9056 | 192.8192 | 99.2837 | 188.0828 | 191.9941 | 98.8787 | 191.4088 | 195.6478 | 100.6529
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 22.4025 | 22.9661 | 11.7897 | 22.4026 | 22.9662 | 11.7916 | 22.4026 | 22.9645 | 11.7903 | 22.3077 | 22.8669 | 11.7469 | 22.781 | 23.3541 | 11.9724
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 22.3969 | 22.9634 | 11.4248 | 22.397 | 22.9636 | 11.4248 | 22.3972 | 22.9631 | 11.4248 | 22.3016 | 22.8653 | 11.3764 | 22.7791 | 23.3534 | 11.618
CA | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.99973 | 0.99987 | 0.969 | 0.99973 | 0.99987 | 0.96884 | 0.99973 | 0.99993 | 0.96894 | 0.9997 | 0.99991 | 0.96841 | 0.9999 | 0.99996 | 0.97035
CA | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 6097_Egan's Hill - Canning 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6097_Egan's Hill - Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0367 | 1.0367 | 1.038 | 1.0364 | 1.0364 | 1.0388 | 1.036 | 1.0404 | 1.0383 | 1.0361 | 1.0404 | 1.0387 | 1.0397 | 1.0427 | 1.0399
CA | 6097_Egan's Hill - Canning 66 kV | Contingency Outage | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA | 6100_Boat Creek - ICI 66 kV | % of Rated A | 7.981% | 7.021% | 8.781% | 7.931% | 6.977% | 8.772% | 7.931% | 6.977% | 8.781% | 7.931% | 6.977% | 8.772% | 7.932% | 6.979% | 8.783%
CA | 6100_Boat Creek - ICI 66 kV | Limiting Line Name | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1
CA | 6100_Boat Creek - ICI 66 kV | Loading (A) | 59.0627 | 56.661 | 58.1305 | 58.6879 | 56.3006 | 58.0694 | 58.6881 | 56.307 | 58.1322 | 58.6882 | 56.3072 | 58.0705 | 58.6954 | 56.3172 | 58.1427
CA | 6100_Boat Creek - ICI 66 kV | Loading (MVA) | 6.7584 | 6.4864 | 6.6969 | 6.7571 | 6.4852 | 6.6967 | 6.7571 | 6.4852 | 6.6969 | 6.7571 | 6.4852 | 6.6967 | 6.7571 | 6.4853 | 6.697
CA | 6100_Boat Creek - ICI 66 kV | Loading (MW) | 5.8603 | 5.6274 | 5.8087 | 5.8601 | 5.6273 | 5.8087 | 5.8601 | 5.6273 | 5.8087 | 5.8601 | 5.6273 | 5.8087 | 5.8601 | 5.6273 | 5.8087
CA | 6100_Boat Creek - ICI 66 kV | Power Factor | 0.86705 | 0.86752 | 0.86731 | 0.86719 | 0.86765 | 0.86733 | 0.86719 | 0.86765 | 0.8673 | 0.86719 | 0.86765 | 0.86733 | 0.86719 | 0.86764 | 0.8673
CA | 6100_Boat Creek - ICI 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 6100_Boat Creek - ICI 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6100_Boat Creek - ICI 66 kV | Min Voltage at Constrained Conductor (pu) | 1.001 | 1.0014 | 1.0078 | 1.0072 | 1.0076 | 1.0088 | 1.0072 | 1.0075 | 1.0078 | 1.0072 | 1.0075 | 1.0088 | 1.0071 | 1.0074 | 1.0076
CA | 6100_Boat Creek - ICI 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 3.804% | 3.675% | 3.904% | 3.779% | 3.652% | 3.9% | 3.779% | 3.652% | 3.904% | 3.779% | 3.652% | 3.9% | 3.78% | 3.653% | 3.905%
CA | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 28.1477 | 29.6597 | 25.8464 | 27.9676 | 29.469 | 25.819 | 27.9677 | 29.4725 | 25.8471 | 27.9678 | 29.4725 | 25.8194 | 27.9712 | 29.4778 | 25.8518
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 3.2195 | 3.3938 | 2.9765 | 3.2188 | 3.393 | 2.9764 | 3.2188 | 3.393 | 2.9765 | 3.2188 | 3.393 | 2.9764 | 3.2188 | 3.393 | 2.9766
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 2.7631 | 2.9114 | 2.5561 | 2.763 | 2.9113 | 2.5561 | 2.763 | 2.9113 | 2.5561 | 2.763 | 2.9113 | 2.5561 | 2.763 | 2.9114 | 2.5561
CA | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.85801 | 0.85764 | 0.85858 | 0.8582 | 0.85783 | 0.85861 | 0.8582 | 0.85783 | 0.85857 | 0.8582 | 0.85783 | 0.85861 | 0.8582 | 0.85782 | 0.85857
CA | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 6102_Boat Creek - Yarwun 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6102_Boat Creek - Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0006 | 1.001 | 1.0074 | 1.0068 | 1.0072 | 1.0084 | 1.0068 | 1.0071 | 1.0074 | 1.0068 | 1.0071 | 1.0084 | 1.0066 | 1.0069 | 1.0072
CA | 6102_Boat Creek - Yarwun 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 84.84% | 76.49% | 77.62% | 84.04% | 75.76% | 77.31% | 84.04% | 75.77% | 77.39% | 84.04% | 75.77% | 77.31% | 84.05% | 75.78% | 77.41%
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 237.5651 | 234.8109 | 213.4485 | 235.3095 | 232.5807 | 212.6097 | 235.3105 | 232.6061 | 212.8285 | 235.311 | 232.6068 | 212.6134 | 235.3383 | 232.6462 | 212.8651
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.5209 | 27.2068 | 24.8868 | 27.5154 | 27.2014 | 24.8849 | 27.5154 | 27.2015 | 24.8854 | 27.5154 | 27.2015 | 24.8849 | 27.5155 | 27.2016 | 24.8855
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 26.3498 | 26.0497 | 23.8316 | 26.346 | 26.046 | 23.8303 | 26.346 | 26.046 | 23.8306 | 26.346 | 26.046 | 23.8303 | 26.3461 | 26.0461 | 23.8307
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 0.95745 | 0.95747 | 0.9576 | 0.9575 | 0.95752 | 0.95762 | 0.9575 | 0.95752 | 0.95762 | 0.9575 | 0.95752 | 0.95762 | 0.9575 | 0.95752 | 0.95761
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0051 | 1.0054 | 1.0126 | 1.0147 | 1.015 | 1.0165 | 1.0147 | 1.0149 | 1.0155 | 1.0147 | 1.0149 | 1.0165 | 1.0146 | 1.0147 | 1.0153
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Contingency Outage | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV
CA | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 85.1% | 76.69% | 77.75% | 84.56% | 76.21% | 77.67% | 84.56% | 76.22% | 77.75% | 84.56% | 76.22% | 77.67% | 84.57% | 76.23% | 77.77%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 238.2692 | 235.4371 | 213.8172 | 236.7788 | 233.9595 | 213.5958 | 236.7798 | 233.986 | 213.8231 | 236.7803 | 233.9867 | 213.5997 | 236.8087 | 234.0277 | 213.8612
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.0542 | 26.7468 | 24.464 | 27.0542 | 26.7467 | 24.464 | 27.0542 | 26.7467 | 24.464 | 27.0542 | 26.7467 | 24.464 | 27.0542 | 26.7467 | 24.464
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 25.9446 | 25.6497 | 23.4607 | 25.9445 | 25.6497 | 23.4607 | 25.9445 | 25.6497 | 23.4607 | 25.9445 | 25.6497 | 23.4607 | 25.9445 | 25.6497 | 23.4607
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 0.95898 | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99312 | 0.99364 | 1.0008 | 0.99937 | 0.99992 | 1.0018 | 0.99937 | 0.99981 | 1.0007 | 0.99936 | 0.9998 | 1.0018 | 0.99924 | 0.99963 | 1.0005
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 102.9% | 73.61% | 55.33% | 103.1% | 73.76% | 55.14% | 103.2% | 73.81% | 55.37% | 103.1% | 73.79% | 55.14% | 104.7% | 74.96% | 55.97%
CA | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1
CA | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 373.6793 | 401.1882 | 255.0854 | 374.3174 | 401.9809 | 254.2039 | 374.5259 | 402.2618 | 255.2478 | 374.3708 | 402.1585 | 254.218 | 380.12 | 408.5449 | 258.0376
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 44.4231 | 47.6289 | 30.2193 | 44.4971 | 47.7207 | 30.1668 | 44.5217 | 47.7503 | 30.2783 | 44.5034 | 47.738 | 30.168 | 45.1755 | 48.4809 | 30.6022
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 43.8307 | 47.2231 | 28.1994 | 43.907 | 47.3173 | 29.5197 | 43.9323 | 47.3481 | 28.2412 | 43.9118 | 47.3345 | 29.5197 | 44.6214 | 48.1085 | 28.6164
CA | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.98609 | 0.99098 | 0.93241 | 0.98616 | 0.99105 | 0.97811 | 0.98619 | 0.99108 | 0.93198 | 0.98613 | 0.99105 | 0.97807 | 0.98717 | 0.99183 | 0.93435
CA | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 6109_Gladstone North - Clinton 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6109_Gladstone North - Clinton 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0394 | 1.0379 | 1.0363 | 1.0394 | 1.0378 | 1.0379 | 1.0394 | 1.0377 | 1.0376 | 1.0394 | 1.0377 | 1.0379 | 1.0391 | 1.0374 | 1.0374
CA | 6109_Gladstone North - Clinton 66 kV | Contingency Outage | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV
CA | 6110_Port Curtis 66 kV | % of Rated A | 68.67% | 47.42% | 38.56% | 68.8% | 47.53% | 35.66% | 68.85% | 47.57% | 38.61% | 68.82% | 47.56% | 35.67% | 69.98% | 48.41% | 38.98%
CA | 6110_Port Curtis 66 kV | Limiting Line Name | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1
CA | 6110_Port Curtis 66 kV | Loading (A) | 249.2692 | 258.4541 | 177.751 | 249.7583 | 259.0518 | 164.4 | 249.9197 | 259.255 | 178.0103 | 249.8198 | 259.1939 | 164.4256 | 254.0378 | 263.8349 | 179.6847
CA | 6110_Port Curtis 66 kV | Loading (MVA) | 29.5706 | 30.6037 | 21.0576 | 29.6271 | 30.6725 | 19.4817 | 29.646 | 30.694 | 21.1162 | 29.6344 | 30.6869 | 19.4845 | 30.1236 | 31.2223 | 21.3094
CA | 6110_Port Curtis 66 kV | Loading (MW) | 26.7305 | 27.7322 | 15.2245 | 26.796 | 27.813 | 16.3965 | 26.8177 | 27.8394 | 15.2603 | 26.8 | 27.8277 | 16.3964 | 27.4093 | 28.4925 | 15.5827
CA | 6110_Port Curtis 66 kV | Power Factor | 0.90232 | 0.90447 | 0.72182 | 0.9028 | 0.90506 | 0.84055 | 0.90295 | 0.90529 | 0.72151 | 0.90271 | 0.90512 | 0.84043 | 0.90822 | 0.91083 | 0.73008
CA | 6110_Port Curtis 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 6110_Port Curtis 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6110_Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0373 | 1.0354 | 1.0355 | 1.0373 | 1.0353 | 1.0365 | 1.0372 | 1.0352 | 1.0369 | 1.0373 | 1.0352 | 1.0365 | 1.0369 | 1.0348 | 1.0366
CA | 6110_Port Curtis 66 kV | Contingency Outage | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV
CA | 6111_Gladstone North - Port Curtis 66 kV | % of Rated A | 91.27% | 65.51% | 49.04% | 91.43% | 65.64% | 49.15% | 91.47% | 65.68% | 49.07% | 91.44% | 65.66% | 49.15% | 92.82% | 66.69% | 49.6%
CA | 6111_Gladstone North - Port Curtis 66 kV | Limiting Line Name | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1 | TR_LINE 60721_1
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (A) | 331.3188 | 357.029 | 226.0883 | 331.873 | 357.7181 | 226.5763 | 332.0539 | 357.9634 | 226.2104 | 331.9173 | 357.8719 | 226.5873 | 336.929 | 363.445 | 228.661
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MVA) | 39.3505 | 42.3471 | 26.7525 | 39.4146 | 42.4267 | 26.8676 | 39.436 | 42.4525 | 26.802 | 39.4198 | 42.4417 | 26.8684 | 40.0054 | 43.0895 | 27.0866
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MW) | 38.9747 | 42.1182 | 25.2654 | 39.0406 | 42.1995 | 26.4376 | 39.0624 | 42.2261 | 25.3013 | 39.0446 | 42.2143 | 26.4376 | 39.6577 | 42.8838 | 25.6249
CA | 6111_Gladstone North - Port Curtis 66 kV | Power Factor | 0.99003 | 0.99424 | 0.94381 | 0.99008 | 0.99429 | 0.98368 | 0.9901 | 0.99432 | 0.9434 | 0.99006 | 0.99429 | 0.98364 | 0.99089 | 0.99489 | 0.94543
CA | 6111_Gladstone North - Port Curtis 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 6111_Gladstone North - Port Curtis 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6111_Gladstone North - Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0384 | 1.0369 | 1.0351 | 1.0384 | 1.0368 | 1.037 | 1.0384 | 1.0367 | 1.0365 | 1.0384 | 1.0367 | 1.037 | 1.0381 | 1.0364 | 1.0362
CA | 6111_Gladstone North - Port Curtis 66 kV | Contingency Outage | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV
CA | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 70.07% | 77.05% | 38.21% | 71.06% | 78.32% | 38.57% | 72.37% | 81.63% | 39.24% | 73.01% | 82.52% | 39.49% | 76.26% | 87.07% | 40.94%
CA | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 50003_1 | TR_LINE 112499_1
CA | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 264.8782 | 319.7759 | 128.7571 | 268.5983 | 325.0385 | 129.9697 | 273.5537 | 338.7448 | 132.2427 | 275.9682 | 342.4491 | 133.076 | 288.2459 | 361.3606 | 137.9755
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 26.5506 | 30.7372 | 14.466 | 26.809 | 31.0409 | 14.5545 | 27.2218 | 31.5626 | 14.7821 | 27.3936 | 31.7666 | 14.8714 | 28.3479 | 33.3298 | 15.3751
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 26.5284 | 30.6578 | 14.3912 | 26.7834 | 30.9528 | 14.5269 | 27.2079 | 31.4477 | 14.7529 | 27.3779 | 31.6445 | 14.8434 | 28.3088 | 33.114 | 15.3538
CA | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.99917 | 0.99741 | 0.99481 | 0.99904 | 0.99716 | 0.99809 | 0.99949 | 0.99636 | 0.99801 | 0.99943 | 0.99616 | 0.9981 | 0.99862 | 0.99353 | 0.9986
CA | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 6298_Tanby - Yeppoon 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6298_Tanby - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 0.87677 | 0.84074 | 0.98261 | 0.87304 | 0.8353 | 0.97938 | 0.87042 | 0.81496 | 0.9776 | 0.86825 | 0.81135 | 0.97734 | 0.86022 | 0.80096 | 0.97455
CA | 6298_Tanby - Yeppoon 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6075_Keppel - Farnborough 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV
CA | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 66.8% | 78.78% | 40.62% | 67.65% | 79.98% | 40.74% | 68.96% | 83.37% | 41.16% | 69.52% | 84.2% | 41.21% | 72.57% | 88.51% | 42.38%
CA | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | 6310_Lakes Creek | 6310_Lakes Creek | TR_LINE 20950_1 | 6310_Lakes Creek | 6310_Lakes Creek | TR_LINE 20950_1 | 6310_Lakes Creek | 6310_Lakes Creek | TR_LINE 20950_1 | 6310_Lakes Creek | 6310_Lakes Creek | TR_LINE 20950_1 | 6310_Lakes Creek | 6310_Lakes Creek | TR_LINE 20950_1
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 267.8675 | 329.3135 | 151.1061 | 271.2934 | 334.3229 | 151.5463 | 276.5258 | 348.472 | 153.1185 | 278.768 | 351.9654 | 153.3052 | 290.9997 | 369.9523 | 157.6431
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 30.9722 | 38.2129 | 17.921 | 31.3411 | 38.7443 | 17.9863 | 32.1335 | 39.9896 | 18.1622 | 32.3848 | 40.3663 | 18.1912 | 33.634 | 42.3615 | 18.7076
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 30.5808 | 37.2317 | 17.6954 | 30.9132 | 37.6853 | 17.765 | 31.5665 | 38.6721 | 17.9536 | 31.7902 | 38.9826 | 17.9852 | 33.0017 | 40.6866 | 18.5562
CA | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.98736 | 0.97432 | 0.98736 | 0.98635 | 0.97267 | 0.98765 | 0.98236 | 0.96705 | 0.98847 | 0.98164 | 0.96572 | 0.98863 | 0.9812 | 0.96046 | 0.99187
CA | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 6310_Lakes Creek - Berserker 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6310_Lakes Creek - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0114 | 1.015 | 1.0372 | 1.0106 | 1.0137 | 1.038 | 1.0165 | 1.0038 | 1.0374 | 1.0162 | 1.0032 | 1.0378 | 1.011 | 1.0016 | 1.0378
CA | 6310_Lakes Creek - Berserker 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 29.26% | 26.11% | 29.46% | 34.09% | 30.47% | 34.35% | 34.09% | 30.47% | 34.38% | 34.09% | 30.47% | 34.35% | 34.09% | 30.47% | 34.39%
CA | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 260.1328 | 256.9223 | 247.1957 | 303.038 | 299.7841 | 288.1693 | 303.0394 | 299.8179 | 288.4753 | 303.04 | 299.8188 | 288.1746 | 303.0763 | 299.8712 | 288.5266
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 62.067 | 61.302 | 58.5701 | 72.2008 | 71.4271 | 68.6475 | 72.2008 | 71.4278 | 68.6534 | 72.2009 | 71.4278 | 68.6476 | 72.2016 | 71.4289 | 68.6544
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 56.3518 | 55.6854 | 53.2163 | 65.43 | 64.7632 | 62.2946 | 65.43 | 64.7632 | 62.2952 | 65.43 | 64.7632 | 62.2946 | 65.4301 | 64.7633 | 62.2953
CA | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.90792 | 0.90838 | 0.90859 | 0.90622 | 0.9067 | 0.90746 | 0.90622 | 0.90669 | 0.90739 | 0.90622 | 0.90669 | 0.90746 | 0.90621 | 0.90668 | 0.90738
CA | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 7290_Boat Creek - Yarwun 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 7290_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0435 | 1.0435 | 1.0362 | 1.042 | 1.042 | 1.0418 | 1.042 | 1.0419 | 1.0408 | 1.0419 | 1.0419 | 1.0418 | 1.0418 | 1.0417 | 1.0406
CA | 7290_Boat Creek - Yarwun 132 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 29.26% | 26.11% | 29.46% | 34.08% | 30.46% | 34.34% | 34.08% | 30.46% | 34.38% | 34.08% | 30.46% | 34.34% | 34.08% | 30.47% | 34.38%
CA | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 260.084 | 256.8748 | 247.1525 | 302.9715 | 299.7192 | 288.1097 | 302.9729 | 299.753 | 288.4154 | 302.9735 | 299.7539 | 288.1149 | 303.0097 | 299.8063 | 288.4666
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 62.0589 | 61.2942 | 58.5631 | 72.1894 | 71.4161 | 68.6374 | 72.1894 | 71.4167 | 68.6433 | 72.1895 | 71.4168 | 68.6375 | 72.1902 | 71.4178 | 68.6443
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 56.3507 | 55.6843 | 53.2154 | 65.4286 | 64.7618 | 62.2933 | 65.4286 | 64.7618 | 62.2939 | 65.4286 | 64.7618 | 62.2933 | 65.4286 | 64.7619 | 62.294
CA | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.90802 | 0.90848 | 0.90868 | 0.90635 | 0.90682 | 0.90757 | 0.90635 | 0.90682 | 0.9075 | 0.90635 | 0.90682 | 0.90757 | 0.90634 | 0.9068 | 0.90749
CA | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 7291_Boat Creek - Yarwun 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 7291_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0436 | 1.0436 | 1.0363 | 1.0421 | 1.0421 | 1.0419 | 1.042 | 1.042 | 1.0409 | 1.042 | 1.042 | 1.0419 | 1.0419 | 1.0418 | 1.0407
CA | 7291_Boat Creek - Yarwun 132 kV | Contingency Outage | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV
CA | 6026_Moura - Theodore 66 kV | % of Rated A | 15.39% | 14.02% | 11.95% | 15.39% | 14.02% | 11.95% | 15.39% | 14.02% | 11.95% | 15.26% | 13.9% | 11.84% | 15.54% | 14.15% | 12.05%
CA | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1
CA | 6026_Moura - Theodore 66 kV | Loading (A) | 112.2101 | 109.787 | 84.8642 | 112.2203 | 109.7884 | 84.8153 | 112.2214 | 109.7982 | 84.8385 | 111.2237 | 108.8343 | 84.0935 | 113.2575 | 110.7827 | 85.5749
CA | 6026_Moura - Theodore 66 kV | Loading (MVA) | 12.6301 | 12.2864 | 9.7163 | 12.6301 | 12.2864 | 9.7161 | 12.6302 | 12.2865 | 9.7162 | 12.527 | 12.1862 | 9.6373 | 12.7334 | 12.3868 | 9.7951
CA | 6026_Moura - Theodore 66 kV | Loading (MW) | 12.2231 | 11.8929 | 9.4312 | 12.2231 | 11.8929 | 9.4311 | 12.2231 | 11.8929 | 9.4312 | 12.1248 | 11.7973 | 9.3554 | 12.3214 | 11.9886 | 9.5069
CA | 6026_Moura - Theodore 66 kV | Power Factor | 0.96777 | 0.96797 | 0.97065 | 0.96777 | 0.96797 | 0.97066 | 0.96777 | 0.96797 | 0.97066 | 0.96789 | 0.96808 | 0.97074 | 0.96764 | 0.96785 | 0.97057
CA | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
CA | 6026_Moura - Theodore 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA | 6026_Moura - Theodore 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98461 | 0.97896 | 1.0015 | 0.98452 | 0.97894 | 1.0021 | 0.98451 | 0.97886 | 1.0018 | 0.98523 | 0.97948 | 1.0025 | 0.98348 | 0.97808 | 1.0013
CA | 6026_Moura - Theodore 66 kV | Contingency Outage | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6091_Egan's Hill - Gavial 66 kV
FN | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 44.54% | 34.2% | 25.15% | 44.54% | 34.2% | 25.15% | 44.64% | 34.28% | 25.21% | 44.34% | 34.05% | 25.04% | 45.13% | 34.65% | 25.48%
FN | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 186.1842 | 153.9164 | 102.6151 | 186.1842 | 153.9164 | 102.6151 | 186.5965 | 154.2541 | 102.8376 | 185.3597 | 153.2411 | 102.17 | 188.6596 | 155.9432 | 103.9506
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 44.6426 | 36.9126 | 24.6181 | 44.6426 | 36.9126 | 24.6181 | 44.7413 | 36.9935 | 24.6715 | 44.4451 | 36.7508 | 24.5115 | 45.2354 | 37.3982 | 24.9382
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 44.2559 | 36.7297 | 24.594 | 44.2559 | 36.7297 | 24.594 | 44.3514 | 36.8089 | 24.647 | 44.0648 | 36.5712 | 24.488 | 44.8292 | 37.2051 | 24.9119
FN | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99121 | 0.99483 | 0.99877 | 0.99121 | 0.99483 | 0.99877 | 0.99116 | 0.99479 | 0.99876 | 0.99131 | 0.99489 | 0.9988 | 0.9909 | 0.99462 | 0.99869
FN | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408
FN | 7206 Woree-Cairns Terminal-Cairns City | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7206 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 1.0474 | 1.0479 | 1.0488 | 1.0474 | 1.0479 | 1.0488 | 1.0474 | 1.0479 | 1.0488 | 1.0474 | 1.048 | 1.0488 | 1.0473 | 1.0479 | 1.0487
FN | 7206 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City
FN | 7227 Woree-Cairns Terminal-Cairns City | % of Rated A | 44.58% | 34.23% | 25.15% | 44.58% | 34.23% | 25.15% | 44.68% | 34.3% | 25.21% | 44.38% | 34.08% | 25.05% | 45.18% | 34.68% | 25.48%
FN | 7227 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1 | TR_LINE 3959_1
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (A) | 186.3517 | 154.0168 | 102.6303 | 186.3521 | 154.0171 | 102.6304 | 186.7659 | 154.3557 | 102.8531 | 185.5265 | 153.3413 | 102.1855 | 188.836 | 156.0492 | 103.9669
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 44.6675 | 36.9255 | 24.6176 | 44.6675 | 36.9255 | 24.6176 | 44.7664 | 37.0065 | 24.671 | 44.4696 | 36.7635 | 24.511 | 45.2615 | 37.4117 | 24.9377
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MW) | 44.2563 | 36.73 | 24.5932 | 44.2563 | 36.73 | 24.5932 | 44.3519 | 36.8092 | 24.6461 | 44.0652 | 36.5715 | 24.4872 | 44.8297 | 37.2054 | 24.911
FN | 7227 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99067 | 0.99449 | 0.99877 | 0.99067 | 0.99449 | 0.99877 | 0.99062 | 0.99445 | 0.99876 | 0.99078 | 0.99456 | 0.9988 | 0.99035 | 0.99427 | 0.99869
FN | 7227 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408
FN | 7227 Woree-Cairns Terminal-Cairns City | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7227 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 1.0471 | 1.0477 | 1.0486 | 1.0471 | 1.0477 | 1.0486 | 1.0471 | 1.0477 | 1.0486 | 1.0471 | 1.0477 | 1.0486 | 1.047 | 1.0476 | 1.0486
FN | 7227 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City
FN | 7332_Cairns North 132 kV | % of Rated A | 47.37% | 47.74% | 32.59% | 47.69% | 48.07% | 32.78% | 48.01% | 48.39% | 32.96% | 48.25% | 48.64% | 33.1% | 49.62% | 50.04% | 33.88%
FN | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN | 7332_Cairns North 132 kV | Loading (A) | 224.0726 | 237.261 | 145.3617 | 225.5814 | 238.8856 | 146.1768 | 227.0929 | 240.513 | 146.9937 | 228.2282 | 241.7355 | 147.6074 | 234.689 | 248.6935 | 151.1032
FN | 7332_Cairns North 132 kV | Loading (MVA) | 53.7914 | 56.9574 | 34.8959 | 54.1536 | 57.3474 | 35.0915 | 54.5164 | 57.7381 | 35.2876 | 54.789 | 58.0316 | 35.435 | 56.34 | 59.7019 | 36.2742
FN | 7332_Cairns North 132 kV | Loading (MW) | 53.5709 | 56.8538 | 32.7742 | 53.9488 | 57.2551 | 33.0047 | 54.3268 | 57.6564 | 33.2353 | 54.6103 | 57.9574 | 33.4082 | 56.2171 | 59.6637 | 34.3882
FN | 7332_Cairns North 132 kV | Power Factor | 0.9959 | 0.99818 | 0.9392 | 0.99622 | 0.99839 | 0.94053 | 0.99652 | 0.99858 | 0.94184 | 0.99674 | 0.99872 | 0.9428 | 0.99782 | 0.99936 | 0.94801
FN | 7332_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 7332_Cairns North 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7332_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
FN | 7332_Cairns North 132 kV | Contingency Outage | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV
FN | 7333_Cairns North 132 kV | % of Rated A | 47.35% | 47.72% | 32.57% | 47.67% | 48.05% | 32.75% | 47.99% | 48.38% | 32.94% | 48.23% | 48.62% | 33.07% | 49.6% | 50.03% | 33.86%
FN | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN | 7333_Cairns North 132 kV | Loading (A) | 223.9488 | 237.1727 | 145.2676 | 225.4611 | 238.8026 | 146.0804 | 226.9761 | 240.4355 | 146.895 | 228.1143 | 241.6622 | 147.507 | 234.5928 | 248.6466 | 150.9936
FN | 7333_Cairns North 132 kV | Loading (MVA) | 53.7617 | 56.9362 | 34.8733 | 54.1247 | 57.3275 | 35.0684 | 54.4884 | 57.7195 | 35.2639 | 54.7616 | 58.014 | 35.4109 | 56.3169 | 59.6907 | 36.2479
FN | 7333_Cairns North 132 kV | Loading (MW) | 53.575 | 56.8585 | 32.7763 | 53.953 | 57.2599 | 33.0069 | 54.331 | 57.6613 | 33.2374 | 54.6146 | 57.9623 | 33.4104 | 56.2217 | 59.6689 | 34.3904
FN | 7333_Cairns North 132 kV | Power Factor | 0.99653 | 0.99863 | 0.93987 | 0.99683 | 0.99882 | 0.94121 | 0.99711 | 0.99899 | 0.94253 | 0.99731 | 0.99911 | 0.94351 | 0.99831 | 0.99964 | 0.94876
FN | 7333_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 7333_Cairns North 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7333_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
FN | 7333_Cairns North 132 kV | Contingency Outage | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV
FN | 3CRO_Croydon 66 kV | % of Rated A | 12.55% | 12% | 8.924% | 12.57% | 12.03% | 8.725% | 12.57% | 12.03% | 8.725% | 12.38% | 11.85% | 8.606% | 12.57% | 12.03% | 8.731%
FN | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN | 3CRO_Croydon 66 kV | Loading (A) | 57.3404 | 58.4506 | 42.1192 | 57.4269 | 58.5774 | 41.1833 | 57.427 | 58.5775 | 41.1834 | 56.5656 | 57.6956 | 40.6213 | 57.4585 | 58.6079 | 41.2099
FN | 3CRO_Croydon 66 kV | Loading (MVA) | 6.8344 | 6.9639 | 5.0139 | 6.8414 | 6.9741 | 4.9267 | 6.8414 | 6.9741 | 4.9267 | 6.7396 | 6.87 | 4.8598 | 6.844 | 6.9765 | 4.9292
FN | 3CRO_Croydon 66 kV | Loading (MW) | 6.0757 | 6.209 | 4.0716 | 6.0764 | 6.21 | 4.068 | 6.0764 | 6.21 | 4.068 | 5.9707 | 6.1019 | 3.9972 | 6.0766 | 6.2103 | 4.0681
FN | 3CRO_Croydon 66 kV | Power Factor | 0.88899 | 0.8916 | 0.81206 | 0.88818 | 0.89044 | 0.82569 | 0.88818 | 0.89044 | 0.82569 | 0.8859 | 0.8882 | 0.8225 | 0.88788 | 0.89017 | 0.8253
FN | 3CRO_Croydon 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 3CRO_Croydon 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3CRO_Croydon 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0426 | 1.0422 | 1.0413 | 1.0421 | 1.0415 | 1.0465 | 1.0421 | 1.0415 | 1.0465 | 1.0423 | 1.0416 | 1.0465 | 1.042 | 1.0413 | 1.0463
FN | 3CRO_Croydon 66 kV | Contingency Outage | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex)
FN | 3NOR_Normanton 66 kV | % of Rated A | 10.13% | 9.716% | 6.764% | 10.15% | 9.734% | 6.651% | 10.15% | 9.734% | 6.651% | 9.949% | 9.546% | 6.524% | 10.15% | 9.739% | 6.654%
FN | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN | 3NOR_Normanton 66 kV | Loading (A) | 46.3024 | 47.3165 | 31.9264 | 46.3629 | 47.4064 | 31.3934 | 46.363 | 47.4064 | 31.3934 | 45.4669 | 46.4898 | 30.7917 | 46.3851 | 47.4281 | 31.4079
FN | 3NOR_Normanton 66 kV | Loading (MVA) | 5.5258 | 5.6437 | 3.8229 | 5.5313 | 5.6518 | 3.7709 | 5.5313 | 5.6518 | 3.7709 | 5.4259 | 5.5441 | 3.6992 | 5.5333 | 5.6537 | 3.7723
FN | 3NOR_Normanton 66 kV | Loading (MW) | 5.2462 | 5.3539 | 3.6196 | 5.2463 | 5.3542 | 3.6193 | 5.2463 | 5.3542 | 3.6193 | 5.1463 | 5.252 | 3.5511 | 5.2464 | 5.3543 | 3.6193
FN | 3NOR_Normanton 66 kV | Power Factor | 0.94939 | 0.94866 | 0.9468 | 0.94849 | 0.94735 | 0.9598 | 0.94849 | 0.94735 | 0.9598 | 0.94848 | 0.94732 | 0.95999 | 0.94816 | 0.94704 | 0.95944
FN | 3NOR_Normanton 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 3NOR_Normanton 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3NOR_Normanton 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0293 | 1.029 | 1.0328 | 1.0292 | 1.0288 | 1.0339 | 1.0292 | 1.0288 | 1.0339 | 1.0295 | 1.0291 | 1.034 | 1.0292 | 1.0288 | 1.0338
FN | 3NOR_Normanton 66 kV | Contingency Outage | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex)
FN | 4KID_Ross - Kidston 132 kV | % of Rated A | 21.35% | 19.91% | 20.96% | 21.93% | 20.44% | 20.49% | 21.93% | 20.44% | 20.49% | 21.85% | 20.36% | 20.44% | 21.96% | 20.47% | 20.51%
FN | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN | 4KID_Ross - Kidston 132 kV | Loading (A) | 75.7926 | 76.6587 | 72.7381 | 77.8413 | 78.6922 | 71.1125 | 77.8414 | 78.6923 | 71.1125 | 77.5528 | 78.3932 | 70.9441 | 77.9585 | 78.8096 | 71.1709
FN | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 18.1911 | 18.3989 | 17.4588 | 18.6832 | 18.8874 | 17.0687 | 18.6832 | 18.8874 | 17.0687 | 18.614 | 18.8156 | 17.0283 | 18.7113 | 18.9155 | 17.0827
FN | 4KID_Ross - Kidston 132 kV | Loading (MW) | 12.0902 | 12.331 | 8.6208 | 9.3586 | 9.706 | 6.3109 | 9.3586 | 9.706 | 6.3109 | 9.2445 | 9.589 | 6.2362 | 9.4504 | 9.7944 | 6.3868
FN | 4KID_Ross - Kidston 132 kV | Power Factor | 0.66462 | 0.6702 | 0.49378 | 0.50091 | 0.51389 | 0.36974 | 0.50091 | 0.51389 | 0.36974 | 0.49664 | 0.50963 | 0.36623 | 0.50507 | 0.5178 | 0.37388
FN | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347
FN | 4KID_Ross - Kidston 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 4KID_Ross - Kidston 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498 | 1.0498
FN | 4KID_Ross - Kidston 132 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV
FN | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 12.36% | 11.09% | 8.062% | 12% | 10.74% | 8.428% | 12% | 10.74% | 8.428% | 11.89% | 10.64% | 8.388% | 11.97% | 10.72% | 8.402%
FN | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 36.84 | 38.1417 | 27.5732 | 35.7469 | 36.9473 | 28.8227 | 35.7469 | 36.9472 | 28.8227 | 35.4269 | 36.6101 | 28.6874 | 35.6809 | 36.8879 | 28.7343
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 8.7805 | 9.0865 | 6.6818 | 8.7241 | 9.0096 | 7.0788 | 8.7241 | 9.0096 | 7.0788 | 8.6478 | 8.9294 | 7.0464 | 8.7056 | 8.9927 | 7.0555
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 7.7806 | 8.1477 | 0.97549 | 7.778 | 8.145 | 5.0569 | 7.778 | 8.145 | 5.0569 | 7.6711 | 8.0356 | 4.9857 | 7.7781 | 8.145 | 5.0567
FN | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.88057 | 0.89084 | 0.14356 | 0.8863 | 0.89849 | 0.71097 | 0.8863 | 0.89849 | 0.71097 | 0.88188 | 0.89445 | 0.70419 | 0.8882 | 0.9002 | 0.71331
FN | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342
FN | 7216_4GEO (Georgetown) 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7216_4GEO (Georgetown) 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0425 | 1.042 | 1.0599 | 1.0674 | 1.0666 | 1.0742 | 1.0674 | 1.0666 | 1.0742 | 1.0677 | 1.0668 | 1.0743 | 1.0672 | 1.0663 | 1.074
FN | 7216_4GEO (Georgetown) 132 kV | Contingency Outage | MOSS_7496 | MOSS_7496 | 3CRO_Croydon 66 kV | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496
FN | 3AT1_Atherton No 1 66 kV | % of Rated A | 40.1% | 44.57% | 29.83% | 40.12% | 44.52% | 29.83% | 40.3% | 44.72% | 29.94% | 40.29% | 44.7% | 29.94% | 41.05% | 45.63% | 30.44%
FN | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1
FN | 3AT1_Atherton No 1 66 kV | Loading (A) | 219.7585 | 249.5933 | 155.4029 | 219.8707 | 249.2955 | 155.4336 | 220.8455 | 250.4153 | 155.9893 | 220.7704 | 250.3071 | 155.9683 | 224.9811 | 255.5494 | 158.5707
FN | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 26.2589 | 29.8133 | 18.7964 | 26.2595 | 29.7922 | 18.7961 | 26.3558 | 29.8977 | 18.857 | 26.3554 | 29.8969 | 18.8573 | 26.7995 | 30.4211 | 19.1438
FN | 3AT1_Atherton No 1 66 kV | Loading (MW) | 26.2587 | 29.8048 | 18.5318 | 26.2593 | 29.7907 | 18.5319 | 26.3557 | 29.8959 | 18.595 | 26.3553 | 29.8953 | 18.595 | 26.7993 | 30.4175 | 18.9149
FN | 3AT1_Atherton No 1 66 kV | Power Factor | 0.99999 | 0.99881 | 0.98581 | 0.99999 | 0.99928 | 0.98583 | 0.99999 | 0.99925 | 0.986 | 0.99999 | 0.99925 | 0.98598 | 0.99999 | 0.99909 | 0.98794
FN | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 3AT1_Atherton No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3AT1_Atherton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0445 | 1.0449 | 1.0578 | 1.044 | 1.0452 | 1.0575 | 1.0432 | 1.0442 | 1.0572 | 1.0436 | 1.0446 | 1.0573 | 1.0413 | 1.0412 | 1.0558
FN | 3AT1_Atherton No 1 66 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3MO2_Mossman No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3MO2_Mossman No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3MO2_Mossman No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3MO2_Mossman No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3MO2_Mossman No 2 66 kV
FN | 3AT2_Atherton No 2 66 kV | % of Rated A | 40.1% | 44.57% | 29.66% | 40.12% | 44.52% | 29.66% | 40.3% | 44.72% | 29.77% | 40.29% | 44.7% | 29.77% | 41.05% | 45.63% | 30.29%
FN | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1
FN | 3AT2_Atherton No 2 66 kV | Loading (A) | 219.7579 | 249.5919 | 154.5074 | 219.8701 | 249.294 | 154.5408 | 220.8449 | 250.4138 | 155.11 | 220.7698 | 250.3057 | 155.0838 | 224.9805 | 255.548 | 157.8367
FN | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 26.259 | 29.8134 | 18.6041 | 26.2596 | 29.7923 | 18.604 | 26.3559 | 29.8978 | 18.6662 | 26.3555 | 29.897 | 18.6662 | 26.7996 | 30.4211 | 18.9689
FN | 3AT2_Atherton No 2 66 kV | Loading (MW) | 26.2588 | 29.8049 | 18.513 | 26.2594 | 29.7908 | 18.5131 | 26.3558 | 29.896 | 18.5763 | 26.3554 | 29.8954 | 18.5762 | 26.7994 | 30.4176 | 18.8967
FN | 3AT2_Atherton No 2 66 kV | Power Factor | 0.99999 | 0.99881 | 0.99504 | 0.99999 | 0.99928 | 0.99505 | 0.99999 | 0.99925 | 0.99512 | 0.99999 | 0.99925 | 0.99512 | 0.99999 | 0.99909 | 0.99614
FN | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 3AT2_Atherton No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3AT2_Atherton No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0445 | 1.0449 | 1.0529 | 1.044 | 1.0452 | 1.0527 | 1.0432 | 1.0442 | 1.0523 | 1.0436 | 1.0446 | 1.0525 | 1.0413 | 1.0412 | 1.0509
FN | 3AT2_Atherton No 2 66 kV | Contingency Outage | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV
FN | 3CHI_Chillagoe 66 kV | % of Rated A | 2.32% | 2.198% | 2.505% | 2.319% | 2.197% | 2.505% | 2.317% | 2.195% | 2.504% | 2.318% | 2.195% | 2.505% | 2.312% | 2.189% | 2.501%
FN | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1
FN | 3CHI_Chillagoe 66 kV | Loading (A) | 12.7149 | 12.7272 | 13.0533 | 12.7088 | 12.7196 | 13.0506 | 12.6997 | 12.7088 | 13.0471 | 12.702 | 12.7115 | 13.0487 | 12.6673 | 12.6768 | 13.0298
FN | 3CHI_Chillagoe 66 kV | Loading (MVA) | 1.5169 | 1.5198 | 1.5791 | 1.5154 | 1.518 | 1.5785 | 1.5133 | 1.5154 | 1.5777 | 1.5138 | 1.5161 | 1.578 | 1.5057 | 1.5079 | 1.5736
FN | 3CHI_Chillagoe 66 kV | Loading (MW) | 0.41822 | 0.44609 | 0.25713 | 0.41821 | 0.44609 | 0.25713 | 0.41821 | 0.44608 | 0.25713 | 0.41821 | 0.44609 | 0.25713 | 0.4182 | 0.44607 | 0.25712
FN | 3CHI_Chillagoe 66 kV | Power Factor | 0.27571 | 0.29352 | 0.16283 | 0.27597 | 0.29386 | 0.1629 | 0.27636 | 0.29436 | 0.16298 | 0.27626 | 0.29423 | 0.16294 | 0.27775 | 0.29583 | 0.1634
FN | 3CHI_Chillagoe 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
FN | 3CHI_Chillagoe 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3CHI_Chillagoe 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0436 | 1.0446 | 1.0583 | 1.0431 | 1.044 | 1.058 | 1.0424 | 1.0431 | 1.0578 | 1.0425 | 1.0433 | 1.0579 | 1.0398 | 1.0405 | 1.0565
FN | 3CHI_Chillagoe 66 kV | Contingency Outage | 3HLA_Helenvale 66 kV | 3HLA_Helenvale 66 kV | MOSS_7496 | 3HLA_Helenvale 66 kV | 3HLA_Helenvale 66 kV | MOSS_7496 | 3HLA_Helenvale 66 kV | 3HLA_Helenvale 66 kV | MOSS_7496 | 3HLA_Helenvale 66 kV | 3HLA_Helenvale 66 kV | MOSS_7496 | 3HLA_Helenvale 66 kV | MOSS_7496 | MOSS_7496
FN | 3COO_Cooktown 66 kV | % of Rated A | 10.01% | 9.757% | 6.735% | 10.02% | 9.768% | 6.739% | 10.04% | 9.732% | 6.743% | 9.81% | 9.513% | 6.596% | 9.986% | 9.764% | 6.753%
FN | 3COO_Cooktown 66 kV | Limiting Line Name | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1
FN | 3COO_Cooktown 66 kV | Loading (A) | 39.9377 | 40.4918 | 24.9208 | 39.9779 | 40.5363 | 24.9331 | 40.0407 | 40.3892 | 24.9499 | 39.1433 | 39.479 | 24.4058 | 39.8443 | 40.5216 | 24.9879
FN | 3COO_Cooktown 66 kV | Loading (MVA) | 4.5779 | 4.6228 | 2.8943 | 4.5774 | 4.6229 | 2.8943 | 4.5776 | 4.6226 | 2.8944 | 4.4817 | 4.5258 | 2.8335 | 4.5777 | 4.6229 | 2.8944
FN | 3COO_Cooktown 66 kV | Loading (MW) | 4.5414 | 4.5862 | 2.8757 | 4.5413 | 4.5863 | 2.8757 | 4.5414 | 4.586 | 2.8757 | 4.4462 | 4.4898 | 2.8155 | 4.5412 | 4.5863 | 2.8757
FN | 3COO_Cooktown 66 kV | Power Factor | 0.98569 | 0.98562 | 0.98967 | 0.98576 | 0.98561 | 0.98966 | 0.98573 | 0.98567 | 0.98965 | 0.98585 | 0.98578 | 0.98984 | 0.98573 | 0.98561 | 0.98962
FN | 3COO_Cooktown 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
FN | 3COO_Cooktown 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3COO_Cooktown 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0027 | 0.9987 | 1.016 | 1.0016 | 0.99762 | 1.0155 | 1.0001 | 1.0012 | 1.0148 | 1.0016 | 1.0028 | 1.0156 | 1.005 | 0.99798 | 1.0133
FN | 3COO_Cooktown 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 3AT2_Atherton No 2 66 kV | 7200_Craiglie No 2 132 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV
FN | 3DIM_Dimbulah 66 kV | % of Rated A | 21.77% | 19.08% | 12.72% | 21.77% | 19.07% | 12.72% | 21.79% | 19.08% | 12.72% | 21.78% | 19.07% | 12.72% | 22.17% | 19.44% | 12.94%
FN | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 88168_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 88168_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 88168_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 88168_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 88168_1
FN | 3DIM_Dimbulah 66 kV | Loading (A) | 47.4485 | 51.3165 | 32.1788 | 47.4686 | 51.2857 | 32.1806 | 47.4958 | 51.3122 | 32.185 | 47.4852 | 51.3045 | 32.1833 | 48.3383 | 52.2989 | 32.7483
FN | 3DIM_Dimbulah 66 kV | Loading (MVA) | 5.6121 | 6.0886 | 3.8395 | 5.6122 | 6.0884 | 3.8394 | 5.6124 | 6.0886 | 3.8393 | 5.6123 | 6.0885 | 3.8393 | 5.7004 | 6.189 | 3.9026
FN | 3DIM_Dimbulah 66 kV | Loading (MW) | 5.6055 | 6.0758 | 3.7432 | 5.6055 | 6.0758 | 3.7432 | 5.6056 | 6.0758 | 3.7432 | 5.6056 | 6.0758 | 3.7432 | 5.6918 | 6.1735 | 3.8142
FN | 3DIM_Dimbulah 66 kV | Power Factor | 0.99868 | 0.99773 | 0.97491 | 0.99866 | 0.99776 | 0.97493 | 0.99864 | 0.99774 | 0.97497 | 0.99865 | 0.99774 | 0.97495 | 0.99834 | 0.99732 | 0.97736
FN | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253
FN | 3DIM_Dimbulah 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3DIM_Dimbulah 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0343 | 1.0375 | 1.0437 | 1.0339 | 1.0381 | 1.0437 | 1.0333 | 1.0376 | 1.0435 | 1.0335 | 1.0378 | 1.0435 | 1.0312 | 1.0348 | 1.0424
FN | 3DIM_Dimbulah 66 kV | Contingency Outage | MOSS_7496 | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | MOSS_7496 | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | MOSS_7496 | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | MOSS_7496 | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | MOSS_7496 | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN | 3EVE_Evelyn 66 kV | % of Rated A | 14.94% | 12.16% | 8.226% | 14.94% | 12.16% | 8.227% | 14.59% | 11.85% | 8.043% | 14.58% | 11.84% | 8.043% | 14.61% | 11.87% | 8.05%
FN | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN | 3EVE_Evelyn 66 kV | Loading (A) | 25.2439 | 29.2968 | 19.3319 | 25.2533 | 29.302 | 19.3342 | 24.651 | 28.5475 | 18.9021 | 24.6449 | 28.538 | 18.9004 | 24.687 | 28.6048 | 18.9181
FN | 3EVE_Evelyn 66 kV | Loading (MVA) | 3.0045 | 3.3919 | 2.3233 | 3.0041 | 3.481 | 2.3231 | 2.9307 | 3.3889 | 2.2706 | 2.9309 | 3.3891 | 2.2708 | 2.9293 | 3.3875 | 2.2689
FN | 3EVE_Evelyn 66 kV | Loading (MW) | 2.8826 | 3.3913 | 2.1085 | 2.8826 | 3.3928 | 2.1085 | 2.8039 | 3.2961 | 2.048 | 2.8039 | 3.2961 | 2.048 | 2.8039 | 3.2962 | 2.048
FN | 3EVE_Evelyn 66 kV | Power Factor | 0.95943 | 0.99985 | 0.90757 | 0.95954 | 0.97467 | 0.90766 | 0.95675 | 0.97264 | 0.90197 | 0.95667 | 0.97257 | 0.90189 | 0.95719 | 0.97303 | 0.90264
FN | 3EVE_Evelyn 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 3EVE_Evelyn 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3EVE_Evelyn 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0411 | 1.0128 | 1.0513 | 1.0406 | 1.0392 | 1.0511 | 1.04 | 1.0384 | 1.0508 | 1.0403 | 1.0388 | 1.051 | 1.038 | 1.0359 | 1.0491
FN | 3EVE_Evelyn 66 kV | Contingency Outage | 3MTG_Mt Garnet 66 kV | 3AT2_Atherton No 2 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV
FN | 3HLA_Helenvale 66 kV | % of Rated A | 11.87% | 11.67% | 7.789% | 11.88% | 11.68% | 7.793% | 11.9% | 11.64% | 7.798% | 11.67% | 11.41% | 7.652% | 11.84% | 11.68% | 7.81%
FN | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1
FN | 3HLA_Helenvale 66 kV | Loading (A) | 44.8572 | 46.556 | 28.8195 | 44.9056 | 46.6059 | 28.8337 | 44.9741 | 46.441 | 28.853 | 44.0959 | 45.545 | 28.3127 | 44.7556 | 46.5894 | 28.8967
FN | 3HLA_Helenvale 66 kV | Loading (MVA) | 5.2538 | 5.4354 | 3.3623 | 5.2539 | 5.4356 | 3.3623 | 5.2542 | 5.4348 | 3.3623 | 5.1565 | 5.3357 | 3.3016 | 5.2534 | 5.4355 | 3.3625
FN | 3HLA_Helenvale 66 kV | Loading (MW) | 5.2538 | 5.4352 | 3.3594 | 5.2539 | 5.4354 | 3.3594 | 5.2542 | 5.4346 | 3.3594 | 5.1564 | 5.3357 | 3.2992 | 5.2534 | 5.4353 | 3.3594
FN | 3HLA_Helenvale 66 kV | Power Factor | 0.99998 | 0.99984 | 0.99899 | 0.99998 | 0.99983 | 0.99898 | 0.99997 | 0.99986 | 0.99897 | 0.99997 | 0.99993 | 0.99912 | 0.99999 | 0.99983 | 0.99895
FN | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370
FN | 3HLA_Helenvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3HLA_Helenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0235 | 1.0203 | 1.0205 | 1.0224 | 1.0193 | 1.02 | 1.0209 | 1.0227 | 1.0194 | 1.0219 | 1.0238 | 1.0201 | 1.0258 | 1.0196 | 1.0179
FN | 3HLA_Helenvale 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 3AT2_Atherton No 2 66 kV | 7200_Craiglie No 2 132 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV
FN | 3MO1_Mossman No 1 66 kV | % of Rated A | 122.8% | 119.4% | 77.7% | 123.3% | 119.9% | 77.96% | 123.8% | 120.5% | 78.23% | 123.3% | 119.9% | 77.97% | 126.4% | 123.2% | 79.55%
FN | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN | 3MO1_Mossman No 1 66 kV | Loading (A) | 162.0506 | 199.3147 | 123.5457 | 162.7262 | 200.1779 | 123.9603 | 163.4364 | 201.16 | 124.383 | 162.7789 | 200.2679 | 123.9705 | 166.8075 | 205.7816 | 126.4875
FN | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 19.2526 | 23.5594 | 14.8663 | 19.3211 | 23.6514 | 14.9119 | 19.3883 | 23.7411 | 14.9567 | 19.3189 | 23.6496 | 14.9107 | 19.7341 | 24.1982 | 15.1847
FN | 3MO1_Mossman No 1 66 kV | Loading (MW) | 18.4655 | 23.1708 | 13.3412 | 18.5449 | 23.2706 | 13.3984 | 18.6244 | 23.3707 | 13.4556 | 18.545 | 23.2708 | 13.3984 | 19.0215 | 23.8706 | 13.7416
FN | 3MO1_Mossman No 1 66 kV | Power Factor | 0.95895 | 0.98337 | 0.89724 | 0.95966 | 0.98377 | 0.89833 | 0.96043 | 0.98426 | 0.89946 | 0.95977 | 0.98385 | 0.8984 | 0.96373 | 0.98633 | 0.90479
FN | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN | 3MO1_Mossman No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3MO1_Mossman No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0388 | 1.0333 | 1.0524 | 1.0381 | 1.0328 | 1.052 | 1.0372 | 1.0317 | 1.0516 | 1.0377 | 1.0323 | 1.0519 | 1.0344 | 1.0279 | 1.0499
FN | 3MO1_Mossman No 1 66 kV | Contingency Outage | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV
FN | 3MO2_Mossman No 2 66 kV | % of Rated A | 102.5% | 88.42% | 57.02% | 102.9% | 88.78% | 57.19% | 103.3% | 89.18% | 57.37% | 102.9% | 88.81% | 57.2% | 105.3% | 91.07% | 58.27%
FN | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1)
FN | 3MO2_Mossman No 2 66 kV | Loading (A) | 173.1858 | 211.3337 | 132.8534 | 173.8522 | 212.1766 | 133.2635 | 174.5538 | 213.1396 | 133.6818 | 173.9061 | 212.2678 | 133.2739 | 177.8745 | 217.6555 | 135.763
FN | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 20.7298 | 25.3003 | 16.0189 | 20.7989 | 25.3937 | 16.0647 | 20.8668 | 25.485 | 16.1096 | 20.7967 | 25.392 | 16.0634 | 21.2164 | 25.9496 | 16.3382
FN | 3MO2_Mossman No 2 66 kV | Loading (MW) | 19.9062 | 24.8994 | 14.3874 | 19.9867 | 25.0008 | 14.4451 | 20.0672 | 25.1026 | 14.5028 | 19.9868 | 25.0011 | 14.4451 | 20.4695 | 25.611 | 14.7913
FN | 3MO2_Mossman No 2 66 kV | Power Factor | 0.96021 | 0.9841 | 0.89809 | 0.96088 | 0.98447 | 0.89912 | 0.96162 | 0.98494 | 0.9002 | 0.961 | 0.98455 | 0.8992 | 0.96473 | 0.9869 | 0.90526
FN | 3MO2_Mossman No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
FN | 3MO2_Mossman No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3MO2_Mossman No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.047 | 1.0471 | 1.0547 | 1.0464 | 1.0468 | 1.0545 | 1.0456 | 1.0458 | 1.0541 | 1.046 | 1.0462 | 1.0543 | 1.0433 | 1.0427 | 1.0527
FN | 3MO2_Mossman No 2 66 kV | Contingency Outage | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV
FN | 3MTG_Mt Garnet 66 kV | % of Rated A | 25.81% | 19.04% | 12.8% | 25.83% | 19.04% | 12.8% | 25.44% | 18.71% | 12.6% | 25.43% | 18.71% | 12.59% | 25.5% | 18.77% | 12.61%
FN | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1
FN | 3MTG_Mt Garnet 66 kV | Loading (A) | 43.6223 | 45.8898 | 30.0752 | 43.6443 | 45.8949 | 30.0809 | 42.998 | 45.1023 | 29.5988 | 42.9834 | 45.0837 | 29.5944 | 43.1025 | 45.2383 | 29.6397
FN | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 5.1368 | 5.4018 | 3.5952 | 5.1367 | 5.4018 | 3.5951 | 5.0575 | 5.3046 | 3.5366 | 5.0576 | 5.3047 | 3.5367 | 5.0575 | 5.3044 | 3.5358
FN | 3MTG_Mt Garnet 66 kV | Loading (MW) | 5.1307 | 5.3923 | 3.5188 | 5.1308 | 5.3923 | 3.5188 | 5.0511 | 5.2943 | 3.4577 | 5.051 | 5.2942 | 3.4577 | 5.0514 | 5.2947 | 3.4578
FN | 3MTG_Mt Garnet 66 kV | Power Factor | 0.99882 | 0.99823 | 0.97874 | 0.99884 | 0.99824 | 0.97878 | 0.99872 | 0.99805 | 0.97769 | 0.99871 | 0.99803 | 0.97766 | 0.99879 | 0.99815 | 0.97794
FN | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 3MTG_Mt Garnet 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3MTG_Mt Garnet 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0255 | 1.025 | 1.0433 | 1.025 | 1.0249 | 1.0431 | 1.0244 | 1.0242 | 1.0429 | 1.0248 | 1.0247 | 1.0431 | 1.0219 | 1.0211 | 1.0412
FN | 3MTG_Mt Garnet 66 kV | Contingency Outage | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV
FN | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 9.705% | 7.889% | 5.96% | 9.707% | 7.891% | 5.96% | 9.402% | 7.609% | 5.814% | 9.401% | 7.608% | 5.814% | 9.407% | 7.618% | 5.814%
FN | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 16.4017 | 19.0119 | 14.0055 | 16.4043 | 19.018 | 14.0057 | 15.8895 | 18.3387 | 13.6628 | 15.888 | 18.3351 | 13.6628 | 15.8985 | 18.3603 | 13.6626
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 1.9521 | 2.2599 | 1.6832 | 1.9514 | 2.2593 | 1.6828 | 1.889 | 2.177 | 1.6412 | 1.8895 | 2.1774 | 1.6415 | 1.8865 | 2.1743 | 1.6386
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 1.6519 | 2.0284 | 1.2717 | 1.6519 | 2.0284 | 1.2717 | 1.5732 | 1.9317 | 1.2111 | 1.5732 | 1.9317 | 1.2111 | 1.5732 | 1.9317 | 1.2111
FN | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.84621 | 0.89756 | 0.75552 | 0.84648 | 0.89782 | 0.75568 | 0.8328 | 0.88734 | 0.73795 | 0.8326 | 0.88716 | 0.73782 | 0.83393 | 0.88844 | 0.73913
FN | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 3RA1_Ravenshoe No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 3RA1_Ravenshoe No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0411 | 1.0398 | 1.0513 | 1.0406 | 1.0392 | 1.0511 | 1.04 | 1.0384 | 1.0508 | 1.0403 | 1.0388 | 1.051 | 1.038 | 1.0359 | 1.0491
FN | 3RA1_Ravenshoe No 1 66 kV | Contingency Outage | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV
FN | 7200_Craiglie No 2 132 kV | % of Rated A | 30.42% | 29.27% | 23.68% | 30.73% | 29.6% | 23.85% | 31.13% | 30.01% | 24.06% | 30.9% | 29.77% | 23.94% | 31.51% | 30.37% | 24.25%
FN | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN | 7200_Craiglie No 2 132 kV | Loading (A) | 137.5003 | 139.3245 | 101.1217 | 138.9076 | 140.874 | 101.844 | 140.7058 | 142.8422 | 102.7567 | 139.6576 | 141.7102 | 102.2126 | 142.4222 | 144.5471 | 103.5366
FN | 7200_Craiglie No 2 132 kV | Loading (MVA) | 33.3897 | 33.5316 | 24.9575 | 33.7147 | 33.8925 | 25.1301 | 34.1253 | 34.3354 | 25.3469 | 33.8824 | 34.077 | 25.217 | 34.4728 | 34.6589 | 25.5096
FN | 7200_Craiglie No 2 132 kV | Loading (MW) | 31.4961 | 31.7557 | 20.5334 | 31.8656 | 32.1626 | 20.7648 | 32.3393 | 32.6706 | 21.0605 | 32.0535 | 32.3682 | 20.8755 | 32.7534 | 33.0739 | 21.3171
FN | 7200_Craiglie No 2 132 kV | Power Factor | 0.94329 | 0.94704 | 0.82273 | 0.94515 | 0.94896 | 0.82629 | 0.94766 | 0.95151 | 0.83089 | 0.94602 | 0.94985 | 0.82783 | 0.95012 | 0.95427 | 0.83565
FN | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 7200_Craiglie No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7200_Craiglie No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0618 | 1.0523 | 1.0795 | 1.0613 | 1.052 | 1.0793 | 1.0605 | 1.051 | 1.0789 | 1.0608 | 1.0514 | 1.0791 | 1.0583 | 1.0483 | 1.0776
FN | 7200_Craiglie No 2 132 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV
FN | 7201_Craiglie No 1 132 kV | % of Rated A | 29.8% | 28.71% | 22.5% | 30.12% | 29.05% | 22.68% | 30.54% | 29.49% | 22.91% | 30.29% | 29.24% | 22.77% | 30.93% | 29.87% | 23.11%
FN | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
FN | 7201_Craiglie No 1 132 kV | Loading (A) | 134.6741 | 136.6562 | 96.0832 | 136.1445 | 138.2742 | 96.858 | 138.053 | 140.3578 | 97.8336 | 136.9224 | 139.1654 | 97.2436 | 139.824 | 142.1814 | 98.6648
FN | 7201_Craiglie No 1 132 kV | Loading (MVA) | 32.6516 | 32.836 | 23.6999 | 32.9915 | 33.2129 | 23.8856 | 33.4301 | 33.6851 | 24.1179 | 33.1653 | 33.4127 | 23.9767 | 33.7852 | 34.0368 | 24.2939
FN | 7201_Craiglie No 1 132 kV | Loading (MW) | 31.5944 | 31.8543 | 20.5527 | 31.9646 | 32.2618 | 20.7843 | 32.4386 | 32.7696 | 21.0806 | 32.1536 | 32.4661 | 20.8953 | 32.8614 | 33.1776 | 21.3393
FN | 7201_Craiglie No 1 132 kV | Power Factor | 0.96762 | 0.9701 | 0.86721 | 0.96887 | 0.97137 | 0.87016 | 0.97034 | 0.97282 | 0.87406 | 0.96949 | 0.97167 | 0.87148 | 0.97266 | 0.97476 | 0.87838
FN | 7201_Craiglie No 1 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 7201_Craiglie No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7201_Craiglie No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0604 | 1.0509 | 1.0789 | 1.0599 | 1.0506 | 1.0786 | 1.0591 | 1.0497 | 1.0782 | 1.0594 | 1.0501 | 1.0784 | 1.0568 | 1.047 | 1.077
FN | 7201_Craiglie No 1 132 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
FN | 7285_4LAK (Lakeland) 132kV | % of Rated A | 8.546% | 8.097% | 8.444% | 8.719% | 8.277% | 8.518% | 8.894% | 8.465% | 8.594% | 8.818% | 8.383% | 8.565% | 8.893% | 8.478% | 8.615%
FN | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN | 7285_4LAK (Lakeland) 132kV | Loading (A) | 43.4142 | 44.0479 | 40.5311 | 44.2915 | 45.0289 | 40.8863 | 45.181 | 46.0474 | 41.2512 | 44.7936 | 45.6013 | 41.1131 | 45.1754 | 46.118 | 41.3529
FN | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 10.6176 | 10.8445 | 10.1409 | 10.8267 | 11.0795 | 10.2272 | 11.0372 | 11.1101 | 10.3153 | 10.9456 | 11.2156 | 10.2823 | 10.9451 | 11.3204 | 10.3324
FN | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 6.8113 | 7.1457 | 4.3834 | 7.1687 | 7.539 | 4.6104 | 7.5265 | 7.9328 | 4.8374 | 7.3382 | 7.7342 | 4.7192 | 7.5264 | 7.9308 | 4.8368
FN | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.64151 | 0.65893 | 0.43226 | 0.66213 | 0.68044 | 0.4508 | 0.68193 | 0.71402 | 0.46895 | 0.67043 | 0.68959 | 0.45896 | 0.68765 | 0.70057 | 0.46812
FN | 7285_4LAK (Lakeland) 132kV | Rating (A) | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480
FN | 7285_4LAK (Lakeland) 132kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | 7285_4LAK (Lakeland) 132kV | Min Voltage at Constrained Conductor (pu) | 1.0697 | 1.0768 | 1.0943 | 1.0692 | 1.0762 | 1.0941 | 1.0685 | 1.0553 | 1.0937 | 1.0688 | 1.0758 | 1.0939 | 1.0597 | 1.0736 | 1.0928
FN | 7285_4LAK (Lakeland) 132kV | Contingency Outage | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | 3DIM_Dimbulah 66 kV | MOSS_7496 | MOSS_7496 | MOSS_7496 | MOSS_7496 | 3RA1_Ravenshoe No 1 66 kV | MOSS_7496 | MOSS_7496
FN | MOSS_7496 | % of Rated A | 26.65% | 27.45% | 20.01% | 26.68% | 27.47% | 20.02% | 26.81% | 27.62% | 20.11% | 26.71% | 27.49% | 20.03% | 27.34% | 28.15% | 20.46%
FN | MOSS_7496 | Limiting Line Name | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a
FN | MOSS_7496 | Loading (A) | 101.0212 | 101.5772 | 64.4451 | 101.1019 | 101.6454 | 64.4687 | 101.6244 | 102.1893 | 64.7589 | 101.2207 | 101.7203 | 64.4822 | 103.6274 | 104.168 | 65.876
FN | MOSS_7496 | Loading (MVA) | 24.2874 | 24.1898 | 15.9088 | 24.2881 | 24.1904 | 15.9089 | 24.3882 | 24.2907 | 15.9719 | 24.3025 | 24.1955 | 15.9085 | 24.8024 | 24.6872 | 16.2244
FN | MOSS_7496 | Loading (MW) | 24.2433 | 24.1504 | 15.9054 | 24.2436 | 24.1507 | 15.9055 | 24.3438 | 24.2491 | 15.9689 | 24.2566 | 24.1545 | 15.9054 | 24.7505 | 24.6406 | 16.2224
FN | MOSS_7496 | Power Factor | 0.99811 | 0.9983 | 0.99978 | 0.99809 | 0.99829 | 0.99979 | 0.99811 | 0.99821 | 0.99981 | 0.99803 | 0.99823 | 0.9998 | 0.99783 | 0.99804 | 0.99988
FN | MOSS_7496 | Rating (A) | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322
FN | MOSS_7496 | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN | MOSS_7496 | Min Voltage at Constrained Conductor (pu) | 1.0511 | 1.0411 | 1.0794 | 1.0503 | 1.0405 | 1.079 | 1.0492 | 1.0392 | 1.0784 | 1.0497 | 1.0399 | 1.0788 | 1.0464 | 1.0361 | 1.0769
FN | MOSS_7496 | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
MK | 231_Carmila 33 kV | % of Rated A | 25.97% | 27.95% | 15.18% | 25.98% | 27.97% | 15.19% | 26% | 28.01% | 15.2% | 0% | 0% | 0% | 0% | 0% | 0%
MK | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 11379_1 | TR_LINE 11379_1 | TR_LINE 11379_1 | TR_LINE 11379_1 | TR_LINE 11379_1 | TR_LINE 11379_1 | TR_LINE 11379_1 | TR_LINE 11379_1 | TR_LINE 11379_1 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Loading (A) | 39.469 | 57.2904 | 29.9105 | 39.4917 | 57.3446 | 29.9219 | 39.5211 | 57.4172 | 29.9405 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Loading (MVA) | 2.1487 | 3.0086 | 1.6872 | 2.1488 | 3.0089 | 1.6873 | 2.1489 | 3.0092 | 1.6872 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Loading (MW) | 2.0822 | 2.9124 | 1.6504 | 2.0822 | 2.9125 | 1.6504 | 2.0822 | 2.9127 | 1.6503 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Power Factor | 0.96891 | 0.96802 | 0.97799 | 0.96888 | 0.96798 | 0.97797 | 0.96885 | 0.96793 | 0.97796 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Rating (A) | 152 | 205 | 197 | 152 | 205 | 197 | 152 | 205 | 197 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Min Voltage at Constrained Conductor (pu) | 0.9521 | 0.91809 | 0.98672 | 0.95159 | 0.91729 | 0.98637 | 0.95094 | 0.91623 | 0.98573 | 0 | 0 | 0 | 0 | 0 | 0
MK | 231_Carmila 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV | 0% | 0% | 0% | 0% | 0% | 0%
MK | 3045_Sarina No 1 33 kV | % of Rated A | 74.67% | 83.42% | 45.5% | 75.11% | 83.96% | 45.76% | 75.17% | 84.05% | 45.78% | 25.49% | 30.17% | 25.02% | 25.61% | 30.59% | 25.16%
MK | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 12173_1 | TR_LINE 113451_1 | TR_LINE 11547_1 | TR_LINE 12173_1 | TR_LINE 113451_1 | TR_LINE 11547_1
MK | 3045_Sarina No 1 33 kV | Loading (A) | 282.2474 | 347.0277 | 189.7259 | 283.9219 | 349.2563 | 190.804 | 284.1502 | 349.6632 | 190.8933 | 76.2129 | 123.11 | 76.3013 | 76.5872 | 124.7918 | 76.7244
MK | 3045_Sarina No 1 33 kV | Loading (MVA) | 15.7348 | 18.8783 | 10.8953 | 15.8199 | 18.9844 | 10.9537 | 15.8207 | 18.9862 | 10.9522 | 4.5858 | 7.3447 | 4.605 | 4.6032 | 7.4447 | 4.6244
MK | 3045_Sarina No 1 33 kV | Loading (MW) | 14.829 | 17.7469 | 10.37 | 14.9102 | 17.8425 | 10.4257 | 14.9104 | 17.843 | 10.4255 | 3.2575 | 7.1345 | 3.2987 | 3.3162 | 7.2378 | 3.3586
MK | 3045_Sarina No 1 33 kV | Power Factor | 0.94243 | 0.94007 | 0.95178 | 0.9425 | 0.93985 | 0.95179 | 0.94246 | 0.93979 | 0.95191 | 0.71022 | 0.97076 | 0.71618 | 0.72028 | 0.97159 | 0.72612
MK | 3045_Sarina No 1 33 kV | Rating (A) | 378 | 416 | 417 | 378 | 416 | 417 | 378 | 416 | 417 | 299 | 408 | 305 | 299 | 408 | 305
MK | 3045_Sarina No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 3045_Sarina No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 0.97509 | 0.95144 | 1.0045 | 0.97458 | 0.95068 | 1.0042 | 0.97385 | 0.94967 | 1.0036 | 1.0527 | 1.0424 | 1.0559 | 1.0515 | 1.0423 | 1.0545
MK | 3045_Sarina No 1 33 kV | Contingency Outage | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 342_South Mackay 33 kV | 3046_Rosella 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 3046_Rosella 33 kV | 342_South Mackay 33 kV
MK | 3046_Rosella 33 kV | % of Rated A | 92.79% | 88.26% | 83.29% | 92.48% | 88.11% | 83.06% | 92.42% | 88.07% | 82.96% | 93.6% | 89.11% | 83.55% | 94.36% | 89.88% | 83.86%
MK | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1
MK | 3046_Rosella 33 kV | Loading (A) | 379.5005 | 360.9772 | 340.6486 | 378.245 | 360.3587 | 339.7184 | 377.9948 | 360.2044 | 339.3227 | 382.817 | 364.4516 | 341.7397 | 385.9179 | 367.5899 | 342.9837
MK | 3046_Rosella 33 kV | Loading (MVA) | 22.929 | 21.775 | 20.3714 | 22.853 | 21.7369 | 20.3157 | 22.8351 | 21.7235 | 20.2897 | 22.9426 | 21.8277 | 20.4986 | 23.1129 | 22.002 | 20.5616
MK | 3046_Rosella 33 kV | Loading (MW) | 22.3983 | 21.0969 | 19.479 | 22.3122 | 21.0555 | 19.4137 | 22.3353 | 21.115 | 19.4408 | 22.3263 | 21.1063 | 19.4163 | 22.7147 | 21.5009 | 19.7476
MK | 3046_Rosella 33 kV | Power Factor | 0.97685 | 0.96886 | 0.9562 | 0.97633 | 0.96865 | 0.9556 | 0.97811 | 0.97199 | 0.95816 | 0.97314 | 0.96695 | 0.9472 | 0.98277 | 0.97723 | 0.96041
MK | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409
MK | 3046_Rosella 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 3046_Rosella 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0569 | 1.0553 | 1.0462 | 1.0569 | 1.0552 | 1.0462 | 1.0568 | 1.055 | 1.046 | 1.0484 | 1.0477 | 1.0493 | 1.0477 | 1.0471 | 1.0487
MK | 3046_Rosella 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 3047_Sarina No 2 33 kV | % of Rated A | 74.29% | 82.72% | 45.2% | 74.72% | 83.25% | 45.47% | 74.75% | 83.34% | 45.5% | 0.1269% | 0.1148% | 0.1165% | 0.1269% | 0.1148% | 0.1164%
MK | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11141_1 | TR_LINE 11141_1 | TR_LINE 11141_1 | TR_LINE 11141_1 | TR_LINE 11141_1 | TR_LINE 11141_1
MK | 3047_Sarina No 2 33 kV | Loading (A) | 282.2849 | 345.7646 | 189.849 | 283.9537 | 347.9734 | 190.9671 | 284.0685 | 348.3621 | 191.0897 | 0.90891 | 0.91578 | 0.9097 | 0.9083 | 0.91576 | 0.90919
MK | 3047_Sarina No 2 33 kV | Loading (MVA) | 15.9211 | 19.1673 | 10.9732 | 16.0083 | 19.2772 | 11.0346 | 16.0045 | 19.2796 | 11.0349 | 0.054472 | 0.055299 | 0.054567 | 0.054399 | 0.055296 | 0.054505
MK | 3047_Sarina No 2 33 kV | Loading (MW) | 14.9625 | 17.9469 | 10.43 | 15.0453 | 18.0451 | 10.4867 | 15.045 | 18.046 | 10.4867 | 2.6938e-06 | 2.7348e-06 | 2.6986e-06 | 2.6902e-06 | 2.7346e-06 | 2.6955e-06
MK | 3047_Sarina No 2 33 kV | Power Factor | 0.93979 | 0.93633 | 0.95049 | 0.93984 | 0.93608 | 0.95035 | 0.94005 | 0.93602 | 0.95032 | 4.9424e-05 | 4.9425e-05 | 4.9425e-05 | 4.9424e-05 | 4.9424e-05 | 4.9425e-05
MK | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 716 | 798 | 781 | 716 | 798 | 781
MK | 3047_Sarina No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 3047_Sarina No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98489 | 0.96753 | 1.01 | 0.98445 | 0.96689 | 1.0097 | 0.98382 | 0.96592 | 1.0091 | 1.0485 | 1.0565 | 1.0494 | 1.0478 | 1.0564 | 1.0488
MK | 3047_Sarina No 2 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 342_South Mackay 33 kV | 347_Mt Bassett 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 347_Mt Bassett 33 kV | 342_South Mackay 33 kV
MK | 3053_Mt Bassett 33 kV | % of Rated A | 77.26% | 65.06% | 37.51% | 77.25% | 65.06% | 37.51% | 77.79% | 65.5% | 38.28% | 77.05% | 65.79% | 37.93% | 79.16% | 66.68% | 38.93%
MK | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK | 3053_Mt Bassett 33 kV | Loading (A) | 181.5505 | 211.4538 | 121.1678 | 181.5385 | 211.4557 | 121.1633 | 182.8115 | 212.8816 | 123.6523 | 181.0713 | 213.823 | 122.5231 | 186.0288 | 216.7105 | 125.7464
MK | 3053_Mt Bassett 33 kV | Loading (MVA) | 10.7071 | 12.5326 | 7.2545 | 10.7071 | 12.5326 | 7.2545 | 10.7953 | 12.6359 | 7.3152 | 10.7079 | 12.535 | 7.2553 | 10.9733 | 12.8454 | 7.4348
MK | 3053_Mt Bassett 33 kV | Loading (MW) | 10.5399 | 12.316 | 7.1619 | 10.5399 | 12.316 | 7.1619 | 10.6261 | 12.4168 | 7.2213 | 10.5398 | 12.3181 | 7.1626 | 10.7994 | 12.6198 | 7.3385
MK | 3053_Mt Bassett 33 kV | Power Factor | 0.98438 | 0.98272 | 0.98723 | 0.98438 | 0.98272 | 0.98723 | 0.98433 | 0.98266 | 0.98716 | 0.9843 | 0.9827 | 0.98722 | 0.98415 | 0.98244 | 0.98706
MK | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323
MK | 3053_Mt Bassett 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 3053_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0235 | 1.0271 | 1.0421 | 1.0236 | 1.0271 | 1.0422 | 1.0248 | 1.0286 | 1.0296 | 1.0263 | 1.0157 | 1.0306 | 1.0235 | 1.027 | 1.0289
MK | 3053_Mt Bassett 33 kV | Contingency Outage | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV
MK | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.189% | 1.639% | 1.708% | 2.19% | 1.639% | 1.707% | 2.193% | 1.64% | 1.688% | 2.196% | 1.625% | 1.69% | 2.19% | 1.637% | 1.687%
MK | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1
MK | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.7657 | 3.6879 | 3.791 | 3.7661 | 3.688 | 3.7906 | 3.7719 | 3.6906 | 3.7485 | 3.7778 | 3.6563 | 3.7524 | 3.7668 | 3.6837 | 3.7453
MK | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.21763 | 0.21221 | 0.22425 | 0.21768 | 0.21222 | 0.2242 | 0.21835 | 0.21253 | 0.21924 | 0.21903 | 0.2086 | 0.21971 | 0.21776 | 0.21173 | 0.21887
MK | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0039987 | 0.0039446 | 0.0041684 | 0.0039995 | 0.0039448 | 0.0041674 | 0.0040119 | 0.0039505 | 0.0040753 | 0.0040245 | 0.0038774 | 0.0040839 | 0.004001 | 0.0039356 | 0.0040684
MK | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588
MK | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222
MK | 340_MK3-1 Farleigh 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 340_MK3-1 Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0111 | 1.0068 | 1.0349 | 1.0112 | 1.0068 | 1.0348 | 1.0128 | 1.0075 | 1.0233 | 1.0144 | 0.99814 | 1.0244 | 1.0114 | 1.0056 | 1.0224
MK | 340_MK3-1 Farleigh 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 351_Alligator Creek 33 kV | 6177_Moranbah - Caval Ridge 66 kV | 422_North Mackay No 1 33 kV | 351_Alligator Creek 33 kV | 6326_Millennium - Daunia 66 kV | 422_North Mackay No 1 33 kV | 372_Pioneer Valley-McKinley Creek 33 kV | 3045_Sarina No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 3045_Sarina No 1 33 kV | 422_North Mackay No 1 33 kV | 372_Pioneer Valley-McKinley Creek 33 kV | 422_North Mackay No 1 33 kV
MK | 341_Tennyson St No 2 33 kV | % of Rated A | 90.88% | 89.86% | 52.38% | 90.12% | 89.16% | 51.97% | 89.84% | 88.92% | 52.53% | 89.12% | 89.42% | 52.13% | 91.13% | 90.24% | 53.27%
MK | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1
MK | 341_Tennyson St No 2 33 kV | Loading (A) | 318.0781 | 314.507 | 183.3167 | 315.4362 | 312.0542 | 181.8807 | 314.4461 | 311.2194 | 183.8696 | 311.9276 | 312.959 | 182.4602 | 318.9565 | 315.8309 | 186.4457
MK | 341_Tennyson St No 2 33 kV | Loading (MVA) | 19.009 | 18.9372 | 11.0693 | 18.8522 | 18.7894 | 10.9831 | 18.8177 | 18.769 | 10.974 | 18.6909 | 18.6461 | 10.8993 | 19.0723 | 19.0276 | 11.1231
MK | 341_Tennyson St No 2 33 kV | Loading (MW) | 18.922 | 18.8606 | 11.0609 | 18.7663 | 18.7151 | 10.9752 | 18.7333 | 18.6959 | 10.9655 | 18.6081 | 18.5725 | 10.8912 | 18.9843 | 18.951 | 11.1139
MK | 341_Tennyson St No 2 33 kV | Power Factor | 0.99456 | 0.99512 | 0.99845 | 0.99457 | 0.99521 | 0.9985 | 0.99464 | 0.99527 | 0.99845 | 0.99469 | 0.99523 | 0.99848 | 0.99453 | 0.99515 | 0.99838
MK | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
MK | 341_Tennyson St No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 341_Tennyson St No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0447 | 1.0525 | 1.056 | 1.0448 | 1.0525 | 1.056 | 1.0461 | 1.0542 | 1.0437 | 1.0475 | 1.0415 | 1.0446 | 1.0453 | 1.0531 | 1.0433
MK | 341_Tennyson St No 2 33 kV | Contingency Outage | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV
MK | 342_South Mackay 33 kV | % of Rated A | 79.49% | 55.53% | 52.39% | 79.24% | 55.44% | 52.25% | 65.94% | 44.35% | 44.09% | 67.06% | 45.23% | 44.93% | 66.38% | 44.61% | 44.34%
MK | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1 | TR_LINE 12106200_1 | TR_CABLE 12199655_1 | TR_CABLE 12199655_1
MK | 342_South Mackay 33 kV | Loading (A) | 372.0207 | 352.6454 | 332.673 | 370.8502 | 352.0202 | 331.7779 | 308.5842 | 281.61 | 279.9398 | 313.86 | 287.223 | 285.3046 | 310.6719 | 283.2956 | 281.5659
MK | 342_South Mackay 33 kV | Loading (MVA) | 22.2214 | 21.1837 | 20.0857 | 22.1521 | 21.1448 | 20.0323 | 18.4707 | 16.9017 | 16.7833 | 18.8128 | 17.1903 | 17.1345 | 18.5799 | 16.9835 | 16.872
MK | 342_South Mackay 33 kV | Loading (MW) | 20.9614 | 19.5975 | 18.1019 | 20.8887 | 19.5655 | 18.047 | 16.0966 | 13.798 | 13.6569 | 16.0454 | 13.7483 | 13.6076 | 16.2508 | 13.9294 | 13.787
MK | 342_South Mackay 33 kV | Power Factor | 0.94316 | 0.92512 | 0.90123 | 0.94283 | 0.92531 | 0.9009 | 0.8713 | 0.81636 | 0.81372 | 0.85273 | 0.79977 | 0.79417 | 0.87448 | 0.82017 | 0.81716
MK | 342_South Mackay 33 kV | Rating (A) | 468 | 635 | 635 | 468 | 635 | 635 | 468 | 635 | 635 | 468 | 635 | 635 | 468 | 635 | 635
MK | 342_South Mackay 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 342_South Mackay 33 kV | Min Voltage at Constrained Conductor (pu) | 1.045 | 1.0509 | 1.0563 | 1.045 | 1.0509 | 1.0563 | 1.0472 | 1.05 | 1.0489 | 1.0487 | 1.0471 | 1.0507 | 1.0463 | 1.0488 | 1.0484
MK | 342_South Mackay 33 kV | Contingency Outage | 3046_Rosella 33 kV | 3046_Rosella 33 kV | 3046_Rosella 33 kV | 3046_Rosella 33 kV | 3046_Rosella 33 kV | 3046_Rosella 33 kV | 344_West Mackay 2 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 341_Tennyson St No 2 33 kV | 344_West Mackay 2 33 kV | 423_North Mackay No 2 33 kV | 341_Tennyson St No 2 33 kV | 344_West Mackay 2 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 341_Tennyson St No 2 33 kV
MK | 343_Pleystowe 33 kV | % of Rated A | 73.51% | 96.44% | 45.95% | 73.5% | 96.44% | 45.94% | 73.4% | 96.26% | 46.52% | 72.68% | 96.77% | 46.1% | 74.12% | 97.21% | 46.94%
MK | 343_Pleystowe 33 kV | Limiting Line Name | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1
MK | 343_Pleystowe 33 kV | Loading (A) | 161.7217 | 212.1664 | 101.08 | 161.7104 | 212.1683 | 101.0761 | 161.4711 | 211.7698 | 102.3467 | 159.9059 | 212.8856 | 101.4177 | 163.0655 | 213.8704 | 103.2593
MK | 343_Pleystowe 33 kV | Loading (MVA) | 9.2845 | 12.0982 | 5.9628 | 9.2845 | 12.0982 | 5.9628 | 9.2841 | 12.0974 | 5.9637 | 9.2104 | 12.0016 | 5.9162 | 9.3634 | 12.196 | 6.0128
MK | 343_Pleystowe 33 kV | Loading (MW) | 9.2407 | 12.0209 | 5.9507 | 9.2407 | 12.0209 | 5.9507 | 9.2404 | 12.0205 | 5.9511 | 9.1676 | 11.9246 | 5.9038 | 9.3183 | 12.1167 | 5.9997
MK | 343_Pleystowe 33 kV | Power Factor | 0.99523 | 0.99357 | 0.99791 | 0.99523 | 0.99357 | 0.99791 | 0.99525 | 0.9936 | 0.99783 | 0.9953 | 0.99354 | 0.99785 | 0.99513 | 0.99345 | 0.99776
MK | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
MK | 343_Pleystowe 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 343_Pleystowe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0044 | 0.99757 | 1.0321 | 1.0045 | 0.99756 | 1.0321 | 1.0059 | 0.99937 | 1.0195 | 1.0077 | 0.98626 | 1.0206 | 1.0046 | 0.99762 | 1.0188
MK | 343_Pleystowe 33 kV | Contingency Outage | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV
MK | 344_West Mackay 2 33 kV | % of Rated A | 48.63% | 47.26% | 26.75% | 48.35% | 46.99% | 26.6% | 48.28% | 46.95% | 26.91% | 47.94% | 47.25% | 26.74% | 48.88% | 47.54% | 27.22%
MK | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK | 344_West Mackay 2 33 kV | Loading (A) | 303.9281 | 295.3768 | 167.1734 | 302.173 | 293.6965 | 166.2332 | 301.7473 | 293.4516 | 168.1882 | 299.6027 | 295.3421 | 167.0959 | 305.4768 | 297.1479 | 170.1496
MK | 344_West Mackay 2 33 kV | Loading (MVA) | 18.1549 | 17.7778 | 10.0968 | 18.0515 | 17.6768 | 10.0405 | 18.0498 | 17.6898 | 10.0403 | 17.9449 | 17.5885 | 9.9837 | 18.2575 | 17.8935 | 10.1531
MK | 344_West Mackay 2 33 kV | Loading (MW) | 17.6344 | 17.2852 | 9.9167 | 17.5369 | 17.1896 | 9.862 | 17.5366 | 17.1919 | 9.862 | 17.4387 | 17.0964 | 9.8072 | 17.7318 | 17.3834 | 9.9714
MK | 344_West Mackay 2 33 kV | Power Factor | 0.97096 | 0.97193 | 0.98189 | 0.97112 | 0.97208 | 0.98196 | 0.97119 | 0.97149 | 0.98197 | 0.97142 | 0.97165 | 0.98206 | 0.97083 | 0.97112 | 0.98183
MK | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625
MK | 344_West Mackay 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 344_West Mackay 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0451 | 1.053 | 1.0567 | 1.0452 | 1.053 | 1.0567 | 1.0465 | 1.0547 | 1.0444 | 1.0479 | 1.0419 | 1.0453 | 1.0457 | 1.0535 | 1.044
MK | 344_West Mackay 2 33 kV | Contingency Outage | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV
MK | 346_Ritchies Rd 33 kV | % of Rated A | 74.7% | 71.4% | 37.76% | 74.69% | 71.4% | 37.76% | 74.58% | 71.26% | 37.76% | 73.84% | 71.67% | 37.76% | 75.32% | 71.99% | 38.02%
MK | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11706_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11706_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11706_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11706_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11706_1
MK | 346_Ritchies Rd 33 kV | Loading (A) | 164.3375 | 217.0614 | 87.9785 | 164.3255 | 217.0635 | 87.9786 | 164.0723 | 216.6314 | 87.9767 | 162.459 | 217.8919 | 87.9777 | 165.7078 | 218.8641 | 88.5823
MK | 346_Ritchies Rd 33 kV | Loading (MVA) | 9.29 | 12.1084 | 5.1977 | 9.29 | 12.1085 | 5.1979 | 9.2895 | 12.1076 | 5.2045 | 9.2163 | 12.0122 | 5.2099 | 9.3681 | 12.2067 | 5.2353
MK | 346_Ritchies Rd 33 kV | Loading (MW) | 9.2451 | 12.0293 | 4.2425 | 9.2451 | 12.0293 | 4.2425 | 9.2449 | 12.0288 | 4.2425 | 9.1721 | 11.9332 | 4.2425 | 9.3223 | 12.1253 | 4.3028
MK | 346_Ritchies Rd 33 kV | Power Factor | 0.99517 | 0.99346 | 0.81478 | 0.99517 | 0.99346 | 0.81475 | 0.99519 | 0.99349 | 0.81371 | 0.9952 | 0.99342 | 0.81286 | 0.99512 | 0.99333 | 0.82044
MK | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 304 | 233 | 220 | 304 | 233 | 220 | 304 | 233 | 220 | 304 | 233 | 220 | 304 | 233
MK | 346_Ritchies Rd 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 346_Ritchies Rd 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98891 | 0.97581 | 1.0336 | 0.98898 | 0.9758 | 1.0336 | 0.99046 | 0.97767 | 1.0349 | 0.9924 | 0.96436 | 1.036 | 0.98897 | 0.97562 | 1.0339
MK | 346_Ritchies Rd 33 kV | Contingency Outage | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 3045_Sarina No 1 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 3045_Sarina No 1 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 3045_Sarina No 1 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 3045_Sarina No 1 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 3045_Sarina No 1 33 kV
MK | 347_Mt Bassett 33 kV | % of Rated A | 70.59% | 82.03% | 47.23% | 70.58% | 82.03% | 47.23% | 71.07% | 82.58% | 48.19% | 70.4% | 82.93% | 47.75% | 72.31% | 84.04% | 49%
MK | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK | 347_Mt Bassett 33 kV | Loading (A) | 180.0012 | 209.1856 | 120.4443 | 179.986 | 209.1833 | 120.4386 | 181.2325 | 210.5742 | 122.8892 | 179.524 | 211.4706 | 121.7746 | 184.3881 | 214.3089 | 124.9568
MK | 347_Mt Bassett 33 kV | Loading (MVA) | 10.7179 | 12.5464 | 7.2593 | 10.7179 | 12.5464 | 7.2593 | 10.8063 | 12.6499 | 7.3202 | 10.7186 | 12.5491 | 7.2602 | 10.9846 | 12.8598 | 7.44
MK | 347_Mt Bassett 33 kV | Loading (MW) | 10.5485 | 12.3269 | 7.1661 | 10.5485 | 12.3269 | 7.1661 | 10.6348 | 12.4279 | 7.2257 | 10.5483 | 12.3292 | 7.1669 | 10.8084 | 12.6311 | 7.3431
MK | 347_Mt Bassett 33 kV | Power Factor | 0.98408 | 0.98239 | 0.98707 | 0.98409 | 0.98239 | 0.98707 | 0.98403 | 0.98233 | 0.98699 | 0.98401 | 0.98237 | 0.98705 | 0.98385 | 0.98211 | 0.98688
MK | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
MK | 347_Mt Bassett 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 347_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0417 | 1.0493 | 1.0545 | 1.0418 | 1.0493 | 1.0545 | 1.0432 | 1.051 | 1.0422 | 1.0446 | 1.0382 | 1.0431 | 1.0423 | 1.0498 | 1.0417
MK | 347_Mt Bassett 33 kV | Contingency Outage | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV
MK | 348_Farleigh 33 kV | % of Rated A | 34.21% | 31.84% | 15.62% | 34.21% | 31.84% | 15.62% | 34.15% | 31.77% | 15.83% | 34.08% | 32.23% | 15.81% | 34.92% | 32.52% | 16.17%
MK | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1
MK | 348_Farleigh 33 kV | Loading (A) | 66.3706 | 82.7717 | 40.3115 | 66.3656 | 82.7725 | 40.3099 | 66.26 | 82.6008 | 40.833 | 66.1213 | 83.8074 | 40.7811 | 67.7473 | 84.5507 | 41.7138
MK | 348_Farleigh 33 kV | Loading (MVA) | 3.7182 | 4.5637 | 2.3465 | 3.7182 | 4.5637 | 2.3465 | 3.7179 | 4.5632 | 2.3468 | 3.7176 | 4.5652 | 2.3468 | 3.7948 | 4.6596 | 2.3953
MK | 348_Farleigh 33 kV | Loading (MW) | 3.7021 | 4.5327 | 2.3454 | 3.7021 | 4.5327 | 2.3454 | 3.702 | 4.5325 | 2.3455 | 3.7018 | 4.5336 | 2.3455 | 3.7781 | 4.6267 | 2.3937
MK | 348_Farleigh 33 kV | Power Factor | 0.99568 | 0.99322 | 0.99951 | 0.99568 | 0.99322 | 0.99951 | 0.99572 | 0.99327 | 0.99942 | 0.99576 | 0.99308 | 0.99943 | 0.99558 | 0.99294 | 0.99932
MK | 348_Farleigh 33 kV | Rating (A) | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258
MK | 348_Farleigh 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 348_Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 0.97891 | 0.96306 | 1.0177 | 0.97898 | 0.96305 | 1.0177 | 0.98048 | 0.96495 | 1.0048 | 0.98245 | 0.95144 | 1.0061 | 0.97876 | 0.96257 | 1.0039
MK | 348_Farleigh 33 kV | Contingency Outage | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV
MK | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 41.42% | 37.76% | 18.77% | 41.29% | 37.78% | 18.77% | 41.55% | 37.76% | 18.77% | 41.22% | 37.47% | 18.65% | 41.9% | 38.42% | 19.02%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 91.1188 | 114.8043 | 56.8649 | 90.8278 | 114.8471 | 56.8692 | 91.4061 | 114.8022 | 56.8817 | 90.6913 | 113.9065 | 56.5064 | 92.1878 | 116.801 | 57.6348
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 10.8591 | 13.5953 | 6.8215 | 10.8564 | 13.5957 | 6.8216 | 10.86 | 13.5953 | 6.8217 | 10.7817 | 13.4932 | 6.7778 | 11.0163 | 13.8008 | 6.9092
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 10.6944 | 13.3114 | 6.7854 | 10.6939 | 13.3115 | 6.7854 | 10.6946 | 13.3114 | 6.7854 | 10.6202 | 13.2153 | 6.7428 | 10.8474 | 13.5075 | 6.8708
MK | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.98484 | 0.97912 | 0.9947 | 0.98502 | 0.9791 | 0.99469 | 0.98477 | 0.97912 | 0.99468 | 0.98502 | 0.97941 | 0.99483 | 0.98466 | 0.97875 | 0.99443
MK | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 349_Pioneer Valley - Pinnacle 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 349_Pioneer Valley - Pinnacle 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0425 | 1.0359 | 1.0494 | 1.0456 | 1.0355 | 1.0493 | 1.0393 | 1.0359 | 1.0491 | 1.0399 | 1.0362 | 1.0493 | 1.0453 | 1.0336 | 1.0487
MK | 349_Pioneer Valley - Pinnacle 66 kV | Contingency Outage | 372_Pioneer Valley-McKinley Creek 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 422_North Mackay No 1 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 422_North Mackay No 1 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV
MK | 351_Alligator Creek 33 kV | % of Rated A | 134.6% | 122.1% | 121.4% | 133.6% | 121.4% | 120.7% | 133.2% | 121.1% | 120.3% | 135.8% | 123.5% | 122.4% | 134.9% | 122.1% | 121%
MK | 351_Alligator Creek 33 kV | Limiting Line Name | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK | 351_Alligator Creek 33 kV | Loading (A) | 314.8695 | 285.6961 | 284.0522 | 312.7151 | 283.9921 | 282.3541 | 311.7963 | 283.2632 | 281.585 | 317.7061 | 288.9149 | 286.4519 | 315.5867 | 285.8207 | 283.146
MK | 351_Alligator Creek 33 kV | Loading (MVA) | 18.361 | 16.7173 | 16.5752 | 18.2419 | 16.6192 | 16.4803 | 18.1699 | 16.5498 | 16.4195 | 18.4017 | 16.7915 | 16.815 | 18.1673 | 16.5195 | 16.5371
MK | 351_Alligator Creek 33 kV | Loading (MW) | 16.4746 | 14.2713 | 14.1249 | 16.3182 | 14.1364 | 13.9914 | 16.2404 | 14.0693 | 13.9249 | 16.1958 | 14.0306 | 13.8848 | 16.401 | 14.2061 | 14.058
MK | 351_Alligator Creek 33 kV | Power Factor | 0.89726 | 0.85368 | 0.85217 | 0.89454 | 0.85061 | 0.84898 | 0.89381 | 0.85012 | 0.84807 | 0.88012 | 0.83558 | 0.82574 | 0.90277 | 0.85996 | 0.85009
MK | 351_Alligator Creek 33 kV | Rating (A) | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
MK | 351_Alligator Creek 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 351_Alligator Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0202 | 1.0237 | 1.0209 | 1.0205 | 1.0238 | 1.0211 | 1.0195 | 1.0222 | 1.0201 | 1.0133 | 1.0168 | 1.027 | 1.0071 | 1.0112 | 1.0218
MK | 351_Alligator Creek 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 15.21% | 12.4% | 11.73% | 15.16% | 12.4% | 11.73% | 15.27% | 12.4% | 11.73% | 15.26% | 12.39% | 11.73% | 15.16% | 12.43% | 11.74%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 13.9949 | 14.7532 | 13.2558 | 13.9444 | 14.7593 | 13.257 | 14.0477 | 14.7528 | 13.2603 | 14.0371 | 14.7475 | 13.2575 | 13.9514 | 14.7972 | 13.2682
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 1.6393 | 1.7126 | 1.5687 | 1.6385 | 1.7127 | 1.5687 | 1.6403 | 1.7126 | 1.5688 | 1.6401 | 1.7125 | 1.5687 | 1.6386 | 1.7133 | 1.5689
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 1.4966 | 1.5644 | 1.4313 | 1.4965 | 1.5644 | 1.4313 | 1.4967 | 1.5644 | 1.4313 | 1.4967 | 1.5644 | 1.4313 | 1.4965 | 1.5645 | 1.4313
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.9129 | 0.91344 | 0.91237 | 0.91333 | 0.9134 | 0.91236 | 0.91244 | 0.91345 | 0.91233 | 0.91253 | 0.91349 | 0.91235 | 0.91327 | 0.9131 | 0.91225
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0247 | 1.0155 | 1.0352 | 1.0279 | 1.0151 | 1.0351 | 1.0214 | 1.0155 | 1.0349 | 1.0221 | 1.0158 | 1.0351 | 1.0274 | 1.0129 | 1.0344
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Contingency Outage | 372_Pioneer Valley-McKinley Creek 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 422_North Mackay No 1 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 422_North Mackay No 1 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV
MK | 364_West Mackay No 1 33 kV | % of Rated A | 104.9% | 71.91% | 40.79% | 104.3% | 71.51% | 40.56% | 104.1% | 71.45% | 41.04% | 103.4% | 71.91% | 40.77% | 105.4% | 72.28% | 41.51%
MK | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK | 364_West Mackay No 1 33 kV | Loading (A) | 304.1362 | 295.5705 | 167.2298 | 302.3784 | 293.8877 | 166.289 | 301.9517 | 293.6431 | 168.2459 | 299.8035 | 295.538 | 167.1527 | 305.6872 | 297.0693 | 170.2087
MK | 364_West Mackay No 1 33 kV | Loading (MVA) | 18.1575 | 17.7802 | 10.0974 | 18.0541 | 17.6792 | 10.0411 | 18.0524 | 17.6922 | 10.0409 | 17.9475 | 17.591 | 9.9843 | 18.2602 | 17.8806 | 10.1538
MK | 364_West Mackay No 1 33 kV | Loading (MW) | 17.629 | 17.28 | 9.9144 | 17.5315 | 17.1845 | 9.8597 | 17.5312 | 17.1868 | 9.8597 | 17.4334 | 17.0912 | 9.805 | 17.7264 | 17.3755 | 9.9691
MK | 364_West Mackay No 1 33 kV | Power Factor | 0.97089 | 0.97187 | 0.98187 | 0.97105 | 0.97202 | 0.98194 | 0.97113 | 0.97143 | 0.98195 | 0.97136 | 0.97159 | 0.98204 | 0.97077 | 0.97175 | 0.98181
MK | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410
MK | 364_West Mackay No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 364_West Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0444 | 1.0523 | 1.0563 | 1.0445 | 1.0524 | 1.0564 | 1.0459 | 1.054 | 1.0441 | 1.0472 | 1.0413 | 1.045 | 1.045 | 1.0529 | 1.0436
MK | 364_West Mackay No 1 33 kV | Contingency Outage | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV
MK | 365_Tennyson St No 1 33 kV | % of Rated A | 12.01% | 10.42% | 6.194% | 11.91% | 10.34% | 6.145% | 11.87% | 10.31% | 6.212% | 11.78% | 10.37% | 6.164% | 12.04% | 10.46% | 6.299%
MK | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1 | TR_LINE 11133_1
MK | 365_Tennyson St No 1 33 kV | Loading (A) | 79.8552 | 78.9583 | 46.0809 | 79.1937 | 78.3435 | 45.7206 | 78.9456 | 78.1343 | 46.217 | 78.3149 | 78.5675 | 45.8638 | 80.0755 | 79.2896 | 46.8627
MK | 365_Tennyson St No 1 33 kV | Loading (MVA) | 4.755 | 4.7373 | 2.777 | 4.7161 | 4.7005 | 2.7555 | 4.7075 | 4.6955 | 2.7528 | 4.6761 | 4.6642 | 2.7342 | 4.7708 | 4.7597 | 2.7901
MK | 365_Tennyson St No 1 33 kV | Loading (MW) | 3.9155 | 3.9152 | 2.3478 | 3.8835 | 3.8868 | 2.3307 | 3.8781 | 3.8842 | 2.3278 | 3.8533 | 3.8579 | 2.3128 | 3.9276 | 3.9346 | 2.358
MK | 365_Tennyson St No 1 33 kV | Power Factor | 0.82344 | 0.82646 | 0.84544 | 0.82345 | 0.8269 | 0.84585 | 0.82381 | 0.82722 | 0.84559 | 0.82403 | 0.82714 | 0.84586 | 0.82328 | 0.82665 | 0.84515
MK | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 758 | 744 | 665 | 758 | 744 | 665 | 758 | 744 | 665 | 758 | 744 | 665 | 758 | 744
MK | 365_Tennyson St No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 365_Tennyson St No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0417 | 1.0496 | 1.0543 | 1.0418 | 1.0497 | 1.0544 | 1.0432 | 1.0514 | 1.0421 | 1.0446 | 1.0386 | 1.043 | 1.0423 | 1.0502 | 1.0416
MK | 365_Tennyson St No 1 33 kV | Contingency Outage | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV
MK | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.06539% | 0.04695% | 0.04706% | 0.06538% | 0.04694% | 0.04706% | 0.06482% | 0.04697% | 0.04708% | 0.06486% | 0.047% | 0.04709% | 0.06535% | 0.04693% | 0.04706%
MK | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16477 | 0.16385 | 0.16376 | 0.16477 | 0.16382 | 0.16375 | 0.16334 | 0.16392 | 0.16382 | 0.16344 | 0.16403 | 0.16387 | 0.16468 | 0.16377 | 0.16377
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.020024 | 0.0198 | 0.019778 | 0.020022 | 0.019793 | 0.019776 | 0.019676 | 0.019817 | 0.019793 | 0.0197 | 0.019845 | 0.019806 | 0.020002 | 0.019781 | 0.01978
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.1549e-08 | 8.0637e-08 | 8.054e-08 | 8.142e-08 | 8.0607e-08 | 8.0476e-08 | 8.0174e-08 | 8.066e-08 | 8.0662e-08 | 8.0283e-08 | 8.0738e-08 | 8.0653e-08 | 8.1399e-08 | 8.0574e-08 | 8.0535e-08
MK | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.0727e-06 | 4.0725e-06 | 4.0721e-06 | 4.0665e-06 | 4.0724e-06 | 4.0693e-06 | 4.0747e-06 | 4.0702e-06 | 4.0752e-06 | 4.0753e-06 | 4.0685e-06 | 4.0722e-06 | 4.0696e-06 | 4.0733e-06 | 4.0716e-06
MK | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348
MK | 367_Pioneer Valley - Greenmount 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 367_Pioneer Valley - Greenmount 66 kV | Min Voltage at Constrained Conductor (pu) | 1.063 | 1.0571 | 1.0565 | 1.063 | 1.0569 | 1.0565 | 1.0538 | 1.0576 | 1.0569 | 1.0544 | 1.0583 | 1.0573 | 1.0625 | 1.0566 | 1.0566
MK | 367_Pioneer Valley - Greenmount 66 kV | Contingency Outage | 6333_Hail Creek 66 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 372_Pioneer Valley-McKinley Creek 33 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 372_Pioneer Valley-McKinley Creek 33 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV
MK | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 12.56% | 11.73% | 5.483% | 12.85% | 12.03% | 5.625% | 12.93% | 12.03% | 5.626% | 12.6% | 11.72% | 5.484% | 12.86% | 12.05% | 5.628%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 24.5002 | 32.5969 | 14.8052 | 25.0631 | 33.4536 | 15.1877 | 25.2103 | 33.4416 | 15.1908 | 24.5615 | 32.5895 | 14.8072 | 25.0707 | 33.5117 | 15.1958
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 2.9315 | 3.8797 | 1.7801 | 3.007 | 3.9798 | 1.8259 | 3.0071 | 3.9798 | 1.8259 | 2.9316 | 3.8797 | 1.7801 | 3.007 | 3.9799 | 1.8259
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 2.8995 | 3.8329 | 1.7629 | 2.9739 | 3.9313 | 1.8081 | 2.9739 | 3.9313 | 1.8081 | 2.8995 | 3.8329 | 1.7629 | 2.9739 | 3.9314 | 1.8081
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.98905 | 0.98793 | 0.99031 | 0.98899 | 0.98781 | 0.99027 | 0.98895 | 0.98781 | 0.99027 | 0.98903 | 0.98793 | 0.99031 | 0.98898 | 0.98779 | 0.99026
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0467 | 1.0412 | 1.0518 | 1.0495 | 1.0407 | 1.0517 | 1.0434 | 1.041 | 1.0515 | 1.0441 | 1.0414 | 1.0517 | 1.0492 | 1.0389 | 1.0511
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Contingency Outage | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV
MK | 422_North Mackay No 1 33 kV | % of Rated A | 90.9% | 109.6% | 50.9% | 91.51% | 110.5% | 51.19% | 92.48% | 111.7% | 51.65% | 93.22% | 112.7% | 52.02% | 96.39% | 117% | 53.47%
MK | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1
MK | 422_North Mackay No 1 33 kV | Loading (A) | 568.1229 | 759.7499 | 344.6247 | 571.9475 | 765.4689 | 346.5392 | 577.9924 | 774.1813 | 349.6824 | 582.6506 | 781.2628 | 352.1471 | 602.4521 | 811.1109 | 361.9783
MK | 422_North Mackay No 1 33 kV | Loading (MVA) | 33.8711 | 45.464 | 20.5522 | 34.0808 | 45.758 | 20.6621 | 34.4328 | 46.2559 | 20.8488 | 34.7158 | 46.6525 | 20.9996 | 35.7679 | 48.1429 | 21.5544
MK | 422_North Mackay No 1 33 kV | Loading (MW) | 33.3965 | 45.3501 | 19.0599 | 33.6183 | 45.6522 | 19.1854 | 33.9865 | 46.158 | 19.395 | 34.2812 | 46.5628 | 19.5624 | 35.3906 | 48.0868 | 20.1906
MK | 422_North Mackay No 1 33 kV | Power Factor | 0.98587 | 0.99743 | 0.92723 | 0.98631 | 0.99763 | 0.92837 | 0.98693 | 0.99782 | 0.93011 | 0.98737 | 0.99802 | 0.93141 | 0.98934 | 0.99879 | 0.93657
MK | 422_North Mackay No 1 33 kV | Rating (A) | 625 | 693 | 677 | 625 | 693 | 677 | 625 | 693 | 677 | 625 | 693 | 677 | 625 | 693 | 677
MK | 422_North Mackay No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 422_North Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0429 | 1.0466 | 1.0434 | 1.0424 | 1.0455 | 1.0432 | 1.0421 | 1.045 | 1.0431 | 1.0423 | 1.0444 | 1.0433 | 1.0385 | 1.0381 | 1.0418
MK | 422_North Mackay No 1 33 kV | Contingency Outage | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV
MK | 423_North Mackay No 2 33 kV | % of Rated A | 45.24% | 58.11% | 30.51% | 45.53% | 58.54% | 30.64% | 45.8% | 58.93% | 30.77% | 46.07% | 59.31% | 30.9% | 47.27% | 61.08% | 31.43%
MK | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1
MK | 423_North Mackay No 2 33 kV | Loading (A) | 344.3071 | 442.2285 | 232.1595 | 346.5038 | 445.476 | 233.1526 | 348.5637 | 448.4197 | 234.1515 | 350.6009 | 451.3181 | 235.1381 | 359.704 | 464.8295 | 239.1744
MK | 423_North Mackay No 2 33 kV | Loading (MVA) | 20.7128 | 26.4207 | 13.9589 | 20.8391 | 26.6009 | 14.017 | 20.9707 | 26.7857 | 14.0827 | 21.1032 | 26.9712 | 14.1463 | 21.606 | 27.6938 | 14.3759
MK | 423_North Mackay No 2 33 kV | Loading (MW) | 19.3812 | 25.8263 | 10.9458 | 19.53 | 26.0255 | 11.0293 | 19.6787 | 26.2243 | 11.1148 | 19.8274 | 26.4231 | 11.1984 | 20.4232 | 27.221 | 11.5309
MK | 423_North Mackay No 2 33 kV | Power Factor | 0.93571 | 0.9775 | 0.78414 | 0.93718 | 0.97837 | 0.78685 | 0.93839 | 0.97904 | 0.78925 | 0.93954 | 0.97968 | 0.79161 | 0.94526 | 0.98293 | 0.8021
MK | 423_North Mackay No 2 33 kV | Rating (A) | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761 | 761
MK | 423_North Mackay No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 423_North Mackay No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0524 | 1.045 | 1.0519 | 1.0521 | 1.0445 | 1.0518 | 1.0524 | 1.0448 | 1.0522 | 1.0529 | 1.0453 | 1.0526 | 1.0507 | 1.0421 | 1.0516
MK | 423_North Mackay No 2 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK | PV 6/4_Glenella No 2 66 kV | % of Rated A | 46.3% | 54.79% | 24.5% | 46.63% | 55.21% | 24.65% | 47.69% | 55.8% | 24.87% | 47.98% | 56.2% | 25.01% | 48.89% | 58.15% | 25.69%
MK | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105536_1 | TR_LINE 105446_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105447_2 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105074_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105525_2 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105543_1 | TR_LINE 105536_1
MK | PV 6/4_Glenella No 2 66 kV | Loading (A) | 374.589 | 497.4716 | 218.317 | 377.2544 | 501.2859 | 219.6544 | 385.8325 | 506.6586 | 221.5981 | 388.1394 | 510.2508 | 222.8319 | 395.5155 | 528.0454 | 228.9349
MK | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 45.438 | 58.5246 | 26.3226 | 45.7545 | 58.8585 | 26.4822 | 46.2405 | 59.3988 | 26.7213 | 46.5436 | 59.7729 | 26.8791 | 47.9433 | 61.4748 | 27.5944
MK | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 45.4055 | 58.5244 | 25.3744 | 45.7265 | 58.8585 | 25.5504 | 46.2219 | 59.3988 | 25.8125 | 46.5273 | 59.7729 | 25.9836 | 47.9348 | 61.4747 | 26.7701
MK | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.99928 | 1 | 0.96397 | 0.99939 | 1 | 0.96481 | 0.9996 | 1 | 0.96598 | 0.99965 | 1 | 0.96667 | 0.99982 | 1 | 0.97012
MK | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | PV 6/4_Glenella No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | PV 6/4_Glenella No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0611 | 1.0284 | 1.0547 | 1.0609 | 1.0267 | 1.0547 | 1.0484 | 1.0255 | 1.0548 | 1.049 | 1.0245 | 1.0552 | 1.0604 | 1.0183 | 1.0544
MK | PV 6/4_Glenella No 2 66 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV
MK | PV 6/5_Glenella No 1 66 kV | % of Rated A | 47.25% | 58.99% | 24.92% | 47.58% | 59.42% | 25.07% | 48.66% | 60.03% | 25.29% | 48.95% | 60.43% | 25.43% | 49.86% | 62.46% | 26.12%
MK | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105534_1 | TR_LINE 105534_1 | TR_LINE 105119_4 | TR_LINE 105534_1
MK | PV 6/5_Glenella No 1 66 kV | Loading (A) | 382.2271 | 535.6406 | 222.0221 | 384.9134 | 539.5697 | 223.3718 | 393.641 | 545.0273 | 225.3321 | 395.9716 | 548.7261 | 226.5748 | 403.3791 | 567.1753 | 232.7335
MK | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 46.3321 | 62.231 | 26.7591 | 46.6507 | 62.6422 | 26.9202 | 47.1423 | 63.2636 | 27.1612 | 47.4476 | 63.6814 | 27.3202 | 48.8535 | 65.5593 | 28.0415
MK | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 46.3178 | 62.1836 | 25.9133 | 46.6392 | 62.5897 | 26.0895 | 47.1366 | 63.2039 | 26.3517 | 47.4434 | 63.6151 | 26.5229 | 48.8533 | 65.4637 | 27.3101
MK | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.99969 | 0.99924 | 0.96837 | 0.99975 | 0.99916 | 0.96912 | 0.99988 | 0.99906 | 0.97017 | 0.99991 | 0.99896 | 0.97079 | 0.99999 | 0.99854 | 0.97389
MK | PV 6/5_Glenella No 1 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | PV 6/5_Glenella No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | PV 6/5_Glenella No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0603 | 1.0158 | 1.0543 | 1.0602 | 1.0151 | 1.0543 | 1.0476 | 1.0149 | 1.0544 | 1.0481 | 1.0147 | 1.0548 | 1.0594 | 1.0106 | 1.054
MK | PV 6/5_Glenella No 1 66 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV
MK | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 13.96% | 13.5% | 10.97% | 13.97% | 13.46% | 11.01% | 13.97% | 13.46% | 11.01% | 13.97% | 13.47% | 11.01% | 14.19% | 13.67% | 11.18%
MK | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1
MK | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 53.8891 | 52.5004 | 37.0907 | 53.9211 | 52.3688 | 37.2227 | 53.9215 | 52.3692 | 37.2227 | 53.9162 | 52.3891 | 37.2208 | 54.7682 | 53.1901 | 37.7992
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 6.412 | 6.2299 | 4.43 | 6.4091 | 6.2321 | 4.4331 | 6.4091 | 6.2321 | 4.4331 | 6.4091 | 6.235 | 4.4331 | 6.5082 | 6.3284 | 4.5011
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 6.0899 | 5.9237 | 4.2297 | 6.0894 | 5.9241 | 4.2301 | 6.0894 | 5.9241 | 4.2301 | 6.0894 | 5.9245 | 4.2301 | 6.182 | 6.0141 | 4.2943
MK | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.94975 | 0.95084 | 0.95477 | 0.9501 | 0.95056 | 0.9542 | 0.9501 | 0.95056 | 0.9542 | 0.95011 | 0.95018 | 0.9542 | 0.94986 | 0.95032 | 0.95403
MK | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
MK | 6328_Broadlea - Moorvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 6328_Broadlea - Moorvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0408 | 1.038 | 1.0448 | 1.0398 | 1.041 | 1.0418 | 1.0398 | 1.041 | 1.0418 | 1.0399 | 1.0411 | 1.0419 | 1.0395 | 1.0408 | 1.0417
MK | 6328_Broadlea - Moorvale 66 kV | Contingency Outage | 6330 Broadlea - Millennium 66 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 7366_Moranbah - Broadlea 132 kV | 7366_Moranbah - Broadlea 132 kV | 6330 Broadlea - Millennium 66 kV | 7366_Moranbah - Broadlea 132 kV | 7366_Moranbah - Broadlea 132 kV | 6330 Broadlea - Millennium 66 kV | 7366_Moranbah - Broadlea 132 kV | 7366_Moranbah - Broadlea 132 kV | 6330 Broadlea - Millennium 66 kV | 7366_Moranbah - Broadlea 132 kV | 7366_Moranbah - Broadlea 132 kV | 6330 Broadlea - Millennium 66 kV
MK | 6329_Broadlea - Coppabella 66 kV | % of Rated A | 22.6% | 21.43% | 22.97% | 22.53% | 21.28% | 23.05% | 22.53% | 21.28% | 23.05% | 22.53% | 21.28% | 23.05% | 22.53% | 21.29% | 23.05%
MK | 6329_Broadlea - Coppabella 66 kV | Limiting Line Name | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1
MK | 6329_Broadlea - Coppabella 66 kV | Loading (A) | 87.2344 | 83.3773 | 77.6367 | 86.9574 | 82.7908 | 77.8976 | 86.9596 | 82.7922 | 77.8974 | 86.9511 | 82.7826 | 77.8933 | 86.975 | 82.806 | 77.9041
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MVA) | 10.3 | 9.8158 | 9.1832 | 10.295 | 9.8127 | 9.1879 | 10.295 | 9.8127 | 9.1879 | 10.2949 | 9.8126 | 9.1879 | 10.2952 | 9.8128 | 9.188
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MW) | 9.9047 | 9.4506 | 8.8522 | 9.903 | 9.4491 | 8.8537 | 9.903 | 9.4491 | 8.8537 | 9.903 | 9.4491 | 8.8537 | 9.903 | 9.4492 | 8.8537
MK | 6329_Broadlea - Coppabella 66 kV | Power Factor | 0.95805 | 0.95873 | 0.95892 | 0.95829 | 0.9587 | 0.95866 | 0.95829 | 0.9587 | 0.95866 | 0.95829 | 0.9587 | 0.95866 | 0.95828 | 0.9587 | 0.95865
MK | 6329_Broadlea - Coppabella 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
MK | 6329_Broadlea - Coppabella 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 6329_Broadlea - Coppabella 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0235 | 1.0216 | 1.0284 | 1.0265 | 1.0289 | 1.0254 | 1.0264 | 1.0289 | 1.0254 | 1.0265 | 1.029 | 1.0254 | 1.0263 | 1.0287 | 1.0253
MK | 6329_Broadlea - Coppabella 66 kV | Contingency Outage | 6330 Broadlea - Millennium 66 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 6330 Broadlea - Millennium 66 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 6330 Broadlea - Millennium 66 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 6330 Broadlea - Millennium 66 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 6330 Broadlea - Millennium 66 kV
MK | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 39.43% | 37.29% | 40.87% | 42.9% | 40.64% | 44.74% | 42.9% | 40.65% | 44.74% | 42.9% | 40.64% | 44.74% | 42.97% | 40.71% | 44.8%
MK | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 277.9872 | 274.0717 | 266.4616 | 302.4427 | 298.7364 | 291.7331 | 302.4498 | 298.7415 | 291.7373 | 302.4217 | 298.7083 | 291.723 | 302.947 | 299.2216 | 292.0666
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 64.0054 | 63.1476 | 61.6783 | 69.3494 | 68.5459 | 67.2609 | 69.3495 | 68.546 | 67.2609 | 69.349 | 68.5454 | 67.2607 | 69.4546 | 68.6479 | 67.3323
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 58.4308 | 57.8705 | 56.4588 | 62.853 | 62.3601 | 61.1082 | 62.853 | 62.3601 | 61.1082 | 62.853 | 62.36 | 61.1081 | 62.9464 | 62.4509 | 61.1728
MK | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.9129 | 0.91643 | 0.91537 | 0.90632 | 0.90976 | 0.90852 | 0.90632 | 0.90976 | 0.90852 | 0.90633 | 0.90976 | 0.90853 | 0.9063 | 0.90973 | 0.90852
MK | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK | 7366_Moranbah - Broadlea 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 7366_Moranbah - Broadlea 132 kV | Min Voltage at Constrained Conductor (pu) | 1.007 | 1.0077 | 1.0124 | 1.0028 | 1.0035 | 1.0084 | 1.0028 | 1.0035 | 1.0083 | 1.0029 | 1.0036 | 1.0084 | 1.0027 | 1.0034 | 1.0083
MK | 7366_Moranbah - Broadlea 132 kV | Contingency Outage | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV
MK | 232_Newlands-Glenden 66 kV | % of Rated A | 9.472% | 6.859% | 3.711% | 9.479% | 6.864% | 3.713% | 9.479% | 6.864% | 3.713% | 9.478% | 6.863% | 3.713% | 10.19% | 7.377% | 3.958%
MK | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1
MK | 232_Newlands-Glenden 66 kV | Loading (A) | 10.9881 | 10.9739 | 5.7899 | 10.9958 | 10.9817 | 5.7925 | 10.996 | 10.9819 | 5.7925 | 10.995 | 10.9807 | 5.7923 | 11.8186 | 11.8033 | 6.1745
MK | 232_Newlands-Glenden 66 kV | Loading (MVA) | 1.3152 | 1.3136 | 0.69153 | 1.3151 | 1.3135 | 0.69139 | 1.3151 | 1.3135 | 0.69139 | 1.3152 | 1.3135 | 0.6914 | 1.4134 | 1.4116 | 0.73695
MK | 232_Newlands-Glenden 66 kV | Loading (MW) | 1.3016 | 1.2999 | 0.64705 | 1.3016 | 1.2999 | 0.64705 | 1.3016 | 1.2999 | 0.64705 | 1.3016 | 1.2999 | 0.64705 | 1.4021 | 1.4003 | 0.6969
MK | 232_Newlands-Glenden 66 kV | Power Factor | 0.98967 | 0.98962 | 0.93568 | 0.98972 | 0.98967 | 0.93586 | 0.98972 | 0.98968 | 0.93586 | 0.98971 | 0.98967 | 0.93585 | 0.992 | 0.99196 | 0.94566
MK | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
MK | 232_Newlands-Glenden 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | 232_Newlands-Glenden 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0471 | 1.0471 | 1.0448 | 1.0463 | 1.0463 | 1.0441 | 1.0463 | 1.0463 | 1.0441 | 1.0463 | 1.0464 | 1.0442 | 1.0462 | 1.0462 | 1.0441
MK | 232_Newlands-Glenden 66 kV | Contingency Outage | 6327_Broadlea - Isaac Plains 66 kV | 6327_Broadlea - Isaac Plains 66 kV | 342_South Mackay 33 kV | 6327_Broadlea - Isaac Plains 66 kV | PV 6/4_Glenella No 2 66 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 39.91% | 36.54% | 39.11% | 39.94% | 36.57% | 39.14% | 39.94% | 36.57% | 39.14% | 39.94% | 36.57% | 39.13% | 39.94% | 36.57% | 39.14%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1 | TR_LINE 182334_1
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 75.0227 | 74.9048 | 72.3508 | 75.0865 | 74.9693 | 72.4028 | 75.0879 | 74.9705 | 72.403 | 75.0802 | 74.9613 | 72.3986 | 75.0957 | 74.9775 | 72.4035
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 8.9397 | 8.9259 | 8.6013 | 8.9406 | 8.9268 | 8.6021 | 8.9406 | 8.9268 | 8.6021 | 8.9405 | 8.9267 | 8.602 | 8.9408 | 8.927 | 8.6021
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 7.8209 | 7.8103 | 7.5344 | 7.8209 | 7.8104 | 7.5345 | 7.8209 | 7.8104 | 7.5345 | 7.8209 | 7.8104 | 7.5344 | 7.8209 | 7.8104 | 7.5345
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.872 | 0.87217 | 0.87298 | 0.87192 | 0.87209 | 0.87291 | 0.87192 | 0.87209 | 0.87291 | 0.87193 | 0.8721 | 0.87291 | 0.87191 | 0.87208 | 0.87291
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0403 | 1.0404 | 1.0383 | 1.0395 | 1.0396 | 1.0376 | 1.0395 | 1.0396 | 1.0376 | 1.0396 | 1.0397 | 1.0377 | 1.0394 | 1.0395 | 1.0376
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Contingency Outage | 6327_Broadlea - Isaac Plains 66 kV | 6327_Broadlea - Isaac Plains 66 kV | 232_Newlands-Glenden 66 kV | 6327_Broadlea - Isaac Plains 66 kV | PV 6/4_Glenella No 2 66 kV | 232_Newlands-Glenden 66 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 232_Newlands-Glenden 66 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 232_Newlands-Glenden 66 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 232_Newlands-Glenden 66 kV
NQ | 6321_Lucinda 66 kV | % of Rated A | 22.1% | 22.58% | 20.19% | 22.3% | 22.6% | 20.26% | 22.15% | 22.57% | 20.25% | 21.76% | 22.19% | 20.01% | 22.29% | 22.63% | 20.25%
NQ | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2
NQ | 6321_Lucinda 66 kV | Loading (A) | 43.983 | 50.3432 | 41.1908 | 44.379 | 50.405 | 41.3282 | 44.0826 | 50.3305 | 41.2999 | 43.3106 | 49.4907 | 40.8197 | 44.3638 | 50.4569 | 41.3085
NQ | 6321_Lucinda 66 kV | Loading (MVA) | 5.2004 | 5.9128 | 4.8409 | 5.201 | 5.9132 | 4.8397 | 5.2 | 5.9127 | 4.8395 | 5.1114 | 5.8114 | 4.7845 | 5.2009 | 5.9135 | 4.8396
NQ | 6321_Lucinda 66 kV | Loading (MW) | 4.9242 | 5.5823 | 4.5471 | 4.9242 | 5.5824 | 4.5469 | 4.9241 | 5.5823 | 4.5469 | 4.8402 | 5.4872 | 4.4949 | 4.9242 | 5.5824 | 4.5469
NQ | 6321_Lucinda 66 kV | Power Factor | 0.94668 | 0.94385 | 0.93911 | 0.94658 | 0.9438 | 0.93929 | 0.94673 | 0.94386 | 0.93932 | 0.94673 | 0.94397 | 0.93925 | 0.94659 | 0.94376 | 0.93931
NQ | 6321_Lucinda 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 6321_Lucinda 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6321_Lucinda 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0343 | 1.0274 | 1.0281 | 1.0252 | 1.0262 | 1.0244 | 1.0319 | 1.0277 | 1.0251 | 1.0324 | 1.0272 | 1.0253 | 1.0255 | 1.0252 | 1.0249
NQ | 6321_Lucinda 66 kV | Contingency Outage | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 40.08% | 43.1% | 24.53% | 298.4% | 43.16% | 24.56% | 40.61% | 253.8% | 24.76% | 40.58% | 43.68% | 24.66% | 298.6% | 270.2% | 25.18%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 78407_1 | TR_LINE 78407_1 | TR_LINE 31691_1 | TR_LINE 32480_1 | TR_LINE 78407_1 | TR_LINE 31691_1 | TR_LINE 78407_1 | TR_LINE 143680_1 | TR_LINE 31691_1 | TR_LINE 78407_1 | TR_LINE 78407_1 | TR_LINE 31691_1 | TR_LINE 32480_1 | TR_LINE 32480_1 | TR_LINE 31691_1
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 52.9045 | 71.9766 | 45.6179 | 564.0055 | 72.0751 | 45.6892 | 53.6085 | 522.8448 | 46.0517 | 53.5709 | 72.9413 | 45.8643 | 564.3943 | 556.5106 | 46.8327
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 6.0909 | 8.1015 | 5.4707 | 59.1513 | 8.1021 | 5.4632 | 6.1613 | 49.2429 | 5.5065 | 6.1614 | 8.2027 | 5.4853 | 59.2017 | 58.543 | 5.5984
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 6.0841 | 8.075 | 4.9218 | 33.6014 | 8.0754 | 4.9231 | 6.154 | 17.9871 | 4.9756 | 6.1542 | 8.1749 | 4.9421 | 33.8547 | 34.197 | 5.0868
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.99888 | 0.99672 | 0.89966 | 0.56795 | 0.9967 | 0.90113 | 0.99882 | 0.36331 | 0.90358 | 0.99882 | 0.99662 | 0.90097 | 0.57174 | 0.58404 | 0.9086
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 132 | 167 | 186 | 189 | 167 | 186 | 132 | 206 | 186 | 132 | 167 | 186 | 189 | 206 | 186
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0071 | 0.98456 | 1.0491 | 0.9169 | 0.98328 | 1.046 | 1.0053 | 0.82036 | 1.046 | 1.0061 | 0.98367 | 1.0462 | 0.91705 | 0.9197 | 1.0457
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Contingency Outage | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 10.94% | 9.306% | 4.169% | 11.01% | 9.317% | 4.183% | 10.94% | 9.304% | 4.181% | 10.39% | 8.84% | 3.974% | 11.01% | 9.325% | 4.182%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 14.6534 | 16.8441 | 7.2963 | 14.7582 | 16.8635 | 7.3211 | 14.6639 | 16.8402 | 7.3167 | 13.9209 | 16.0006 | 6.9542 | 14.7534 | 16.8786 | 7.318
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 1.7477 | 2.0015 | 0.87055 | 1.7478 | 2.0015 | 0.87047 | 1.7477 | 2.0015 | 0.87049 | 1.6598 | 1.9007 | 0.82752 | 1.7478 | 2.0014 | 0.87048
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 1.7471 | 1.9998 | 0.86817 | 1.7471 | 1.9998 | 0.86818 | 1.7471 | 1.9998 | 0.86818 | 1.6595 | 1.8994 | 0.8247 | 1.7471 | 1.9997 | 0.86818
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.99953 | 0.99901 | 0.99727 | 0.9995 | 0.999 | 0.99736 | 0.99953 | 0.99901 | 0.99735 | 0.99968 | 0.99921 | 0.99659 | 0.99951 | 0.99901 | 0.99735
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0433 | 1.0394 | 1.0437 | 1.036 | 1.0383 | 1.04 | 1.0426 | 1.0397 | 1.0407 | 1.043 | 1.0391 | 1.0409 | 1.0363 | 1.0373 | 1.0405
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Contingency Outage | 6321_Lucinda 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 26.05% | 25.81% | 41.19% | 26.28% | 25.84% | 41.33% | 26.11% | 25.8% | 41.3% | 25.72% | 25.43% | 41.07% | 26.27% | 25.87% | 41.31%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 51.8306 | 57.5508 | 84.0232 | 52.3041 | 57.6221 | 84.3132 | 51.9501 | 57.5362 | 84.2562 | 51.1757 | 56.7008 | 83.7766 | 52.2859 | 57.682 | 84.2735
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 6.169 | 6.8115 | 9.9377 | 6.1712 | 6.8121 | 9.9368 | 6.169 | 6.8113 | 9.9363 | 6.0792 | 6.7085 | 9.8817 | 6.1711 | 6.8127 | 9.9365
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 5.7395 | 6.3398 | 8.5378 | 5.74 | 6.3399 | 8.5377 | 5.7395 | 6.3397 | 8.5376 | 5.6546 | 6.2435 | 8.4851 | 5.74 | 6.3401 | 8.5377
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.93034 | 0.93072 | 0.85911 | 0.93009 | 0.93065 | 0.85918 | 0.93034 | 0.93073 | 0.85921 | 0.93013 | 0.93065 | 0.85864 | 0.93011 | 0.93059 | 0.8592
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0412 | 1.0353 | 1.0346 | 1.0321 | 1.0342 | 1.0309 | 1.0388 | 1.0356 | 1.0316 | 1.0391 | 1.035 | 1.0318 | 1.0325 | 1.0332 | 1.0314
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Contingency Outage | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ | 118_Cannonvale No 2 66 kV | % of Rated A | 86.16% | 62.78% | 45.09% | 86.17% | 62.78% | 45.09% | 85.82% | 62.52% | 44.99% | 85.47% | 62.26% | 44.89% | 86.53% | 63.06% | 45.28%
NQ | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1
NQ | 118_Cannonvale No 2 66 kV | Loading (A) | 166.2962 | 172.0035 | 120.3921 | 166.3015 | 172.0155 | 120.3909 | 165.6306 | 171.3028 | 120.1258 | 164.953 | 170.5789 | 119.8632 | 167.0082 | 172.7787 | 120.8861
NQ | 118_Cannonvale No 2 66 kV | Loading (MVA) | 19.4756 | 20.2482 | 14.0578 | 19.475 | 20.2472 | 14.0568 | 19.3976 | 20.1642 | 14.0262 | 19.3215 | 20.0828 | 13.9967 | 19.5491 | 20.3261 | 14.2752
NQ | 118_Cannonvale No 2 66 kV | Loading (MW) | 18.2129 | 19.1069 | 10.5191 | 18.2129 | 19.107 | 10.5191 | 18.1156 | 19.0047 | 10.4641 | 18.0182 | 18.9024 | 10.4091 | 18.3105 | 19.2097 | 10.5756
NQ | 118_Cannonvale No 2 66 kV | Power Factor | 0.93509 | 0.94356 | 0.7482 | 0.93512 | 0.94362 | 0.74826 | 0.93383 | 0.94243 | 0.74596 | 0.93248 | 0.94115 | 0.74361 | 0.93657 | 0.945 | 0.74077
NQ | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267
NQ | 118_Cannonvale No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 118_Cannonvale No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0244 | 1.0297 | 1.0214 | 1.0244 | 1.0296 | 1.0214 | 1.0244 | 1.0296 | 1.0214 | 1.0246 | 1.0298 | 1.0215 | 1.0239 | 1.029 | 1.033
NQ | 118_Cannonvale No 2 66 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV
NQ | 119_Cannonvale No 1 66 kV | % of Rated A | 180.4% | 128.4% | 79.37% | 180.9% | 128.7% | 79.55% | 180.4% | 128.4% | 79.38% | 179.9% | 128% | 79.2% | 182.5% | 130% | 79.22%
NQ | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQ | 119_Cannonvale No 1 66 kV | Loading (A) | 333.7011 | 332.4748 | 200.0029 | 334.6727 | 333.4171 | 200.4603 | 333.7172 | 332.4999 | 200.0292 | 332.7354 | 331.5783 | 199.5902 | 337.6246 | 336.6976 | 199.622
NQ | 119_Cannonvale No 1 66 kV | Loading (MVA) | 38.2631 | 38.0261 | 22.9881 | 38.3647 | 38.144 | 23.0374 | 38.2624 | 38.0381 | 22.9888 | 38.1599 | 37.9224 | 22.9407 | 38.6692 | 38.4713 | 23.1929
NQ | 119_Cannonvale No 1 66 kV | Loading (MW) | 38.2441 | 38.0038 | 21.9796 | 38.3471 | 38.112 | 22.0369 | 38.2431 | 38.004 | 21.9801 | 38.1387 | 37.8979 | 21.9233 | 38.6555 | 38.4465 | 22.192
NQ | 119_Cannonvale No 1 66 kV | Power Factor | 0.99937 | 0.99927 | 0.95547 | 0.99942 | 0.99899 | 0.95591 | 0.99936 | 0.99893 | 0.95546 | 0.99931 | 0.99921 | 0.95498 | 0.99953 | 0.9992 | 0.9562
NQ | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252
NQ | 119_Cannonvale No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 119_Cannonvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0005 | 0.99798 | 1.0047 | 1.0002 | 0.99827 | 1.0045 | 1.0004 | 0.99826 | 1.0046 | 1.0007 | 0.99797 | 1.0047 | 0.99931 | 0.99698 | 1.0155
NQ | 119_Cannonvale No 1 66 kV | Contingency Outage | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV
NQ | 120_Prosperpine - Calen 66 kV | % of Rated A | 21.18% | 26.24% | 15.38% | 22.01% | 27.27% | 15.93% | 22% | 27.28% | 15.92% | 22% | 27.27% | 15.92% | 22.02% | 27.28% | 15.78%
NQ | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1
NQ | 120_Prosperpine - Calen 66 kV | Loading (A) | 27.9639 | 46.4396 | 26.1389 | 29.0473 | 48.2739 | 27.0726 | 29.0464 | 48.2776 | 27.0723 | 29.0425 | 48.2642 | 27.0707 | 29.0644 | 48.2887 | 26.8286
NQ | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 3.2268 | 5.2835 | 3.0077 | 3.3512 | 5.4866 | 3.1148 | 3.3513 | 5.4866 | 3.1148 | 3.3513 | 5.4865 | 3.1148 | 3.3511 | 5.4867 | 3.1171
NQ | 120_Prosperpine - Calen 66 kV | Loading (MW) | 3.1872 | 5.2777 | 2.9675 | 3.3162 | 5.4794 | 3.0789 | 3.3162 | 5.4794 | 3.0789 | 3.3161 | 5.4793 | 3.0789 | 3.3162 | 5.4794 | 3.0779
NQ | 120_Prosperpine - Calen 66 kV | Power Factor | 0.98772 | 0.99888 | 0.98662 | 0.98953 | 0.99867 | 0.98849 | 0.98953 | 0.99867 | 0.98849 | 0.98951 | 0.99867 | 0.98848 | 0.98959 | 0.99866 | 0.98742
NQ | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
NQ | 120_Prosperpine - Calen 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 120_Prosperpine - Calen 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0094 | 0.99517 | 1.0066 | 1.0092 | 0.99415 | 1.0064 | 1.0093 | 0.99408 | 1.0064 | 1.0094 | 0.99434 | 1.0065 | 1.0086 | 0.99386 | 1.0163
NQ | 120_Prosperpine - Calen 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | 118_Cannonvale No 2 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV
NQ | 426_Mt Rooper 66 kV | % of Rated A | 49.14% | 38.82% | 25.04% | 49.17% | 38.79% | 25.05% | 49.14% | 38.78% | 25.05% | 49.12% | 38.81% | 25.04% | 49.23% | 38.88% | 24.76%
NQ | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1
NQ | 426_Mt Rooper 66 kV | Loading (A) | 122.3575 | 108.6856 | 70.1175 | 122.4266 | 108.6046 | 70.1368 | 122.3686 | 108.5813 | 70.1261 | 122.2988 | 108.6648 | 70.1105 | 122.5809 | 108.8575 | 69.3392
NQ | 426_Mt Rooper 66 kV | Loading (MVA) | 13.3633 | 11.8114 | 7.9209 | 13.3638 | 11.8111 | 7.921 | 13.3634 | 11.811 | 7.9209 | 13.3629 | 11.8113 | 7.9209 | 13.3586 | 11.8122 | 7.9185
NQ | 426_Mt Rooper 66 kV | Loading (MW) | 13.1461 | 11.5821 | 7.8005 | 13.1463 | 11.582 | 7.8006 | 13.1461 | 11.582 | 7.8006 | 13.146 | 11.5821 | 7.8005 | 13.1442 | 11.5825 | 7.7997
NQ | 426_Mt Rooper 66 kV | Power Factor | 0.98375 | 0.98012 | 0.98412 | 0.98372 | 0.98014 | 0.98411 | 0.98374 | 0.98014 | 0.98412 | 0.98376 | 0.98012 | 0.98412 | 0.98395 | 0.98008 | 0.9843
NQ | 426_Mt Rooper 66 kV | Rating (A) | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280
NQ | 426_Mt Rooper 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 426_Mt Rooper 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95537 | 0.95066 | 0.9882 | 0.95486 | 0.95134 | 0.98793 | 0.95528 | 0.95154 | 0.98808 | 0.9558 | 0.95084 | 0.98829 | 0.95329 | 0.94923 | 0.99899
NQ | 426_Mt Rooper 66 kV | Contingency Outage | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV
NQ | CANN_JUPO (Ex119&118) | % of Rated A | 61.57% | 58.02% | 34.99% | 61.9% | 58.31% | 35.17% | 61.87% | 58.29% | 35.17% | 61.84% | 58.34% | 35.16% | 62.59% | 59.1% | 35.11%
NQ | CANN_JUPO (Ex119&118) | Limiting Line Name | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1
NQ | CANN_JUPO (Ex119&118) | Loading (A) | 172.3826 | 162.4606 | 97.9836 | 173.324 | 163.2579 | 98.4884 | 173.2431 | 163.2231 | 98.4734 | 173.1458 | 163.3475 | 98.4516 | 175.2637 | 165.4736 | 98.3206
NQ | CANN_JUPO (Ex119&118) | Loading (MVA) | 18.8797 | 17.757 | 11.1055 | 18.973 | 17.8571 | 11.1599 | 18.9726 | 17.8569 | 11.1598 | 18.972 | 17.8575 | 11.1597 | 19.1544 | 18.0602 | 11.2647
NQ | CANN_JUPO (Ex119&118) | Loading (MW) | 18.6814 | 17.5986 | 11.0696 | 18.7734 | 17.6978 | 11.1235 | 18.7732 | 17.6977 | 11.1235 | 18.773 | 17.698 | 11.1235 | 18.955 | 17.8973 | 11.2302
NQ | CANN_JUPO (Ex119&118) | Power Factor | 0.9885 | 0.99005 | 0.99534 | 0.98848 | 0.99006 | 0.99532 | 0.98849 | 0.99006 | 0.99533 | 0.98851 | 0.99004 | 0.99533 | 0.98859 | 0.98996 | 0.99551
NQ | CANN_JUPO (Ex119&118) | Rating (A) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
NQ | CANN_JUPO (Ex119&118) | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CANN_JUPO (Ex119&118) | Min Voltage at Constrained Conductor (pu) | 0.95807 | 0.95613 | 0.99147 | 0.95758 | 0.95682 | 0.99122 | 0.958 | 0.95702 | 0.99136 | 0.95851 | 0.95632 | 0.99158 | 0.95603 | 0.95475 | 1.0022
NQ | CANN_JUPO (Ex119&118) | Contingency Outage | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 70.25% | 71.14% | 60.1% | 70.09% | 70.99% | 60% | 70.05% | 70.96% | 59.97% | 69.76% | 70.64% | 59.78% | 70.57% | 71.51% | 59.35%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 136.9784 | 155.0857 | 119.5975 | 136.6763 | 154.7504 | 119.3999 | 136.6034 | 154.6894 | 119.3408 | 136.0333 | 153.9996 | 118.964 | 137.6135 | 155.8819 | 118.1068
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 16.1618 | 18.3234 | 14.1262 | 16.1262 | 18.2836 | 14.1029 | 16.1177 | 18.2763 | 14.0959 | 16.0521 | 18.1972 | 14.0522 | 16.2323 | 18.411 | 14.0187
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 15.842 | 18.002 | 13.8881 | 15.8043 | 17.9598 | 13.8637 | 15.7959 | 17.9527 | 13.8571 | 15.7255 | 17.8679 | 13.811 | 15.9199 | 18.0983 | 13.6078
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.9802 | 0.98245 | 0.98314 | 0.98003 | 0.98228 | 0.98304 | 0.98002 | 0.98229 | 0.98305 | 0.97964 | 0.98189 | 0.98283 | 0.98074 | 0.983 | 0.97068
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0321 | 1.0335 | 1.0332 | 1.0321 | 1.0335 | 1.0332 | 1.0321 | 1.0335 | 1.0332 | 1.0322 | 1.0336 | 1.0332 | 1.0318 | 1.0331 | 1.0383
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 32.15% | 27.54% | 19.82% | 32.24% | 27.64% | 19.88% | 32.18% | 27.6% | 19.84% | 32.05% | 27.49% | 19.77% | 32.65% | 28% | 20.08%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 62.0529 | 65.8183 | 43.2089 | 62.221 | 66.0581 | 43.3363 | 62.1036 | 65.9666 | 43.2413 | 61.8617 | 65.7114 | 43.0984 | 63.0224 | 66.9133 | 43.7713
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 7.2687 | 7.7191 | 5.0786 | 7.288 | 7.7468 | 5.0934 | 7.2748 | 7.7351 | 5.0823 | 7.2472 | 7.7067 | 5.0657 | 7.3791 | 7.843 | 5.1439
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 7.081 | 7.2433 | 4.9222 | 7.1017 | 7.2749 | 4.938 | 7.0885 | 7.264 | 4.9276 | 7.0571 | 7.2266 | 4.9089 | 7.2054 | 7.3992 | 4.9959
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.97418 | 0.93836 | 0.9692 | 0.97443 | 0.9391 | 0.96948 | 0.97439 | 0.93909 | 0.96956 | 0.97376 | 0.93771 | 0.96906 | 0.97646 | 0.94341 | 0.97122
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0123 | 1.0258 | 1.0281 | 1.0122 | 1.0257 | 1.028 | 1.0123 | 1.0256 | 1.0281 | 1.0126 | 1.0258 | 1.0281 | 1.0114 | 1.0252 | 1.0279
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 61.39% | 63.48% | 68.55% | 61.13% | 63.19% | 68.38% | 61.12% | 63.2% | 68.38% | 60.84% | 62.86% | 68.19% | 61.45% | 63.58% | 68.59%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1 | TR_LINE 31892_1
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 169.4416 | 200.6072 | 199.4889 | 168.7153 | 199.6811 | 198.9903 | 168.6991 | 199.7042 | 198.9877 | 167.9141 | 198.6503 | 198.4461 | 169.6048 | 200.9158 | 199.5965
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 19.6063 | 23.2999 | 23.2023 | 19.52 | 23.188 | 23.1425 | 19.52 | 23.1882 | 23.1425 | 19.434 | 23.0752 | 23.0824 | 19.6061 | 23.303 | 23.2032
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 19.4999 | 23.2874 | 23.1965 | 19.4098 | 23.1738 | 23.1362 | 19.4096 | 23.1741 | 23.1362 | 19.3189 | 23.0589 | 23.0756 | 19.5017 | 23.2915 | 23.1975
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.99456 | 0.99946 | 0.99974 | 0.99434 | 0.99938 | 0.99972 | 0.99433 | 0.99939 | 0.99972 | 0.99406 | 0.99929 | 0.9997 | 0.99466 | 0.9995 | 0.99975
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 276 | 316 | 291 | 276 | 316 | 291 | 276 | 316 | 291 | 276 | 316 | 291 | 276 | 316 | 291
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0121 | 1.0159 | 1.0173 | 1.012 | 1.0157 | 1.0172 | 1.0121 | 1.0156 | 1.0172 | 1.0123 | 1.016 | 1.0173 | 1.0111 | 1.0144 | 1.0168
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 16.34% | 14.52% | 8.249% | 16.34% | 14.53% | 8.25% | 16.48% | 14.65% | 8.318% | 16.47% | 14.64% | 8.318% | 16.89% | 15.01% | 8.441%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 28.9166 | 34.2705 | 18.6425 | 28.9214 | 34.2811 | 18.645 | 29.1609 | 34.569 | 18.7994 | 29.1567 | 34.5601 | 18.7982 | 29.9025 | 35.4332 | 19.0762
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 3.3366 | 3.9606 | 2.1451 | 3.3366 | 3.9606 | 2.1451 | 3.3643 | 3.9936 | 2.1629 | 3.3643 | 3.9936 | 2.1629 | 3.4476 | 4.0926 | 2.2163
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 3.2725 | 3.8804 | 2.108 | 3.2725 | 3.8804 | 2.108 | 3.2995 | 3.9125 | 2.1255 | 3.2995 | 3.9125 | 2.1255 | 3.3807 | 4.0087 | 2.1777
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.98078 | 0.97973 | 0.98272 | 0.98078 | 0.97973 | 0.98272 | 0.98073 | 0.97967 | 0.98269 | 0.98073 | 0.97967 | 0.98269 | 0.98058 | 0.97949 | 0.98258
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0094 | 1.011 | 1.0065 | 1.0092 | 1.0107 | 1.0064 | 1.0092 | 1.0106 | 1.0064 | 1.0094 | 1.0108 | 1.0065 | 1.0086 | 1.0104 | 1.0163
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | 118_Cannonvale No 2 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV
NQ | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 32.73% | 29.1% | 16.52% | 32.73% | 29.11% | 16.52% | 33% | 29.35% | 16.65% | 33% | 29.35% | 16.65% | 33.85% | 30.09% | 16.9%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 57.9272 | 68.6732 | 37.3241 | 57.937 | 68.6947 | 37.329 | 58.4175 | 69.2727 | 37.6385 | 58.4091 | 69.2547 | 37.636 | 59.9058 | 71.0079 | 38.1938
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 6.6838 | 7.9363 | 4.2946 | 6.6838 | 7.9364 | 4.2946 | 6.7395 | 8.0026 | 4.3302 | 6.7394 | 8.0025 | 4.3302 | 6.9066 | 8.2013 | 4.4373
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 6.5556 | 7.7759 | 4.2205 | 6.5556 | 7.7759 | 4.2205 | 6.6099 | 7.8403 | 4.2554 | 6.6099 | 7.8403 | 4.2554 | 6.7728 | 8.0335 | 4.3602
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.98081 | 0.97977 | 0.98274 | 0.98081 | 0.97977 | 0.98274 | 0.98076 | 0.97971 | 0.98271 | 0.98077 | 0.97971 | 0.98271 | 0.98062 | 0.97953 | 0.98261
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0093 | 1.0109 | 1.0065 | 1.0092 | 1.0106 | 1.0064 | 1.0092 | 1.0105 | 1.0064 | 1.0093 | 1.0108 | 1.0065 | 1.0085 | 1.0103 | 1.0163
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV | 118_Cannonvale No 2 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV
NQ | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 25.13% | 22.19% | 22.76% | 25.16% | 22.22% | 22.78% | 25.28% | 22.32% | 22.88% | 25.25% | 22.29% | 22.86% | 25.3% | 22.35% | 22.9%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 214.8233 | 206.3426 | 198.4734 | 215.0824 | 206.6293 | 198.6001 | 216.1216 | 207.575 | 199.5049 | 215.8578 | 207.2828 | 199.376 | 216.3518 | 207.8615 | 199.6449
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 81.361 | 78.4407 | 75.6641 | 81.4534 | 78.5436 | 75.7102 | 81.4978 | 78.5758 | 75.7424 | 81.4053 | 78.4726 | 75.6962 | 81.5841 | 78.6743 | 75.7911
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 79.2795 | 76.6458 | 73.8515 | 79.3707 | 76.7471 | 73.8976 | 79.3733 | 76.7489 | 73.8989 | 79.2821 | 76.6475 | 73.8528 | 79.4708 | 76.8441 | 73.9458
NQ | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.97319 | 0.97595 | 0.97492 | 0.97321 | 0.97596 | 0.97494 | 0.9727 | 0.97557 | 0.97453 | 0.97268 | 0.97556 | 0.97452 | 0.97286 | 0.97555 | 0.97452
NQ | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872
NQ | 7018_Mica Creek C - Chumvale 220 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 7018_Mica Creek C - Chumvale 220 kV | Min Voltage at Constrained Conductor (pu) | 0.99392 | 0.99763 | 1.0005 | 0.99385 | 0.99755 | 1.0004 | 0.98961 | 0.99341 | 0.99633 | 0.9897 | 0.99351 | 0.99636 | 0.9896 | 0.99329 | 0.99627
NQ | 7018_Mica Creek C - Chumvale 220 kV | Contingency Outage | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 40.12% | 37.69% | 18.63% | 40.62% | 38.18% | 18.87% | 40.6% | 38.35% | 18.94% | 40.1% | 37.85% | 18.7% | 41.15% | 38.56% | 19.18%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 65.4008 | 68.5931 | 32.0506 | 66.2145 | 69.4955 | 32.4566 | 66.1744 | 69.791 | 32.5682 | 65.3562 | 68.8832 | 32.1613 | 67.0725 | 70.1749 | 32.9889
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 7.3497 | 7.7337 | 3.6448 | 7.4396 | 7.8337 | 3.6906 | 7.4395 | 7.8336 | 3.6908 | 7.3496 | 7.7336 | 3.645 | 7.5374 | 7.9315 | 3.7379
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 7.2803 | 7.6633 | 3.6244 | 7.3698 | 7.7627 | 3.6701 | 7.3698 | 7.7627 | 3.6701 | 7.2803 | 7.6633 | 3.6245 | 7.4654 | 7.8579 | 3.7165
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.99048 | 0.99082 | 0.9942 | 0.99054 | 0.99087 | 0.99424 | 0.99055 | 0.99088 | 0.99422 | 0.99049 | 0.99083 | 0.99417 | 0.99037 | 0.99066 | 0.99407
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98258 | 0.98577 | 0.99473 | 0.98237 | 0.98553 | 0.99462 | 0.98295 | 0.98134 | 0.99124 | 0.98323 | 0.98159 | 0.99134 | 0.98254 | 0.98817 | 0.9911
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Contingency Outage | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 89.12% | 58.39% | 23.52% | 90.56% | 59.47% | 23.8% | 91.14% | 59.88% | 24.16% | 89.63% | 58.8% | 23.87% | 92.85% | 61.03% | 24.45%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 167387_1 | TR_LINE 167387_1 | TR_LINE 234732_1 | TR_LINE 167387_1 | TR_LINE 167387_1 | TR_LINE 234732_1 | TR_LINE 167387_1 | TR_LINE 167387_1 | TR_LINE 234732_1 | TR_LINE 167387_1 | TR_LINE 167387_1 | TR_LINE 234732_1 | TR_LINE 167387_1 | TR_LINE 167387_1 | TR_LINE 234732_1
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 73.972 | 79.4143 | 33.1594 | 75.1652 | 80.8838 | 33.5565 | 75.6478 | 81.434 | 34.0677 | 74.3943 | 79.9663 | 33.6591 | 77.0655 | 83.0066 | 34.477
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 7.9035 | 8.3731 | 3.9947 | 8.0108 | 8.4982 | 4.0413 | 8.0193 | 8.5083 | 4.0338 | 7.9095 | 8.384 | 3.9867 | 8.1395 | 8.6342 | 4.0803
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 7.8525 | 8.3106 | 3.8844 | 7.9576 | 8.4316 | 3.9347 | 7.9644 | 8.4398 | 3.9415 | 7.8577 | 8.319 | 3.891 | 8.0796 | 8.5589 | 3.9928
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.99345 | 0.99247 | 0.9724 | 0.99327 | 0.9921 | 0.97363 | 0.99307 | 0.99189 | 0.9771 | 0.99336 | 0.99219 | 0.97597 | 0.99256 | 0.99123 | 0.97856
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.93297 | 0.92049 | 1.0537 | 0.93058 | 0.91721 | 1.0534 | 0.9256 | 0.91206 | 1.0356 | 0.92835 | 0.91529 | 1.036 | 0.92215 | 0.90797 | 1.0351
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Contingency Outage | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 36.08% | 31.98% | 16.71% | 36.08% | 31.98% | 16.71% | 36.22% | 32.1% | 16.77% | 36.02% | 31.92% | 16.68% | 36.72% | 32.55% | 17%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 138.547 | 157.0125 | 77.2075 | 138.5494 | 157.0154 | 77.208 | 139.0787 | 157.62 | 77.4943 | 138.3092 | 156.7447 | 77.0726 | 141.001 | 159.8061 | 78.5482
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 32.4422 | 36.7673 | 18.1715 | 32.4422 | 36.7673 | 18.1715 | 32.445 | 36.771 | 18.172 | 32.2671 | 36.5689 | 18.0733 | 32.8898 | 37.2763 | 18.4185
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 32.3062 | 36.5677 | 18.1705 | 32.3062 | 36.5677 | 18.1705 | 32.3067 | 36.5684 | 18.1707 | 32.1312 | 36.3696 | 18.0723 | 32.7453 | 37.0652 | 18.4169
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.9958 | 0.99457 | 0.99994 | 0.9958 | 0.99457 | 0.99994 | 0.99573 | 0.99449 | 0.99993 | 0.99579 | 0.99455 | 0.99994 | 0.9956 | 0.99434 | 0.9999
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0242 | 1.0242 | 1.0294 | 1.0242 | 1.0242 | 1.0294 | 1.0204 | 1.0204 | 1.0256 | 1.0204 | 1.0204 | 1.0256 | 1.0202 | 1.0202 | 1.0256
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Contingency Outage | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 49.66% | 45.51% | 22.99% | 49.66% | 45.51% | 22.99% | 49.85% | 45.69% | 23.08% | 49.58% | 45.43% | 22.95% | 50.54% | 46.32% | 23.39%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 138.5525 | 157.0119 | 77.258 | 138.5546 | 157.0148 | 77.2585 | 139.0839 | 157.619 | 77.5463 | 138.3145 | 156.7439 | 77.1233 | 141.0056 | 159.8041 | 78.6033
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 32.4426 | 36.7679 | 18.1631 | 32.4426 | 36.7679 | 18.1631 | 32.4454 | 36.7715 | 18.1636 | 32.2675 | 36.5695 | 18.065 | 32.8902 | 37.2769 | 18.4104
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 32.3067 | 36.5683 | 18.154 | 32.3067 | 36.5683 | 18.154 | 32.3071 | 36.5689 | 18.154 | 32.1317 | 36.3702 | 18.0558 | 32.7458 | 37.0658 | 18.3997
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.9958 | 0.99457 | 0.99949 | 0.9958 | 0.99457 | 0.99949 | 0.99573 | 0.99449 | 0.99947 | 0.99578 | 0.99455 | 0.99949 | 0.9956 | 0.99434 | 0.99942
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0241 | 1.0242 | 1.0283 | 1.0241 | 1.0242 | 1.0283 | 1.0203 | 1.0204 | 1.0245 | 1.0204 | 1.0204 | 1.0245 | 1.0202 | 1.0203 | 1.0244
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Contingency Outage | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV
NQ | MICC-MICB No 1 132 kV | % of Rated A | 93.34% | 66.03% | 63.41% | 93.42% | 66.1% | 63.44% | 93.83% | 66.37% | 63.69% | 93.75% | 66.31% | 63.66% | 93.93% | 66.44% | 63.72%
NQ | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ | MICC-MICB No 1 132 kV | Loading (A) | 487.2231 | 474.7726 | 456.5803 | 487.6496 | 475.2362 | 456.7853 | 489.8148 | 477.2237 | 458.5511 | 489.3763 | 476.7488 | 458.3413 | 490.3041 | 477.7028 | 458.7703
NQ | MICC-MICB No 1 132 kV | Loading (MVA) | 114.1536 | 111.3222 | 107.3014 | 114.251 | 111.4282 | 107.3486 | 114.3253 | 111.4744 | 107.362 | 114.2271 | 111.3679 | 107.3146 | 114.4322 | 111.5785 | 107.4103
NQ | MICC-MICB No 1 132 kV | Loading (MW) | 113.9871 | 111.285 | 107.3003 | 114.0809 | 111.3891 | 107.3475 | 114.0991 | 111.4078 | 107.3612 | 114.0052 | 111.3037 | 107.3139 | 114.1999 | 111.5082 | 107.4093
NQ | MICC-MICB No 1 132 kV | Power Factor | 0.99854 | 0.99967 | 0.99999 | 0.99851 | 0.99965 | 0.99999 | 0.99802 | 0.9994 | 0.99999 | 0.99806 | 0.99942 | 0.99999 | 0.99797 | 0.99937 | 0.99999
NQ | MICC-MICB No 1 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | MICC-MICB No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MICC-MICB No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0247 | 1.0255 | 1.0278 | 1.0247 | 1.0255 | 1.0278 | 1.0208 | 1.0216 | 1.024 | 1.0208 | 1.0216 | 1.024 | 1.0207 | 1.0215 | 1.024
NQ | MICC-MICB No 1 132 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV
NQ | MICC-MICB No 2 132 kV | % of Rated A | 93.33% | 66.03% | 63.41% | 93.41% | 66.09% | 63.44% | 93.83% | 66.37% | 63.69% | 93.74% | 66.3% | 63.66% | 93.92% | 66.44% | 63.72%
NQ | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ | MICC-MICB No 2 132 kV | Loading (A) | 487.1957 | 474.7579 | 456.5709 | 487.6219 | 475.218 | 456.7758 | 489.784 | 477.203 | 458.5397 | 489.3458 | 476.7284 | 458.3299 | 490.273 | 477.6818 | 458.7587
NQ | MICC-MICB No 2 132 kV | Loading (MVA) | 114.1492 | 111.3203 | 107.3006 | 114.2465 | 111.4257 | 107.3478 | 114.3202 | 111.4714 | 107.3608 | 114.2221 | 111.3649 | 107.3134 | 114.4271 | 111.5754 | 107.4091
NQ | MICC-MICB No 2 132 kV | Loading (MW) | 113.9858 | 111.2843 | 107.2992 | 114.0796 | 111.3879 | 107.3465 | 114.0978 | 111.4065 | 107.3602 | 114.0038 | 111.3025 | 107.3128 | 114.1985 | 111.507 | 107.4083
NQ | MICC-MICB No 2 132 kV | Power Factor | 0.99857 | 0.99968 | 0.99999 | 0.99854 | 0.99966 | 0.99999 | 0.99805 | 0.99942 | 0.99999 | 0.99809 | 0.99944 | 0.99999 | 0.998 | 0.99939 | 0.99999
NQ | MICC-MICB No 2 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | MICC-MICB No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MICC-MICB No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0247 | 1.0255 | 1.0279 | 1.0247 | 1.0255 | 1.0278 | 1.0208 | 1.0216 | 1.024 | 1.0209 | 1.0217 | 1.024 | 1.0207 | 1.0216 | 1.024
NQ | MICC-MICB No 2 132 kV | Contingency Outage | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV
NQ | 6127_Bohle-Black River 1 66 kV | % of Rated A | 32.46% | 43.82% | 21.03% | 32.95% | 44.28% | 21.35% | 33.55% | 45.28% | 21.83% | 34.12% | 46.06% | 22.19% | 35.42% | 47.97% | 22.95%
NQ | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ | 6127_Bohle-Black River 1 66 kV | Loading (A) | 236.6314 | 343.1205 | 149.3381 | 240.2109 | 346.7206 | 151.5517 | 244.5944 | 354.5218 | 154.9799 | 248.7454 | 360.6611 | 157.5429 | 258.2077 | 375.5717 | 162.9266
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 28.1135 | 40.4351 | 17.8946 | 28.3885 | 40.8465 | 18.0684 | 29.0159 | 41.773 | 18.465 | 29.5004 | 42.4779 | 18.7676 | 30.6253 | 44.129 | 19.4769
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 28.0415 | 40.1573 | 17.8888 | 28.3145 | 40.5576 | 18.0617 | 28.9332 | 41.4606 | 18.457 | 29.4117 | 42.1574 | 18.7587 | 30.5233 | 43.7611 | 19.4659
NQ | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.99744 | 0.99313 | 0.99968 | 0.99739 | 0.99293 | 0.99963 | 0.99715 | 0.99252 | 0.99957 | 0.99699 | 0.99245 | 0.99952 | 0.99667 | 0.99166 | 0.99944
NQ | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 6127_Bohle-Black River 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6127_Bohle-Black River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0393 | 1.0309 | 1.0482 | 1.0338 | 1.0305 | 1.0429 | 1.0377 | 1.0307 | 1.0422 | 1.0374 | 1.0303 | 1.0421 | 1.0375 | 1.0278 | 1.0457
NQ | 6127_Bohle-Black River 1 66 kV | Contingency Outage | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV
NQ | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 32.46% | 43.82% | 21.03% | 32.95% | 44.28% | 21.35% | 33.55% | 45.28% | 21.83% | 34.12% | 46.06% | 22.19% | 35.42% | 47.97% | 22.95%
NQ | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 236.6385 | 343.1281 | 149.342 | 240.2181 | 346.7281 | 151.5556 | 244.6018 | 354.529 | 154.984 | 248.7528 | 360.6682 | 157.5471 | 258.2153 | 375.5782 | 162.931
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 28.1147 | 40.4376 | 17.895 | 28.3897 | 40.849 | 18.0688 | 29.0172 | 41.7757 | 18.4654 | 29.5017 | 42.4807 | 18.7681 | 30.6267 | 44.1319 | 19.4774
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 28.0424 | 40.1591 | 17.8892 | 28.3154 | 40.5595 | 18.0621 | 28.9342 | 41.4626 | 18.4574 | 29.4127 | 42.1595 | 18.7591 | 30.5243 | 43.7633 | 19.4664
NQ | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.99743 | 0.99311 | 0.99967 | 0.99738 | 0.99291 | 0.99963 | 0.99714 | 0.99251 | 0.99957 | 0.99698 | 0.99244 | 0.99952 | 0.99666 | 0.99165 | 0.99943
NQ | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 6266_Bohle-Black River No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6266_Bohle-Black River No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0392 | 1.0308 | 1.0482 | 1.0338 | 1.0305 | 1.0429 | 1.0377 | 1.0306 | 1.0422 | 1.0374 | 1.0302 | 1.042 | 1.0375 | 1.0277 | 1.0457
NQ | 6266_Bohle-Black River No 2 66 kV | Contingency Outage | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV
NQ | 6299_Townsville Port 66 kV | % of Rated A | 36.35% | 35.15% | 23.65% | 37.65% | 34.23% | 23.66% | 37.45% | 35.18% | 23.83% | 37.42% | 35.21% | 23.83% | 37.83% | 36.12% | 24.12%
NQ | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96490_1 | TR_LINE 96488_1 | TR_LINE 96490_1 | TR_LINE 96488_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96490_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96490_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96490_1
NQ | 6299_Townsville Port 66 kV | Loading (A) | 396.9646 | 423.5628 | 261.7775 | 411.1649 | 412.4287 | 261.9012 | 408.9103 | 423.925 | 263.8071 | 408.6024 | 424.2761 | 263.7497 | 413.106 | 435.2848 | 266.994
NQ | 6299_Townsville Port 66 kV | Loading (MVA) | 47.8044 | 51.1752 | 31.6049 | 49.4706 | 49.5709 | 31.4929 | 49.3026 | 51.1613 | 31.7136 | 49.2677 | 51.2036 | 31.7073 | 49.8926 | 52.4853 | 32.1562
NQ | 6299_Townsville Port 66 kV | Loading (MW) | 47.5984 | 51.1593 | 31.4746 | 49.2815 | 49.399 | 31.4633 | 49.2092 | 51.1429 | 31.6912 | 49.1763 | 51.1849 | 31.6842 | 49.8785 | 52.4557 | 32.0621
NQ | 6299_Townsville Port 66 kV | Power Factor | 0.99569 | 0.99969 | 0.99587 | 0.99618 | 0.99653 | 0.99906 | 0.99811 | 0.99964 | 0.99929 | 0.99815 | 0.99964 | 0.99927 | 0.99972 | 0.99943 | 0.99707
NQ | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
NQ | 6299_Townsville Port 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6299_Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0534 | 1.0569 | 1.0561 | 1.0524 | 1.0514 | 1.0519 | 1.0547 | 1.0557 | 1.0516 | 1.0547 | 1.0557 | 1.0516 | 1.0565 | 1.0547 | 1.0536
NQ | 6299_Townsville Port 66 kV | Contingency Outage | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV
NQ | 6312_Merinda - Home Hill 66 kV | % of Rated A | 5.945% | 5.422% | 5.08% | 5.943% | 5.42% | 5.08% | 5.95% | 5.433% | 5.088% | 5.948% | 5.43% | 5.088% | 5.943% | 5.424% | 5.078%
NQ | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1
NQ | 6312_Merinda - Home Hill 66 kV | Loading (A) | 14.6237 | 14.8017 | 13.3083 | 14.6206 | 14.7974 | 13.3084 | 14.6358 | 14.8309 | 13.3301 | 14.6321 | 14.8229 | 13.3307 | 14.6189 | 14.8088 | 13.3044
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 1.6637 | 1.6585 | 1.5587 | 1.6641 | 1.659 | 1.5588 | 1.6622 | 1.655 | 1.5767 | 1.6626 | 1.6559 | 1.5772 | 1.6643 | 1.6576 | 1.5551
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 1.5407 | 1.5382 | 1.214 | 1.5407 | 1.5382 | 1.214 | 1.5407 | 1.5382 | 1.2139 | 1.5407 | 1.5382 | 1.2139 | 1.5407 | 1.5382 | 1.214
NQ | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.92603 | 0.92747 | 0.77886 | 0.92581 | 0.92716 | 0.7788 | 0.92692 | 0.92943 | 0.76992 | 0.92665 | 0.9289 | 0.76968 | 0.92568 | 0.92795 | 0.78064
NQ | 6312_Merinda - Home Hill 66 kV | Rating (A) | 246 | 273 | 262 | 246 | 273 | 262 | 246 | 273 | 262 | 246 | 273 | 262 | 246 | 273 | 262
NQ | 6312_Merinda - Home Hill 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6312_Merinda - Home Hill 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9937 | 0.97858 | 1.0245 | 0.99414 | 0.97919 | 1.0246 | 0.99193 | 0.9746 | 1.0347 | 0.99247 | 0.97567 | 1.035 | 0.9944 | 0.97761 | 1.0225
NQ | 6312_Merinda - Home Hill 66 kV | Contingency Outage | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 91.63% | 94.08% | 55.23% | 92.94% | 94.7% | 56.2% | 92.87% | 95.02% | 56.36% | 92.3% | 94.51% | 56.05% | 93.94% | 96.58% | 57.14%
NQ | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 98272_1
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 297.7821 | 312.3465 | 161.8248 | 302.0629 | 314.4059 | 164.6703 | 301.8249 | 315.4642 | 165.132 | 299.9875 | 313.7751 | 164.2235 | 305.3099 | 320.659 | 167.4177
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 35.4594 | 37.1205 | 19.3978 | 35.9565 | 37.7363 | 19.7008 | 36.0131 | 37.8452 | 19.7484 | 35.7943 | 37.6422 | 19.6394 | 36.5562 | 38.4697 | 20.0562
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 34.4408 | 36.1592 | 19.0397 | 34.9369 | 36.7707 | 19.3428 | 35.003 | 36.8819 | 19.3924 | 34.8004 | 36.6931 | 19.2886 | 35.5282 | 37.4886 | 19.6967
NQ | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.97127 | 0.9741 | 0.98154 | 0.97165 | 0.97441 | 0.98183 | 0.97195 | 0.97455 | 0.98197 | 0.97223 | 0.97479 | 0.98214 | 0.97188 | 0.9745 | 0.98208
NQ | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293
NQ | 6325_Oonoonba-Stuart 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6325_Oonoonba-Stuart 66 kV | Min Voltage at Constrained Conductor (pu) | 1.04 | 1.0379 | 1.0478 | 1.0396 | 1.0482 | 1.0457 | 1.0421 | 1.0477 | 1.0453 | 1.0421 | 1.0477 | 1.0453 | 1.0457 | 1.0477 | 1.0471
NQ | 6325_Oonoonba-Stuart 66 kV | Contingency Outage | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV
NQ | 6382 JACR-HUGH 66kV | % of Rated A | 97.96% | 102.5% | 65.61% | 96.98% | 103.5% | 65.44% | 97.45% | 103.8% | 64.06% | 96.41% | 102.5% | 64.19% | 98.41% | 102.5% | 63.65%
NQ | 6382 JACR-HUGH 66kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ | 6382 JACR-HUGH 66kV | Loading (A) | 139.1012 | 145.6208 | 93.1623 | 137.7129 | 146.9373 | 92.9292 | 138.3831 | 147.3799 | 90.9716 | 136.8967 | 145.5028 | 91.1468 | 139.7433 | 145.4914 | 90.3797
NQ | 6382 JACR-HUGH 66kV | Loading (MVA) | 16.1821 | 17.1602 | 13.2267 | 16.0774 | 17.0857 | 13.1606 | 16.0852 | 17.0938 | 12.612 | 15.9797 | 16.9751 | 12.6606 | 16.2003 | 17.1675 | 12.4484
NQ | 6382 JACR-HUGH 66kV | Loading (MW) | 16.178 | 17.1602 | 0.27124 | 16.07 | 17.0845 | 0.26988 | 16.08 | 17.0919 | 0.25863 | 15.9713 | 16.9748 | 0.25963 | 16.1978 | 17.1675 | 0.25528
NQ | 6382 JACR-HUGH 66kV | Power Factor | 0.99919 | 0.99984 | 0.0076707 | 0.99888 | 0.99993 | 0.0076707 | 0.99908 | 0.99989 | 0.0076707 | 0.99879 | 0.99991 | 0.0076707 | 0.99935 | 0.99983 | 0.0076707
NQ | 6382 JACR-HUGH 66kV | Rating (A) | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142
NQ | 6382 JACR-HUGH 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6382 JACR-HUGH 66kV | Min Voltage at Constrained Conductor (pu) | 0.99386 | 1.005 | 1.242 | 0.99798 | 0.99076 | 1.2388 | 0.99324 | 0.98805 | 1.2128 | 0.99804 | 0.99457 | 1.2151 | 0.99004 | 1.0064 | 1.2049
NQ | 6382 JACR-HUGH 66kV | Contingency Outage | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7460 CPRE-JACR 132kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7460 CPRE-JACR 132kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7460 CPRE-JACR 132kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7460 CPRE-JACR 132kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7460 CPRE-JACR 132kV
NQ | 6383 CARI-CPRE 66kV | % of Rated A | 50.68% | 46.63% | 35.97% | 50.39% | 46.29% | 35.89% | 50.49% | 46.85% | 35.79% | 50.17% | 56.02% | 35.83% | 50.78% | 47.11% | 35.76%
NQ | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ | 6383 CARI-CPRE 66kV | Loading (A) | 158.1083 | 166.9435 | 118.3504 | 157.2307 | 165.7023 | 118.0653 | 157.5354 | 167.728 | 117.7526 | 156.538 | 200.5635 | 117.8853 | 158.4219 | 168.6614 | 117.6379
NQ | 6383 CARI-CPRE 66kV | Loading (MVA) | 17.4454 | 18.2607 | 15.2253 | 17.3906 | 18.1427 | 15.1496 | 17.3609 | 18.1015 | 15.0738 | 17.3052 | 18.9279 | 15.1026 | 17.431 | 18.239 | 15.0523
NQ | 6383 CARI-CPRE 66kV | Loading (MW) | 16.6964 | 17.7401 | 4.2908 | 16.5819 | 17.6573 | 4.2664 | 16.5943 | 17.6784 | 4.2723 | 16.4786 | 15.9859 | 4.2367 | 16.7187 | 17.7588 | 4.3078
NQ | 6383 CARI-CPRE 66kV | Power Factor | 0.95704 | 0.97146 | 0.28177 | 0.95346 | 0.97321 | 0.28157 | 0.95581 | 0.9766 | 0.28337 | 0.9522 | 0.84457 | 0.28048 | 0.9591 | 0.97364 | 0.28614
NQ | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 6383 CARI-CPRE 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 6383 CARI-CPRE 66kV | Min Voltage at Constrained Conductor (pu) | 0.96518 | 0.95681 | 1.1254 | 0.96752 | 0.95774 | 1.1225 | 0.964 | 0.94403 | 1.1198 | 0.96703 | 0.82538 | 1.1207 | 0.96247 | 0.94593 | 1.1193
NQ | 6383 CARI-CPRE 66kV | Contingency Outage | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV
NQ | 7182 Ross - Milchester | % of Rated A | 56.32% | 51.36% | 43.78% | 56.08% | 51.06% | 43.71% | 64.19% | 57.73% | 48.01% | 63.88% | 63% | 47.9% | 64.37% | 57.91% | 48.27%
NQ | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 221851_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1
NQ | 7182 Ross - Milchester | Loading (A) | 175.7169 | 183.8782 | 144.0459 | 174.9656 | 182.792 | 143.8018 | 200.2678 | 206.6682 | 157.9365 | 199.3126 | 225.5268 | 157.5895 | 200.8355 | 207.3014 | 158.8038
NQ | 7182 Ross - Milchester | Loading (MVA) | 41.4928 | 43.1683 | 35.1167 | 41.3347 | 42.933 | 34.9546 | 46.6933 | 47.921 | 38.0515 | 46.5038 | 49.0134 | 37.977 | 46.8036 | 48.04 | 38.195
NQ | 7182 Ross - Milchester | Loading (MW) | 40.5296 | 42.6449 | 28.8879 | 40.304 | 42.3665 | 28.6588 | 46.4247 | 47.8437 | 33.8545 | 46.2027 | 44.8639 | 33.7289 | 46.5555 | 47.9755 | 34.3917
NQ | 7182 Ross - Milchester | Power Factor | 0.97679 | 0.98788 | 0.82262 | 0.97506 | 0.9868 | 0.81989 | 0.99412 | 0.99824 | 0.8897 | 0.99342 | 0.91534 | 0.88814 | 0.99457 | 0.99852 | 0.90042
NQ | 7182 Ross - Milchester | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 7182 Ross - Milchester | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 7182 Ross - Milchester | Min Voltage at Constrained Conductor (pu) | 1.0274 | 1.0198 | 1.0663 | 1.0281 | 1.0205 | 1.0632 | 1.0109 | 1.0037 | 1.0538 | 1.0118 | 0.95049 | 1.054 | 1.0103 | 1.003 | 1.052
NQ | 7182 Ross - Milchester | Contingency Outage | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | 7460 CPRE-JACR 132kV | % of Rated A | 45.05% | 29.6% | 21.03% | 44.8% | 29.38% | 20.98% | 44.89% | 29.74% | 20.93% | 44.61% | 35.68% | 20.95% | 45.14% | 29.91% | 20.91%
NQ | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ | 7460 CPRE-JACR 132kV | Loading (A) | 77.9432 | 82.3014 | 58.4706 | 77.5108 | 81.6876 | 58.3298 | 77.6609 | 82.6884 | 58.175 | 77.1694 | 99.1792 | 58.2411 | 78.0976 | 83.1504 | 58.1177
NQ | 7460 CPRE-JACR 132kV | Loading (MVA) | 17.5247 | 18.3282 | 15.4486 | 17.4735 | 18.2052 | 15.3718 | 17.4412 | 18.1602 | 15.2946 | 17.3887 | 18.5618 | 15.3243 | 17.5079 | 18.3049 | 15.2724
NQ | 7460 CPRE-JACR 132kV | Loading (MW) | 16.6466 | 17.6894 | 4.2331 | 16.532 | 17.6068 | 4.209 | 16.5447 | 17.6286 | 4.2151 | 16.4288 | 15.9387 | 4.1794 | 16.669 | 17.7086 | 4.2508
NQ | 7460 CPRE-JACR 132kV | Power Factor | 0.94989 | 0.96515 | 0.27401 | 0.94612 | 0.96713 | 0.27381 | 0.9486 | 0.97072 | 0.27559 | 0.9448 | 0.85775 | 0.27273 | 0.95209 | 0.96742 | 0.27833
NQ | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
NQ | 7460 CPRE-JACR 132kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | 7460 CPRE-JACR 132kV | Min Voltage at Constrained Conductor (pu) | 0.98321 | 0.97375 | 1.1556 | 0.98583 | 0.97448 | 1.1527 | 0.98209 | 0.96028 | 1.1499 | 0.98539 | 0.81859 | 1.1508 | 0.98032 | 0.96257 | 1.1494
NQ | 7460 CPRE-JACR 132kV | Contingency Outage | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 53.46% | 40.25% | 27.6% | 53.39% | 39.8% | 27.6% | 52.76% | 39.6% | 27.49% | 52.25% | 39.22% | 27.24% | 53.23% | 40.03% | 27.57%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 178.0351 | 156.9884 | 100.1925 | 177.7733 | 155.2242 | 100.1969 | 175.6754 | 154.4275 | 99.7743 | 173.9925 | 152.9766 | 98.8674 | 177.2507 | 156.1341 | 100.0965
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 21.2117 | 18.6638 | 12.0644 | 21.1118 | 18.5772 | 12.0045 | 21.0105 | 18.4896 | 11.9499 | 20.81 | 18.3143 | 11.8414 | 21.2111 | 18.6646 | 12.0656
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 21.2116 | 18.6546 | 11.9177 | 21.1117 | 18.5654 | 11.8616 | 21.0099 | 18.477 | 11.8053 | 20.809 | 18.3004 | 11.6926 | 21.2108 | 18.6539 | 11.9176
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.99999 | 0.9995 | 0.98784 | 0.99999 | 0.99936 | 0.98809 | 0.99997 | 0.99932 | 0.9879 | 0.99995 | 0.99923 | 0.98744 | 0.99998 | 0.99942 | 0.98774
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0421 | 1.0398 | 1.0533 | 1.0387 | 1.0468 | 1.048 | 1.046 | 1.0472 | 1.0476 | 1.0461 | 1.0471 | 1.0476 | 1.0466 | 1.0456 | 1.0544
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Contingency Outage | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 72.01% | 59.39% | 41.3% | 72.09% | 59.36% | 41.27% | 71.61% | 58.98% | 41.09% | 71.06% | 58.55% | 40.81% | 72.26% | 59.63% | 41.41%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 331.2423 | 306.4649 | 195.7682 | 331.6274 | 306.3079 | 195.5976 | 329.3896 | 304.3501 | 194.765 | 326.8756 | 302.1098 | 193.4345 | 332.4002 | 307.7052 | 196.2987
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 39.8501 | 36.8923 | 23.6234 | 39.6578 | 36.7014 | 23.4988 | 39.4579 | 36.5218 | 23.3917 | 39.1613 | 36.2537 | 23.2333 | 39.8503 | 36.8821 | 23.6094
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 39.8318 | 36.832 | 23.0227 | 39.6373 | 36.6529 | 22.9096 | 39.4393 | 36.4686 | 22.7957 | 39.1399 | 36.1962 | 22.6251 | 39.8345 | 36.8359 | 23.0234
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.99949 | 0.99828 | 0.97439 | 0.99943 | 0.9986 | 0.97475 | 0.99948 | 0.99846 | 0.97435 | 0.9994 | 0.99833 | 0.97365 | 0.99956 | 0.99867 | 0.975
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0518 | 1.0525 | 1.0555 | 1.0455 | 1.0476 | 1.0508 | 1.0473 | 1.0492 | 1.0505 | 1.0474 | 1.0492 | 1.0506 | 1.0481 | 1.048 | 1.052
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Contingency Outage | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 38.52% | 42.34% | 42.53% | 38.19% | 42% | 42.4% | 38.27% | 42.13% | 42.56% | 37.95% | 41.76% | 42.5% | 39.14% | 42.9% | 34.66%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 99.7608 | 125.3323 | 116.5441 | 98.8994 | 124.3223 | 116.1717 | 99.1302 | 124.717 | 116.623 | 98.2846 | 123.5954 | 116.442 | 101.3798 | 126.9798 | 94.9691
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 11.1058 | 13.6584 | 12.7065 | 11.0162 | 13.5586 | 12.6684 | 11.0169 | 13.559 | 12.8262 | 10.9288 | 13.4526 | 12.8117 | 11.305 | 13.8626 | 10.6442
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 9.0782 | 11.1196 | 6.9247 | 8.9996 | 11.0311 | 6.8846 | 8.9999 | 11.0315 | 6.948 | 8.8951 | 10.9062 | 6.9027 | 8.998 | 11.0284 | 8.6235
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.81713 | 0.81406 | 0.54443 | 0.81664 | 0.81351 | 0.54289 | 0.81661 | 0.81353 | 0.54114 | 0.81359 | 0.81063 | 0.53822 | 0.79561 | 0.79547 | 0.80979
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97308 | 0.95198 | 0.95276 | 0.97366 | 0.95273 | 0.95296 | 0.97144 | 0.94973 | 0.96111 | 0.97199 | 0.95085 | 0.96152 | 0.97471 | 0.95366 | 0.97983
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Contingency Outage | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 76.28% | 80.1% | 60.81% | 75.95% | 79.76% | 60.68% | 76.14% | 80.04% | 60.63% | 75.85% | 79.67% | 60.63% | 76.2% | 79.91% | 56.89%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 196.812 | 236.3074 | 165.4007 | 195.9458 | 235.2801 | 165.0606 | 196.4439 | 236.1033 | 164.9147 | 195.6831 | 235.0384 | 164.9086 | 196.6061 | 235.7416 | 154.7442
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 22.154 | 26.109 | 18.2652 | 22.0677 | 26.0132 | 18.2308 | 22.0748 | 26.0248 | 18.369 | 22.0007 | 25.9359 | 18.376 | 22.1606 | 26.0831 | 17.5
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 21.5687 | 25.1671 | 15.3079 | 21.4902 | 25.0806 | 15.2757 | 21.4926 | 25.0847 | 15.3651 | 21.4113 | 24.9873 | 15.3505 | 21.8074 | 25.4326 | 17.2116
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.97358 | 0.96393 | 0.83809 | 0.97383 | 0.96415 | 0.8379 | 0.97362 | 0.96388 | 0.83647 | 0.97321 | 0.96343 | 0.83536 | 0.98406 | 0.97506 | 0.98352
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98457 | 0.96637 | 0.96591 | 0.98507 | 0.96703 | 0.96608 | 0.98289 | 0.96409 | 0.97426 | 0.9834 | 0.96515 | 0.97467 | 0.9859 | 0.96774 | 0.9892
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Contingency Outage | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 27.28% | 33.74% | 24.23% | 33.99% | 39.91% | 142.5% | 34.17% | 40.3% | 24.49% | 33.96% | 34.23% | 24.4% | 34.82% | 35.1% | 24.85%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 217287_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 128321_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 128321_1 | TR_LINE 214252_1
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 51.5648 | 69.5023 | 45.0746 | 64.2341 | 82.2151 | 116.8622 | 64.5844 | 83.0246 | 45.5479 | 64.1884 | 70.5119 | 45.3776 | 65.8019 | 72.316 | 46.2137
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 6.0426 | 8.0155 | 5.417 | 7.6159 | 9.7292 | 11.8208 | 7.6873 | 9.8281 | 5.443 | 7.6392 | 8.1186 | 5.4223 | 7.8323 | 8.3193 | 5.5412
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 6.0382 | 7.9957 | 4.8425 | 7.3767 | 9.6239 | 2.0142 | 7.4483 | 9.7269 | 4.8927 | 7.3891 | 8.0975 | 4.8599 | 7.6029 | 8.2965 | 4.9971
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.99926 | 0.99752 | 0.89394 | 0.96859 | 0.98918 | 0.17029 | 0.96891 | 0.98971 | 0.8989 | 0.96727 | 0.99739 | 0.89629 | 0.97072 | 0.99725 | 0.90181
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 82 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.025 | 1.0087 | 1.0506 | 1.0358 | 1.0331 | 0.88481 | 1.0398 | 1.0334 | 1.0447 | 1.0397 | 1.007 | 1.0446 | 1.0398 | 1.0062 | 1.0482
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 90.04% | 118.9% | 58.98% | 93.05% | 121.4% | 61.06% | 95.17% | 125.1% | 62.93% | 96.31% | 126.7% | 63.63% | 99.68% | 131.6% | 65.4%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 402.4643 | 531.4742 | 263.6487 | 415.9159 | 542.5223 | 272.9248 | 425.4222 | 559.1945 | 281.2763 | 430.5249 | 566.5381 | 284.4394 | 445.5861 | 588.0487 | 292.3586
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 48.0672 | 63.0269 | 31.696 | 49.4832 | 64.7114 | 32.6398 | 50.9435 | 66.6291 | 33.6187 | 51.5423 | 67.4794 | 33.9922 | 53.3681 | 69.9783 | 35.1552
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 47.7048 | 62.148 | 31.664 | 49.0547 | 63.731 | 32.5888 | 50.4766 | 65.5538 | 33.5513 | 51.0566 | 66.3748 | 33.9204 | 52.8194 | 68.7303 | 35.0718
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.9922 | 0.98577 | 0.99873 | 0.99108 | 0.98456 | 0.99818 | 0.99057 | 0.98357 | 0.99774 | 0.99031 | 0.98334 | 0.99763 | 0.98945 | 0.98187 | 0.99737
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0448 | 1.0374 | 1.0517 | 1.0408 | 1.0434 | 1.0462 | 1.0475 | 1.0423 | 1.0455 | 1.0473 | 1.0419 | 1.0454 | 1.0477 | 1.041 | 1.0519
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 84.12% | 71.98% | 114.1% | 84.02% | 71.23% | 114.1% | 134.7% | 112.5% | 176.4% | 134.1% | 111.9% | 175.3% | 134.7% | 113% | 108.2%
NQ | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102297_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102297_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 102293_1
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 217.0298 | 212.3333 | 310.3763 | 216.7721 | 210.1385 | 310.3745 | 347.634 | 332.0058 | 479.9128 | 345.9576 | 330.2373 | 476.8622 | 347.5015 | 333.3312 | 294.3695
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 25.833 | 25.2002 | 36.6976 | 25.805 | 24.9471 | 36.6986 | 41.19 | 39.001 | 56.8508 | 41.0114 | 38.8175 | 56.5163 | 41.213 | 39.1991 | 34.6577
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 25.6714 | 25.0348 | 36.6739 | 25.6468 | 24.8103 | 36.6751 | 40.0281 | 37.9993 | 54.7742 | 39.88 | 37.8493 | 54.5716 | 40.0581 | 38.1711 | 34.181
NQ | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.99375 | 0.99343 | 0.99935 | 0.99387 | 0.99451 | 0.99935 | 0.97179 | 0.97431 | 0.96347 | 0.97241 | 0.97506 | 0.96559 | 0.97198 | 0.97377 | 0.98624
NQ | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | CHTO_Clare South - Charters Towers 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CHTO_Clare South - Charters Towers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0238 | 1.0211 | 1.0342 | 1.0239 | 1.0218 | 1.0342 | 1.0045 | 0.99734 | 0.99046 | 1.0052 | 0.99824 | 0.99157 | 1.0055 | 0.99827 | 1.0047
NQ | CHTO_Clare South - Charters Towers 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 50.83% | 52.57% | 36.73% | 50.55% | 52.27% | 36.53% | 50.69% | 52.55% | 36.16% | 50.28% | 52.08% | 35.95% | 50.64% | 52.42% | 36.74%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 158.5906 | 190.8315 | 123.7856 | 157.704 | 189.7433 | 123.1081 | 158.1452 | 190.7386 | 121.8439 | 156.8736 | 189.0616 | 121.1561 | 157.9913 | 190.2884 | 123.8024
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 18.1138 | 21.4857 | 14.1678 | 18.0201 | 21.3756 | 14.0933 | 18.0312 | 21.3918 | 14.0928 | 17.8951 | 21.2258 | 13.726 | 18.0574 | 21.4047 | 14.1528
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 17.5896 | 20.6727 | 13.8305 | 17.5039 | 20.573 | 13.7616 | 17.5109 | 20.5817 | 13.7661 | 17.3786 | 20.4215 | 12.0114 | 17.6755 | 20.7634 | 13.8889
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.97106 | 0.96216 | 0.97619 | 0.97135 | 0.96245 | 0.97647 | 0.97115 | 0.96213 | 0.97682 | 0.97113 | 0.96211 | 0.87504 | 0.97885 | 0.97004 | 0.98136
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99809 | 0.98354 | 1.0005 | 0.99852 | 0.98412 | 1.0007 | 0.99633 | 0.97971 | 1.0111 | 0.99684 | 0.98074 | 0.99033 | 0.99878 | 0.98266 | 0.99928
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Contingency Outage | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | ST-GI-1_Stuart-Giru 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 92% | 78.32% | 52.04% | 91.49% | 77.87% | 51.76% | 91.74% | 78.3% | 51.22% | 91% | 77.61% | 50.82% | 91.67% | 78.12% | 52.06%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 155.4803 | 187.19 | 121.2586 | 154.613 | 186.1175 | 120.5961 | 155.0481 | 187.1454 | 119.3501 | 153.7958 | 185.491 | 118.411 | 154.9282 | 186.7102 | 121.3052
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 18.0097 | 21.4615 | 14.0229 | 17.9147 | 21.3479 | 13.9481 | 17.9276 | 21.3722 | 13.9431 | 17.7893 | 21.2012 | 13.8369 | 17.9465 | 21.3711 | 14.0078
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 17.5651 | 20.726 | 13.7618 | 17.4776 | 20.6232 | 13.692 | 17.4862 | 20.6366 | 13.6929 | 17.3522 | 20.4728 | 13.5894 | 17.6303 | 20.7954 | 13.8095
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.97531 | 0.96573 | 0.98138 | 0.9756 | 0.96605 | 0.98164 | 0.97538 | 0.96558 | 0.98206 | 0.97543 | 0.96564 | 0.98211 | 0.98238 | 0.97306 | 0.98585
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0059 | 0.99345 | 1.0063 | 1.0062 | 0.99396 | 1.0065 | 1.0041 | 0.98951 | 1.0168 | 1.0045 | 0.99046 | 1.0171 | 1.0061 | 0.992 | 1.0049
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Contingency Outage | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 43.77% | 29.64% | 80.55% | 41.98% | 28.5% | 80.36% | 43.89% | 29.06% | 78.78% | 43.72% | 30.47% | 78.9% | 43.7% | 28.98% | 78.32%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 62.5959 | 62.8301 | 168.3596 | 60.0349 | 60.4278 | 167.9528 | 62.7697 | 61.6115 | 164.6452 | 62.5208 | 64.5864 | 164.892 | 62.4956 | 61.4384 | 163.6824
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 6.6855 | 6.7432 | 21.0309 | 6.4517 | 6.5239 | 20.926 | 6.7244 | 6.4501 | 20.1633 | 6.6746 | 6.0954 | 20.2131 | 6.6648 | 6.4063 | 19.9529
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 3.1956 | 3.5468 | 11.5559 | 3.353 | 3.7015 | 11.494 | 3.1392 | 3.6721 | 11.3591 | 3.1254 | 6.0903 | 11.3197 | 3.2099 | 3.7493 | 11.3706
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.47799 | 0.52599 | 0.5494 | 0.51971 | 0.56737 | 0.54919 | 0.46683 | 0.56931 | 0.56328 | 0.46825 | 0.99916 | 0.55994 | 0.48162 | 0.58525 | 0.5698
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9343 | 0.93884 | 1.0927 | 0.94008 | 0.94442 | 1.0899 | 0.93713 | 0.91581 | 1.0713 | 0.93389 | 0.82555 | 1.0723 | 0.9329 | 0.91214 | 1.0663
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | 7460 CPRE-JACR 132kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV
NQ | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 41.35% | 37.63% | 38.64% | 41.34% | 37.62% | 38.65% | 41.53% | 38.01% | 38.33% | 41.03% | 37.55% | 37.87% | 41.96% | 38.4% | 38.84%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 80.6275 | 82.0279 | 76.9031 | 80.6181 | 82.0057 | 76.9054 | 80.9854 | 82.8672 | 76.2823 | 80.0132 | 81.8594 | 75.3634 | 81.8262 | 83.7125 | 77.2986
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 9.4786 | 9.6126 | 8.8914 | 9.4785 | 9.6123 | 8.8914 | 9.4834 | 9.6156 | 8.8905 | 9.3756 | 9.5062 | 8.7868 | 9.5895 | 9.723 | 8.9955
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 7.9149 | 8.0183 | 7.4211 | 7.9149 | 8.0182 | 7.4211 | 7.9154 | 8.0188 | 7.4209 | 7.8326 | 7.9349 | 7.3409 | 7.998 | 8.1025 | 7.501
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.83498 | 0.8341 | 0.8346 | 0.83499 | 0.83412 | 0.8346 | 0.83462 | 0.8339 | 0.83466 | 0.83538 | 0.83467 | 0.8354 | 0.834 | 0.83329 | 0.83382
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0284 | 1.0251 | 1.0114 | 1.0285 | 1.0253 | 1.0113 | 1.0243 | 1.015 | 1.0195 | 1.025 | 1.0158 | 1.0199 | 1.0251 | 1.016 | 1.018
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 40.69% | 38.7% | 77.99% | 40.59% | 38.54% | 77.81% | 40.16% | 38.34% | 77.77% | 40.07% | 53.97% | 77.83% | 40.29% | 38.5% | 77.46%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 64803_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 74.8622 | 77.4081 | 140.3815 | 74.693 | 77.071 | 140.0569 | 73.8982 | 76.6777 | 139.9893 | 73.7246 | 107.9436 | 140.0948 | 74.1302 | 77.0053 | 139.4349
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 8.7112 | 9.0079 | 16.6956 | 8.6964 | 8.949 | 16.615 | 8.5695 | 8.8356 | 16.3466 | 8.5603 | 10.379 | 16.3679 | 8.5975 | 8.8639 | 16.2178
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 7.2668 | 7.8756 | 11.4912 | 7.2072 | 7.8042 | 11.4318 | 7.0491 | 7.7311 | 11.3927 | 6.992 | 9.9707 | 11.3456 | 7.1161 | 7.8143 | 11.4281
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.83419 | 0.87429 | 0.68724 | 0.82876 | 0.87208 | 0.68701 | 0.82258 | 0.875 | 0.6959 | 0.81679 | 0.96066 | 0.69211 | 0.82769 | 0.88158 | 0.70363
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0177 | 1.0176 | 1.0404 | 1.0183 | 1.0154 | 1.0377 | 1.0142 | 1.0077 | 1.0215 | 1.0155 | 0.83813 | 1.022 | 1.0143 | 1.0066 | 1.0174
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Contingency Outage | CS-ML-1_Clare South - Millaroo 66 kV | CS-ML-1_Clare South - Millaroo 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | CS-ML-1_Clare South - Millaroo 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | CS-ML-1_Clare South - Millaroo 66 kV | CS-ML-1_Clare South - Millaroo 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | CS-ML-1_Clare South - Millaroo 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | CS-ML-1_Clare South - Millaroo 66 kV | CS-ML-1_Clare South - Millaroo 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 45.75% | 43.09% | 73.9% | 45.45% | 42.8% | 73.81% | 64.2% | 58.16% | 70.19% | 63.63% | 59.16% | 70.17% | 64.17% | 58.08% | 57.58%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 32864_1
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 127.1867 | 133.9967 | 209.8713 | 126.3544 | 133.1117 | 209.6118 | 178.4835 | 180.8868 | 199.3255 | 176.8899 | 183.9927 | 199.2709 | 178.3827 | 180.6406 | 163.5239
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 14.8352 | 15.6221 | 22.8237 | 14.758 | 15.538 | 22.7947 | 20.7732 | 20.7921 | 18.4311 | 20.6211 | 20.7892 | 18.5819 | 20.7404 | 20.7376 | 19.1311
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 14.7035 | 15.3817 | 16.7871 | 14.6313 | 15.3008 | 16.7183 | 20.329 | 20.336 | 16.6676 | 20.1807 | 15.4344 | 16.6431 | 20.3001 | 20.2856 | 19.082
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.99112 | 0.98461 | 0.73538 | 0.99142 | 0.98473 | 0.7333 | 0.97862 | 0.97806 | 0.90422 | 0.97864 | 0.74242 | 0.89556 | 0.97877 | 0.9782 | 0.99742
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0203 | 1.0198 | 0.9513 | 1.0216 | 1.021 | 0.95127 | 1.018 | 1.0054 | 0.80886 | 1.0197 | 0.98824 | 0.81571 | 1.017 | 1.0041 | 1.0233
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Contingency Outage | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | 7182 Ross - Milchester | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | 7182 Ross - Milchester | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | 7182 Ross - Milchester | ST-WO-1_Stuart-Woodstock South 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | 7182 Ross - Milchester | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 73.51% | 64.79% | 45.77% | 73.39% | 64.05% | 45.75% | 72.52% | 63.71% | 45.56% | 71.98% | 63.25% | 45.25% | 73.19% | 64.43% | 45.73%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 332.2601 | 308.4064 | 195.4249 | 331.7405 | 304.8734 | 195.3509 | 327.794 | 303.2652 | 194.5241 | 325.3432 | 301.0814 | 193.2017 | 330.8322 | 306.6987 | 195.2558
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 39.7207 | 36.771 | 23.5558 | 39.5295 | 36.5895 | 23.4294 | 39.3327 | 36.4108 | 23.3221 | 39.0381 | 36.1442 | 23.1632 | 39.722 | 36.7677 | 23.5601
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 39.6982 | 36.7096 | 22.97 | 39.5021 | 36.5258 | 22.8572 | 39.3032 | 36.3436 | 22.7438 | 39.0055 | 36.0727 | 22.5737 | 39.6959 | 36.7084 | 22.9699
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.9994 | 0.99829 | 0.97504 | 0.99928 | 0.99822 | 0.97549 | 0.99922 | 0.99811 | 0.97511 | 0.99913 | 0.99798 | 0.97446 | 0.99931 | 0.99834 | 0.97486
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0453 | 1.0426 | 1.0543 | 1.0419 | 1.0495 | 1.049 | 1.0492 | 1.0499 | 1.0486 | 1.0492 | 1.0498 | 1.0486 | 1.0499 | 1.0483 | 1.0554
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Contingency Outage | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 54.87% | 53.84% | 39.75% | 55.26% | 53.78% | 40.09% | 55.31% | 54.21% | 40.46% | 55.62% | 54.53% | 40.71% | 57.43% | 56.41% | 41.74%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 302.3089 | 313.3536 | 208.2956 | 304.4907 | 312.9985 | 210.0699 | 304.7475 | 315.5231 | 212.0275 | 306.4672 | 317.3855 | 213.2955 | 316.4216 | 328.3126 | 218.7357
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 36.0448 | 37.2435 | 25.0139 | 36.1541 | 37.3388 | 25.0932 | 36.4353 | 37.653 | 25.3162 | 36.6345 | 37.8642 | 25.4648 | 37.8188 | 39.0998 | 26.2799
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 35.6889 | 36.8233 | 24.9458 | 35.785 | 36.9216 | 25.0191 | 36.0667 | 37.2207 | 25.2364 | 36.2562 | 37.4203 | 25.3813 | 37.3923 | 38.5971 | 26.1844
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.99013 | 0.98872 | 0.99728 | 0.98979 | 0.98883 | 0.99705 | 0.98988 | 0.98852 | 0.99685 | 0.98967 | 0.98828 | 0.99672 | 0.98872 | 0.98714 | 0.99637
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0429 | 1.0396 | 1.0504 | 1.0385 | 1.0434 | 1.0449 | 1.0457 | 1.0438 | 1.0444 | 1.0456 | 1.0435 | 1.0443 | 1.0454 | 1.0416 | 1.0509
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Contingency Outage | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 56.53% | 46.66% | 23.27% | 56.75% | 46.48% | 23.38% | 56.65% | 46.67% | 23.49% | 56.39% | 46.46% | 23.39% | 57.65% | 47.59% | 23.77%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 141.899 | 179.6315 | 88.4235 | 142.4484 | 178.931 | 88.8351 | 142.1828 | 179.6693 | 89.2557 | 141.5478 | 178.875 | 88.869 | 144.6975 | 183.239 | 90.3141
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 17.0731 | 21.5573 | 10.6732 | 17.0731 | 21.5553 | 10.669 | 17.151 | 21.6547 | 10.7155 | 17.0731 | 21.5551 | 10.6686 | 17.463 | 22.0543 | 10.9079
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 17.067 | 21.551 | 10.556 | 17.0678 | 21.5498 | 10.5563 | 17.1449 | 21.6488 | 10.6047 | 17.0665 | 21.5497 | 10.5564 | 17.4584 | 22.0459 | 10.7978
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.99965 | 0.99971 | 0.98902 | 0.99969 | 0.99975 | 0.98944 | 0.99964 | 0.99973 | 0.98966 | 0.99962 | 0.99975 | 0.98948 | 0.99974 | 0.99962 | 0.9899
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0525 | 1.0498 | 1.0559 | 1.0485 | 1.0538 | 1.0506 | 1.0552 | 1.0543 | 1.0502 | 1.0551 | 1.0541 | 1.0502 | 1.0557 | 1.0529 | 1.0565
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Contingency Outage | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV
NQ | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 87.3% | 69.65% | 46.95% | 86.91% | 69.34% | 46.79% | 87.18% | 69.74% | 46.64% | 86.77% | 69.37% | 46.48% | 87.36% | 69.63% | 45.54%
NQ | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 183.3341 | 219.387 | 145.5309 | 182.5172 | 218.4137 | 145.0638 | 183.0761 | 219.6735 | 144.5821 | 182.2191 | 218.5121 | 144.0833 | 183.4661 | 219.3381 | 141.1886
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 20.7901 | 24.4705 | 16.1786 | 20.7062 | 24.3756 | 16.129 | 20.7226 | 24.401 | 16.2106 | 20.6323 | 24.2918 | 16.1608 | 20.843 | 24.4789 | 16.0802
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 20.1238 | 23.4258 | 13.6977 | 20.0489 | 23.3416 | 13.654 | 20.0588 | 23.3537 | 13.7086 | 19.9655 | 23.2416 | 13.651 | 20.4261 | 23.7606 | 15.7905
NQ | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.96795 | 0.95731 | 0.84666 | 0.96825 | 0.95758 | 0.84655 | 0.96797 | 0.95708 | 0.84566 | 0.96768 | 0.95677 | 0.8447 | 0.98 | 0.97065 | 0.98198
NQ | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | EAAY_Clare South - East Ayr 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | EAAY_Clare South - East Ayr 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9918 | 0.97548 | 0.97232 | 0.99222 | 0.97603 | 0.97246 | 0.98998 | 0.97144 | 0.98064 | 0.9903 | 0.97223 | 0.98101 | 0.99362 | 0.97604 | 0.99616
NQ | EAAY_Clare South - East Ayr 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 72.92% | 90.72% | 50.3% | 75.53% | 93.58% | 52.04% | 77.67% | 96.49% | 53.63% | 78.58% | 97.77% | 54.22% | 81.52% | 101.3% | 56.02%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 401.8008 | 527.989 | 263.5756 | 416.1525 | 544.6593 | 272.6862 | 427.9385 | 561.5777 | 281.0049 | 432.9736 | 569.0486 | 284.1287 | 449.1796 | 589.7119 | 293.5237
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 47.4904 | 61.9205 | 31.4801 | 48.8454 | 63.5217 | 32.403 | 50.2836 | 65.363 | 33.3633 | 50.8635 | 66.1962 | 33.7301 | 52.6335 | 68.5709 | 34.8806
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 47.2356 | 61.3307 | 31.4593 | 48.5531 | 62.8799 | 32.3697 | 49.9547 | 64.6495 | 33.3189 | 50.5221 | 65.4508 | 33.6828 | 52.247 | 67.7338 | 34.8222
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.99463 | 0.99047 | 0.99934 | 0.99402 | 0.9899 | 0.99897 | 0.99346 | 0.98908 | 0.99867 | 0.99329 | 0.98874 | 0.9986 | 0.99266 | 0.98779 | 0.99833
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0339 | 1.0258 | 1.0447 | 1.0267 | 1.0201 | 1.0394 | 1.0278 | 1.0181 | 1.0386 | 1.0276 | 1.0175 | 1.0384 | 1.025 | 1.0171 | 1.0395
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 84.42% | 85.08% | 49.99% | 86.2% | 87.01% | 51.02% | 86.14% | 87.14% | 51.16% | 85.62% | 86.68% | 50.88% | 87.41% | 88.69% | 51.85%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 291.2508 | 305.4269 | 159.9785 | 297.3801 | 312.3758 | 163.2575 | 297.1796 | 312.823 | 163.7138 | 295.3953 | 311.1956 | 162.8142 | 301.5625 | 318.3969 | 165.9091
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 34.9784 | 36.6726 | 19.2806 | 35.4844 | 37.3101 | 19.5819 | 35.5467 | 37.4174 | 19.6301 | 35.3371 | 37.2229 | 19.5234 | 36.0801 | 38.0362 | 19.9359
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 34.0701 | 35.8071 | 18.9401 | 34.5676 | 36.4309 | 19.2424 | 34.6375 | 36.5422 | 19.2923 | 34.4415 | 36.3595 | 19.1903 | 35.1587 | 37.1433 | 19.5952
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.97403 | 0.9764 | 0.98234 | 0.97416 | 0.97644 | 0.98266 | 0.97442 | 0.97661 | 0.98279 | 0.97466 | 0.97681 | 0.98294 | 0.97446 | 0.97653 | 0.98291
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0497 | 1.0494 | 1.0538 | 1.0429 | 1.0438 | 1.0488 | 1.0454 | 1.0454 | 1.0484 | 1.0455 | 1.0454 | 1.0485 | 1.0457 | 1.044 | 1.0507
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Contingency Outage | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 73.8% | 40.55% | 32.69% | 81.72% | 44.74% | 36.08% | 85.05% | 46.66% | 37.6% | 84.54% | 46.39% | 37.39% | 85.98% | 47.19% | 37.96%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 124.7278 | 96.9047 | 76.165 | 138.1089 | 106.9334 | 84.0646 | 143.7308 | 111.5218 | 87.6196 | 142.8744 | 110.8734 | 87.1082 | 145.3006 | 112.7755 | 88.4413
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 14.9948 | 11.6551 | 9.182 | 16.5057 | 12.8171 | 10.0874 | 17.2171 | 13.3594 | 10.5102 | 17.1159 | 13.2816 | 10.4493 | 17.4187 | 13.5181 | 10.6314
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 14.9226 | 11.631 | 9.1777 | 16.3809 | 12.7653 | 10.0709 | 17.0518 | 13.2863 | 10.4818 | 16.9535 | 13.2099 | 10.4216 | 17.2481 | 13.4399 | 10.6019
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.99519 | 0.99794 | 0.99953 | 0.99244 | 0.99596 | 0.99836 | 0.9904 | 0.99453 | 0.99729 | 0.99051 | 0.9946 | 0.99735 | 0.9902 | 0.99422 | 0.99722
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0516 | 1.0521 | 1.0545 | 1.0454 | 1.0485 | 1.0497 | 1.0478 | 1.0479 | 1.0493 | 1.0479 | 1.0478 | 1.0493 | 1.0486 | 1.0485 | 1.0515
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Contingency Outage | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 59.14% | 55.53% | 30.25% | 56.07% | 55.32% | 31.64% | 54.43% | 55.72% | 32.7% | 54.38% | 55.89% | 32.64% | 56.79% | 57.72% | 33.35%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 35540_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 35540_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 35540_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 152.5761 | 163.8222 | 82.2825 | 144.6548 | 163.1863 | 86.0621 | 140.4187 | 164.3882 | 88.9466 | 140.2918 | 164.8788 | 88.7764 | 146.5268 | 170.2629 | 90.705
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 18.3909 | 19.797 | 9.8892 | 17.3993 | 19.6333 | 10.3286 | 16.922 | 19.844 | 10.6716 | 16.9078 | 19.9034 | 10.6516 | 17.6727 | 20.5354 | 10.8695
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 16.2852 | 19.1311 | 9.8783 | 17.3772 | 19.275 | 10.3281 | 16.8554 | 19.8415 | 10.6708 | 16.8378 | 19.901 | 10.6508 | 17.647 | 20.535 | 10.8693
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.88542 | 0.96632 | 0.9989 | 0.99873 | 0.98172 | 0.99995 | 0.99606 | 0.99987 | 0.99992 | 0.99585 | 0.99988 | 0.99993 | 0.99854 | 0.99998 | 0.99998
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0544 | 1.057 | 1.0513 | 1.0521 | 1.0523 | 1.0495 | 1.0541 | 1.0558 | 1.0492 | 1.0541 | 1.0558 | 1.0492 | 1.0549 | 1.0549 | 1.0482
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Contingency Outage | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6299_Townsville Port 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6299_Townsville Port 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6299_Townsville Port 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6299_Townsville Port 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6299_Townsville Port 66 kV
NQ | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 22.65% | 25.23% | 125.8% | 22.64% | 25.21% | 125.9% | 22.7% | 25.33% | 126.8% | 22.22% | 24.79% | 126.8% | 23.19% | 25.8% | 19.9%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 42.8095 | 51.9674 | 234.0745 | 42.7902 | 51.9352 | 234.1156 | 42.8966 | 52.1722 | 235.7846 | 41.9935 | 51.0574 | 235.8 | 43.8316 | 53.1444 | 37.0104
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 4.8387 | 5.7723 | 23.513 | 4.8384 | 5.7719 | 23.5222 | 4.8396 | 5.7744 | 23.8959 | 4.7401 | 5.657 | 23.909 | 4.9556 | 5.8989 | 4.1903
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 4.7136 | 5.5995 | 13.3374 | 4.7135 | 5.5993 | 13.3416 | 4.7138 | 5.6002 | 13.5118 | 4.6013 | 5.4663 | 13.4424 | 4.8394 | 5.7363 | 4.1287
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.97413 | 0.97004 | 0.56719 | 0.97416 | 0.97008 | 0.56714 | 0.97398 | 0.96981 | 0.5654 | 0.97069 | 0.96628 | 0.56219 | 0.97654 | 0.97241 | 0.98528
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98873 | 0.97165 | 0.87855 | 0.98913 | 0.97219 | 0.87874 | 0.98692 | 0.96818 | 0.88638 | 0.98743 | 0.9692 | 0.8868 | 0.98901 | 0.97097 | 0.99041
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Contingency Outage | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV
NQ | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 49.8% | 45.25% | 27.95% | 49.56% | 44.86% | 27.86% | 49.17% | 45.28% | 27.73% | 48.63% | 45.27% | 27.43% | 49.29% | 46.56% | 27.83%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 106404_1 | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 106404_1 | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 106404_1 | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 106404_1 | TR_LINE 98259_1
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 171.8098 | 160.1985 | 87.1983 | 170.9963 | 158.7915 | 86.9291 | 169.6366 | 160.278 | 86.5093 | 167.7905 | 160.2732 | 85.5936 | 170.05 | 164.8174 | 86.8194
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 20.0338 | 18.64 | 10.3424 | 19.9285 | 18.7736 | 10.2891 | 19.8194 | 18.9758 | 10.2354 | 19.6075 | 18.9758 | 10.1277 | 19.9345 | 19.4832 | 10.2888
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 18.9893 | 17.6966 | 9.912 | 18.8914 | 18.6694 | 9.8611 | 18.7928 | 18.8694 | 9.8101 | 18.5968 | 18.8694 | 9.7082 | 18.8917 | 19.3701 | 9.861
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.94786 | 0.94939 | 0.95838 | 0.94796 | 0.99445 | 0.95839 | 0.9482 | 0.99439 | 0.95844 | 0.94846 | 0.99439 | 0.95857 | 0.94768 | 0.99419 | 0.95842
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0199 | 1.0178 | 1.0375 | 1.0194 | 1.0339 | 1.0354 | 1.0219 | 1.0353 | 1.035 | 1.0221 | 1.0353 | 1.035 | 1.0254 | 1.0337 | 1.0366
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Contingency Outage | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | 6325_Oonoonba-Stuart 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | 6325_Oonoonba-Stuart 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | 6325_Oonoonba-Stuart 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | 6325_Oonoonba-Stuart 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 23.45% | 20.36% | 12.47% | 23.22% | 20.15% | 12.42% | 23.28% | 20.83% | 12.36% | 23.16% | 20.67% | 12.31% | 23.65% | 21.3% | 12.32%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163218_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163218_1 | TR_LINE 163213_1
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 66.8427 | 73.9197 | 41.4114 | 66.1708 | 73.1526 | 41.2385 | 66.3384 | 75.6056 | 41.0363 | 65.9934 | 75.0226 | 40.8721 | 67.4064 | 77.3155 | 40.8864
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 7.503 | 8.3032 | 5.8794 | 7.4134 | 8.2 | 5.8402 | 7.414 | 8.2312 | 4.079 | 7.413 | 8.2289 | 5.6773 | 7.5156 | 8.3645 | 5.6315
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 7.4764 | 8.3003 | 3.7933 | 7.3841 | 8.196 | 3.7485 | 7.3867 | 8.231 | 3.7885 | 7.3813 | 8.2289 | 3.7483 | 7.4952 | 8.3621 | 3.7981
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.99647 | 0.99965 | 0.64519 | 0.99604 | 0.99951 | 0.64184 | 0.99632 | 0.99996 | 0.92879 | 0.99573 | 0.99999 | 0.66022 | 0.99728 | 0.99966 | 0.67445
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9697 | 0.98259 | 1.242 | 0.96809 | 0.98055 | 1.2388 | 0.96556 | 0.95086 | 0.86951 | 0.97079 | 0.95948 | 1.2151 | 0.96273 | 0.94488 | 1.2049
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 14.59% | 13.39% | 12.12% | 14.6% | 13.4% | 12.09% | 14.61% | 13.59% | 11.89% | 14.58% | 13.55% | 11.91% | 14.63% | 13.64% | 11.83%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 38.215 | 38.9666 | 31.9912 | 38.2462 | 39.0032 | 31.9264 | 38.2847 | 39.5516 | 31.3887 | 38.2051 | 39.4202 | 31.4363 | 38.3209 | 39.6869 | 31.2287
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 4.2974 | 4.377 | 4.5419 | 4.2925 | 4.372 | 4.5214 | 4.2864 | 4.3105 | 4.3516 | 4.2991 | 4.3238 | 4.3666 | 4.2808 | 4.2988 | 4.3013
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 3.8839 | 4.0011 | 1.977 | 3.8844 | 4.0016 | 1.9768 | 3.885 | 4.009 | 1.9752 | 3.8838 | 4.0072 | 1.9754 | 3.8855 | 4.0107 | 1.9748
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.9038 | 0.91411 | 0.43528 | 0.90492 | 0.91527 | 0.43722 | 0.90635 | 0.93004 | 0.45391 | 0.90342 | 0.92678 | 0.45238 | 0.90766 | 0.93299 | 0.45912
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98369 | 0.9826 | 1.242 | 0.98179 | 0.98056 | 1.2388 | 0.9794 | 0.95336 | 1.2128 | 0.98434 | 0.95949 | 1.2151 | 0.97719 | 0.94752 | 1.2049
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 42.49% | 35.03% | 21.73% | 42.36% | 34.91% | 21.66% | 42.47% | 35.11% | 21.44% | 42.32% | 34.96% | 21.36% | 44.02% | 36.09% | 22.94%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 71.8115 | 84.0668 | 50.8388 | 71.5836 | 83.7857 | 50.6788 | 71.7764 | 84.2545 | 50.1618 | 71.5226 | 83.9006 | 49.9844 | 74.396 | 86.6246 | 53.6909
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 8.0248 | 9.2025 | 5.7297 | 8.0036 | 9.1783 | 5.7133 | 8.0063 | 9.1818 | 5.7153 | 7.9823 | 9.1536 | 5.6972 | 8.3301 | 9.4864 | 6.1946
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 7.9624 | 9.1851 | 5.607 | 7.9394 | 9.1599 | 5.5883 | 7.944 | 9.1612 | 5.5914 | 7.9205 | 9.1332 | 5.5739 | 8.1133 | 9.3482 | 1.9356
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.99223 | 0.9981 | 0.97858 | 0.99198 | 0.998 | 0.97812 | 0.99222 | 0.99776 | 0.97832 | 0.99226 | 0.99777 | 0.97836 | 0.97397 | 0.98544 | 0.31239
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97745 | 0.95748 | 0.98586 | 0.97798 | 0.95816 | 0.98613 | 0.97568 | 0.95319 | 0.99665 | 0.97621 | 0.95427 | 0.99701 | 0.97941 | 0.95788 | 1.0093
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Contingency Outage | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 18.21% | 17.09% | 15.48% | 17.79% | 16.71% | 15.14% | 17.83% | 16.75% | 15.01% | 17.82% | 16.73% | 15% | 17.77% | 16.69% | 14.71%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 36.2315 | 38.1193 | 31.5886 | 35.3975 | 37.2569 | 30.8767 | 35.4832 | 37.3585 | 30.6169 | 35.462 | 37.3115 | 30.6033 | 35.3572 | 37.2183 | 30.017
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 3.9995 | 4.1142 | 3.4171 | 3.9105 | 4.0251 | 3.3413 | 3.9109 | 4.0231 | 3.3419 | 3.9108 | 4.0229 | 3.3419 | 3.9103 | 4.0249 | 3.3411
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 3.387 | 3.4828 | 2.9016 | 3.3132 | 3.4071 | 2.8384 | 3.3132 | 3.4069 | 2.8384 | 3.3132 | 3.4069 | 2.8384 | 3.3132 | 3.4071 | 2.8384
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.84684 | 0.84651 | 0.84912 | 0.84724 | 0.84646 | 0.84946 | 0.84716 | 0.84682 | 0.84932 | 0.84718 | 0.84686 | 0.84933 | 0.84728 | 0.84649 | 0.84951
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.96564 | 0.94414 | 0.94628 | 0.96639 | 0.94506 | 0.94663 | 0.96415 | 0.94204 | 0.95484 | 0.96471 | 0.94318 | 0.95525 | 0.96744 | 0.946 | 0.97369
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Contingency Outage | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 50.15% | 41.77% | 30.84% | 49.88% | 41.65% | 30.74% | 49.8% | 41.51% | 30.75% | 49.49% | 41.26% | 30.59% | 50.37% | 42.05% | 31.05%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 129.3983 | 123.2145 | 83.8771 | 128.6833 | 122.8567 | 83.6263 | 128.4873 | 122.4603 | 83.6434 | 127.692 | 121.7149 | 83.1932 | 129.9491 | 124.0353 | 84.4595
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 15.5806 | 14.8858 | 10.1307 | 15.4839 | 14.7867 | 10.0622 | 15.4879 | 14.796 | 10.061 | 15.393 | 14.7062 | 10.0071 | 15.6806 | 14.9741 | 10.175
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 15.2632 | 14.5176 | 9.3201 | 15.1626 | 14.4221 | 9.2588 | 15.1624 | 14.4219 | 9.2588 | 15.0617 | 14.3261 | 9.1974 | 15.3637 | 14.6134 | 9.3815
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.9796 | 0.97524 | 0.91998 | 0.97922 | 0.97532 | 0.92015 | 0.97895 | 0.97469 | 0.92027 | 0.97845 | 0.97413 | 0.91909 | 0.97976 | 0.97589 | 0.92201
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0531 | 1.0567 | 1.0565 | 1.0524 | 1.0527 | 1.0525 | 1.0543 | 1.0568 | 1.0522 | 1.0544 | 1.0568 | 1.0522 | 1.0554 | 1.0559 | 1.0538
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Contingency Outage | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 50.19% | 41.8% | 30.91% | 49.91% | 41.68% | 30.82% | 49.84% | 41.55% | 30.83% | 49.53% | 41.3% | 30.66% | 50.4% | 42.08% | 31.13%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 129.4938 | 123.3233 | 84.0881 | 128.779 | 122.9648 | 83.8365 | 128.5849 | 122.5707 | 83.8535 | 127.7911 | 121.8268 | 83.4049 | 130.0442 | 124.1421 | 84.6677
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 15.5924 | 14.8992 | 10.1567 | 15.4957 | 14.8 | 10.088 | 15.4999 | 14.8097 | 10.0867 | 15.4052 | 14.72 | 10.033 | 15.6924 | 14.9873 | 10.2006
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 15.2615 | 14.5162 | 9.3202 | 15.1609 | 14.4207 | 9.2589 | 15.1607 | 14.4205 | 9.2589 | 15.06 | 14.3247 | 9.1975 | 15.362 | 14.612 | 9.3816
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.97875 | 0.97427 | 0.91764 | 0.97837 | 0.97435 | 0.91781 | 0.97809 | 0.9737 | 0.91793 | 0.97757 | 0.97313 | 0.91672 | 0.97892 | 0.97494 | 0.91971
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0532 | 1.0568 | 1.0566 | 1.0525 | 1.0528 | 1.0526 | 1.0544 | 1.0569 | 1.0522 | 1.0544 | 1.0569 | 1.0523 | 1.0555 | 1.056 | 1.0539
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Contingency Outage | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV
NQ | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 106.7% | 84.21% | 64.01% | 106.3% | 83.87% | 63.85% | 106.9% | 84.56% | 63.79% | 106.4% | 84.16% | 63.62% | 107.2% | 84.63% | 59.71%
NQ | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 224.0477 | 265.2695 | 198.4329 | 223.1426 | 264.1958 | 197.9288 | 224.4447 | 266.3684 | 197.7441 | 223.5246 | 265.1061 | 197.2168 | 225.2209 | 266.5992 | 185.1007
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 26.7383 | 31.5677 | 23.2479 | 26.633 | 31.4454 | 23.1883 | 26.7368 | 31.58 | 23.3484 | 26.6305 | 31.4453 | 23.2916 | 26.8477 | 31.6434 | 21.859
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 25.0971 | 29.1866 | 19.4064 | 25.0074 | 29.0837 | 19.3553 | 25.0877 | 29.1803 | 19.4746 | 24.9786 | 29.0461 | 19.4105 | 25.4646 | 29.583 | 20.7819
NQ | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.93862 | 0.92457 | 0.83476 | 0.93896 | 0.9249 | 0.8347 | 0.93832 | 0.92401 | 0.83409 | 0.93797 | 0.9237 | 0.83337 | 0.94848 | 0.93489 | 0.95073
NQ | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | MOPA_Clare South - Mona Park 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MOPA_Clare South - Mona Park 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0439 | 1.0409 | 1.0248 | 1.044 | 1.0411 | 1.0247 | 1.042 | 1.037 | 1.0328 | 1.0421 | 1.0375 | 1.033 | 1.0427 | 1.0382 | 1.033
NQ | MOPA_Clare South - Mona Park 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 72.24% | 59.88% | 42.43% | 71.81% | 59.53% | 42.25% | 71.95% | 59.82% | 42.15% | 71.49% | 59.41% | 41.98% | 71.91% | 59.55% | 37.71%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 143.7627 | 176.0527 | 122.6084 | 142.8977 | 175.0274 | 122.1135 | 143.1782 | 175.8829 | 121.7993 | 142.2619 | 174.6737 | 121.3221 | 143.1025 | 175.0672 | 108.9704
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 16.0779 | 19.2882 | 13.3541 | 15.9897 | 19.1893 | 13.303 | 15.9835 | 19.1887 | 13.3824 | 15.8875 | 19.0744 | 13.3356 | 16.0333 | 19.1907 | 12.2587
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 15.7087 | 18.6344 | 10.8626 | 15.628 | 18.5445 | 10.816 | 15.6195 | 18.5363 | 10.8602 | 15.5198 | 18.4173 | 10.8006 | 15.8297 | 18.7655 | 12.1214
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.97704 | 0.9661 | 0.81343 | 0.97738 | 0.9664 | 0.81305 | 0.97723 | 0.966 | 0.81153 | 0.97686 | 0.96555 | 0.80991 | 0.9873 | 0.97784 | 0.9888
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97829 | 0.95837 | 0.95276 | 0.97882 | 0.95904 | 0.95296 | 0.97652 | 0.95434 | 0.96111 | 0.9769 | 0.95523 | 0.96152 | 0.98008 | 0.95889 | 0.98407
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | ST-GI-1_Stuart-Giru 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 114.2% | 61.59% | 64.94% | 113.3% | 60.84% | 64.78% | 113.7% | 69.5% | 63.86% | 112.7% | 69.13% | 63.88% | 114.4% | 69.94% | 63.67%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 69138_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 198899_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 69138_1 | TR_LINE 165123_1
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 177.0285 | 141.0499 | 146.7594 | 175.5392 | 139.3332 | 146.4032 | 176.2381 | 159.1491 | 144.3137 | 174.6492 | 158.2972 | 144.3638 | 177.291 | 160.1658 | 143.8981
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 20.3693 | 16.5451 | 17.679 | 20.2264 | 16.3736 | 17.5902 | 20.2781 | 17.4058 | 17.0982 | 20.1381 | 14.9503 | 17.1109 | 20.3865 | 17.4649 | 16.9914
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 20.0901 | 16.5409 | 10.5721 | 19.8836 | 16.3604 | 10.517 | 19.958 | 17.4056 | 10.4662 | 19.7468 | 13.0464 | 10.417 | 20.1179 | 17.4632 | 10.5111
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.98627 | 0.99975 | 0.59792 | 0.98303 | 0.99919 | 0.59781 | 0.98419 | 0.99999 | 0.61205 | 0.98055 | 0.87265 | 0.60872 | 0.98681 | 0.9999 | 0.61853
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0065 | 1.026 | 1.0538 | 1.0079 | 1.0279 | 1.051 | 1.0064 | 0.95669 | 1.0364 | 1.0086 | 0.82558 | 1.0368 | 1.0058 | 0.95384 | 1.0329
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 40.19% | 35.53% | 42.36% | 40.12% | 35.61% | 42.36% | 40.2% | 35.92% | 40.74% | 40.09% | 36.1% | 40.38% | 40.23% | 35.88% | 39.11%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 165132_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 165129_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 75.5663 | 72.8401 | 78.3739 | 75.4345 | 72.9912 | 78.3726 | 75.5675 | 73.6294 | 101.0364 | 75.3681 | 73.9996 | 100.1372 | 75.6262 | 73.5632 | 72.3476
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 8.3078 | 8.0874 | 8.1749 | 8.3052 | 8.0971 | 8.1748 | 8.3078 | 8.1028 | 9.325 | 8.3038 | 8.1032 | 9.2865 | 8.309 | 8.1015 | 8.0929
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 7.3364 | 7.1612 | 7.2055 | 7.3354 | 7.163 | 7.2055 | 7.3364 | 7.1667 | 8.0179 | 7.3349 | 7.1685 | 8.0007 | 7.3368 | 7.1662 | 7.1665
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.86938 | 0.87073 | 0.86988 | 0.86948 | 0.86991 | 0.86988 | 0.86938 | 0.87017 | 0.85983 | 0.86952 | 0.87063 | 0.86117 | 0.86934 | 0.87022 | 0.87041
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 248 | 188 | 205 | 248 | 188 | 205 | 185
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.94532 | 0.95736 | 0.89179 | 0.94686 | 0.9564 | 0.8918 | 0.94531 | 0.94779 | 0.80734 | 0.94763 | 0.94249 | 0.80427 | 0.94462 | 0.94859 | 0.9654
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7182 Ross - Milchester | CT-CR-1_Charters Towers-CARI No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | 7182 Ross - Milchester | CT-CR-1_Charters Towers-CARI No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7182 Ross - Milchester | CT-CR-1_Charters Towers-CARI No 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | 7182 Ross - Milchester | CT-CR-1_Charters Towers-CARI No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 74.12% | 68.51% | 52.9% | 74.65% | 68.36% | 53.24% | 75.7% | 69.41% | 53.99% | 76.39% | 69.9% | 54.47% | 78.86% | 72.53% | 56.45%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 191.218 | 202.0993 | 143.8971 | 192.5898 | 201.6681 | 144.8142 | 195.2981 | 204.751 | 146.8438 | 197.0861 | 206.1939 | 148.1606 | 203.4578 | 213.965 | 153.5418
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 22.5739 | 23.8229 | 17.1254 | 22.6815 | 23.9173 | 17.204 | 22.9907 | 24.2468 | 17.435 | 23.1969 | 24.4602 | 17.5889 | 24.0154 | 25.3374 | 18.2063
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 21.7196 | 22.872 | 16.6221 | 21.8154 | 22.9701 | 16.6951 | 22.101 | 23.2713 | 16.9131 | 22.2914 | 23.4711 | 17.0585 | 23.052 | 24.274 | 17.6402
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.96215 | 0.96009 | 0.97062 | 0.96182 | 0.9604 | 0.97042 | 0.9613 | 0.95977 | 0.97007 | 0.96096 | 0.95956 | 0.96984 | 0.95988 | 0.95803 | 0.96891
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0321 | 1.0305 | 1.0406 | 1.0296 | 1.0368 | 1.0388 | 1.0291 | 1.0352 | 1.0382 | 1.0289 | 1.037 | 1.038 | 1.0319 | 1.0352 | 1.0368
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Contingency Outage | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 10.11% | 10.17% | 5.579% | 10.12% | 10.18% | 5.573% | 10.14% | 10.6% | 5.514% | 10.09% | 10.5% | 5.519% | 10.41% | 11% | 5.535%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 32331_1
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 35.8804 | 39.449 | 23.4324 | 35.9204 | 39.5106 | 23.4048 | 36.0091 | 41.1302 | 23.1606 | 35.8267 | 40.7478 | 23.1816 | 36.9607 | 42.6967 | 23.2482
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 3.8867 | 4.0351 | 3.3633 | 3.8861 | 4.0353 | 3.3515 | 3.8845 | 4.0386 | 3.2439 | 3.8877 | 4.0377 | 3.2533 | 3.9719 | 4.1396 | 3.2332
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 3.8067 | 3.9686 | 1.9938 | 3.8072 | 3.9687 | 1.9939 | 3.8082 | 3.9697 | 1.9942 | 3.8061 | 3.9694 | 1.9942 | 3.9071 | 4.0672 | 2.0432
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.9794 | 0.98351 | 0.59281 | 0.97971 | 0.98348 | 0.59492 | 0.98035 | 0.98291 | 0.61476 | 0.97901 | 0.98308 | 0.61296 | 0.98368 | 0.98248 | 0.63194
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.94758 | 0.89478 | 1.2556 | 0.94637 | 0.89342 | 1.2526 | 0.94367 | 0.85894 | 1.2252 | 0.94926 | 0.8668 | 1.2277 | 0.94004 | 0.84812 | 1.2166
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7460 CPRE-JACR 132kV
NQ | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 0% | 23.33% | 18.23% | 0% | 281.6% | 18.31% | 22.97% | 23.17% | 0% | 22.46% | 22.7% | 0% | 23.57% | 0% | 220%
NQ | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | 0 | TR_LINE 195943_1 | TR_LINE 195943_1 | 0 | TR_LINE 195977_1 | TR_LINE 195943_1 | TR_LINE 195987_1 | TR_LINE 195943_1 | 0 | TR_LINE 195987_1 | TR_LINE 195943_1 | 0 | TR_LINE 195987_1 | 0 | TR_LINE 31680_2
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 0 | 48.068 | 33.9144 | 0 | 470.218 | 34.0474 | 30.3183 | 47.7246 | 0 | 29.6408 | 46.7691 | 0 | 31.1105 | 0 | 211.1739
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 0 | 5.7344 | 4.0682 | 0 | 44.0543 | 4.0696 | 3.5771 | 5.7299 | 0 | 3.4979 | 5.6125 | 0 | 3.681 | 0 | 21.7997
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 0 | 5.5969 | 4.0237 | 0 | 18.1834 | 4.024 | 3.233 | 5.5954 | 0 | 3.1228 | 5.4633 | 0 | 3.36 | 0 | 4.3782
NQ | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0 | 0.97535 | 0.98835 | 0 | 0.40507 | 0.98809 | 0.90355 | 0.97585 | 0 | 0.89251 | 0.97268 | 0 | 0.91251 | 0 | 0.17111
NQ | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 0 | 206 | 186 | 0 | 167 | 186 | 132 | 206 | 0 | 132 | 206 | 0 | 132 | 0 | 96
NQ | ST-GI-1_Stuart-Giru 66 kV | Time | 0:00 | 19:00:00 | 05:30:00 | 0:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 0 | 16:30:00 | 19:00:00 | 0 | 16:30:00 | 0 | 05:30:00
NQ | ST-GI-1_Stuart-Giru 66 kV | Min Voltage at Constrained Conductor (pu) | 0 | 1.0432 | 1.0493 | 0 | 0.8039 | 1.0456 | 1.0321 | 1.0499 | 0 | 1.0323 | 1.0495 | 0 | 1.035 | 0 | 0.89039
NQ | ST-GI-1_Stuart-Giru 66 kV | Contingency Outage | 0% | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | 0% | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | 0% | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | 0% | GI-AY-1_Giru - Ayr 1 66 kV | 0% | GI-AY-1_Giru - Ayr 1 66 kV
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 26.03% | 31.28% | 17.02% | 26.1% | 31.08% | 17.07% | 26.16% | 31.21% | 17.15% | 26.04% | 31.06% | 17.08% | 26.55% | 31.83% | 17.43%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 32143_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32143_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32143_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32143_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32143_1 | TR_LINE 32428_1
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 143.4405 | 182.0209 | 89.1614 | 143.786 | 180.9088 | 89.4423 | 144.1548 | 181.6307 | 89.8673 | 143.4944 | 180.7836 | 89.4774 | 146.3131 | 185.2317 | 91.31
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 17.2095 | 21.4426 | 10.7364 | 17.2104 | 21.4411 | 10.7334 | 17.2891 | 21.5395 | 10.78 | 17.2096 | 21.441 | 10.733 | 17.6058 | 21.9338 | 10.9696
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 17.2078 | 21.4384 | 10.6098 | 17.209 | 21.4378 | 10.6104 | 17.2877 | 21.5358 | 10.6593 | 17.208 | 21.4377 | 10.6104 | 17.6049 | 21.9284 | 10.8544
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.99975 | 0.9998 | 0.9882 | 0.99977 | 0.99984 | 0.98854 | 0.99978 | 0.99983 | 0.9888 | 0.99975 | 0.99985 | 0.98858 | 0.99983 | 0.99975 | 0.9895
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0412 | 1.0305 | 1.0502 | 1.0386 | 1.0367 | 1.0465 | 1.0407 | 1.0374 | 1.0461 | 1.0408 | 1.0374 | 1.0461 | 1.044 | 1.0358 | 1.0475
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Contingency Outage | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 44.95% | 43.26% | 31.7% | 45.18% | 43.1% | 31.85% | 45.57% | 43.54% | 32.15% | 45.83% | 43.7% | 32.35% | 47.18% | 45.21% | 33.44%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32392_1
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 305.1845 | 315.8272 | 210.1626 | 306.7701 | 314.6627 | 211.1766 | 309.4542 | 317.8396 | 213.1839 | 311.2144 | 319.0289 | 214.4696 | 320.3494 | 330.0314 | 221.6774
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 36.1327 | 37.3438 | 25.0647 | 36.2347 | 37.4323 | 25.1414 | 36.5379 | 37.7561 | 25.3666 | 36.74 | 37.9641 | 25.5165 | 37.9303 | 39.2095 | 26.3453
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 35.7474 | 36.892 | 24.9854 | 35.8436 | 36.9894 | 25.0588 | 36.1306 | 37.2923 | 25.2776 | 36.3219 | 37.4928 | 25.4234 | 37.4623 | 38.6759 | 26.2313
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.98934 | 0.9879 | 0.99684 | 0.98921 | 0.98817 | 0.99671 | 0.98885 | 0.98772 | 0.99649 | 0.98862 | 0.98759 | 0.99635 | 0.98766 | 0.98639 | 0.99567
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0356 | 1.0342 | 1.0432 | 1.0332 | 1.0405 | 1.0414 | 1.0328 | 1.039 | 1.0408 | 1.0326 | 1.0409 | 1.0407 | 1.0357 | 1.0392 | 1.0396
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Contingency Outage | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 65.32% | 51.18% | 35.77% | 65.95% | 51.78% | 35.37% | 65.49% | 51.67% | 34.89% | 65.15% | 51.5% | 34.7% | 66.85% | 52.67% | 35.18%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 163.9612 | 160.707 | 100.8657 | 165.5227 | 162.5735 | 99.7332 | 164.3706 | 162.2434 | 98.3852 | 163.5253 | 161.6957 | 97.8454 | 167.792 | 165.3888 | 99.1976
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 19.5696 | 19.2496 | 12.1488 | 19.617 | 19.6014 | 11.9657 | 19.5306 | 19.5516 | 11.7997 | 19.4319 | 19.4845 | 11.7347 | 19.9766 | 19.9098 | 11.9222
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 18.6977 | 18.447 | 11.4832 | 19.2742 | 19.5255 | 11.5185 | 19.1964 | 19.4886 | 11.3802 | 19.091 | 19.4203 | 11.3078 | 19.7978 | 19.8539 | 11.4657
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.95542 | 0.95829 | 0.94521 | 0.98251 | 0.99612 | 0.96263 | 0.98288 | 0.99677 | 0.96445 | 0.98244 | 0.9967 | 0.96362 | 0.99104 | 0.99719 | 0.9617
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0441 | 1.0478 | 1.0536 | 1.0367 | 1.0547 | 1.0495 | 1.0394 | 1.0541 | 1.0491 | 1.0395 | 1.0541 | 1.0491 | 1.0414 | 1.053 | 1.0513
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 53.76% | 52.84% | 36.33% | 53.97% | 54.31% | 36.23% | 54.46% | 54.71% | 36.76% | 54.51% | 54.83% | 36.82% | 56.65% | 56.32% | 37.7%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 32403_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 32403_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 32403_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 32403_1 | TR_LINE 157896_1
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 495.1346 | 530.495 | 333.4915 | 497.0279 | 545.2363 | 332.6046 | 501.6035 | 549.2681 | 337.4726 | 502.0571 | 550.5179 | 338.0019 | 521.7703 | 565.4822 | 346.114
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 59.1735 | 63.3387 | 40.007 | 59.2297 | 65.2368 | 39.7425 | 59.9462 | 65.7923 | 40.3081 | 59.9982 | 65.9361 | 40.3694 | 62.6764 | 67.6475 | 41.4367
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 58.7215 | 62.8941 | 39.4612 | 58.9624 | 65.1966 | 39.4572 | 59.4003 | 65.787 | 40.0641 | 59.4566 | 65.9298 | 40.1296 | 62.6763 | 67.6285 | 40.9191
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.99231 | 0.99293 | 0.98632 | 0.99545 | 0.99938 | 0.99279 | 0.99084 | 0.99992 | 0.99392 | 0.99092 | 0.9999 | 0.99403 | 1 | 0.99972 | 0.98747
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0454 | 1.0444 | 1.0494 | 1.0424 | 1.0466 | 1.0452 | 1.0454 | 1.0477 | 1.0448 | 1.0454 | 1.0476 | 1.0448 | 1.0507 | 1.0464 | 1.0473
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Contingency Outage | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 55.08% | 54.51% | 38.06% | 55.48% | 56.58% | 37.54% | 55.71% | 57.46% | 38.14% | 55.76% | 57.6% | 38.21% | 57.21% | 58.55% | 38.76%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157898_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157898_1 | TR_LINE 157887_1 | TR_LINE 157887_1 | TR_LINE 157898_1 | TR_LINE 157887_1 | TR_LINE 157887_1
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 507.273 | 547.2806 | 349.4355 | 510.9732 | 568.1076 | 344.6346 | 513.0752 | 576.9476 | 350.1504 | 513.5665 | 578.3054 | 350.7383 | 526.8713 | 587.8605 | 355.7961
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 60.971 | 65.6038 | 42.0365 | 61.2326 | 68.393 | 41.4181 | 61.7151 | 69.4139 | 42.0585 | 61.772 | 69.5705 | 42.1272 | 63.3116 | 70.7557 | 42.8386
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 60.971 | 65.5838 | 41.8683 | 61.2088 | 67.6259 | 41.3282 | 61.7129 | 68.6041 | 41.9461 | 61.77 | 68.7489 | 42.0125 | 63.3114 | 70.1114 | 42.8276
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 1 | 0.9997 | 0.996 | 0.99961 | 0.98878 | 0.99783 | 0.99996 | 0.98833 | 0.99733 | 0.99997 | 0.98819 | 0.99728 | 1 | 0.99089 | 0.99974
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0513 | 1.0485 | 1.0523 | 1.0482 | 1.053 | 1.0512 | 1.0521 | 1.0523 | 1.0507 | 1.0521 | 1.0522 | 1.0506 | 1.0511 | 1.0527 | 1.0532
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Contingency Outage | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 67.01% | 55.45% | 104.1% | 66.14% | 55.27% | 103.7% | 85.67% | 70.48% | 125.3% | 84.78% | 69.66% | 124.4% | 85.9% | 70.31% | 53.44%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 88.4512 | 92.5964 | 165.5785 | 87.3091 | 92.2981 | 164.8961 | 113.0831 | 117.6988 | 199.1673 | 111.9092 | 116.3308 | 197.7532 | 113.382 | 117.4187 | 84.9634
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 10.3377 | 10.7885 | 19.2794 | 10.1861 | 10.8132 | 19.1535 | 13.0501 | 13.6126 | 22.2815 | 12.9234 | 13.4643 | 22.1611 | 13.1215 | 13.567 | 9.9871
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 10.1538 | 10.6439 | 17.4561 | 9.9837 | 10.6851 | 17.278 | 12.9855 | 13.5867 | 22.0873 | 12.852 | 13.4335 | 21.9249 | 13.0671 | 13.5432 | 9.5845
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.98215 | 0.98647 | 0.90045 | 0.98009 | 0.98806 | 0.897 | 0.99473 | 0.99788 | 0.98953 | 0.99416 | 0.99749 | 0.9874 | 0.99557 | 0.99804 | 0.95962
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0173 | 1.0137 | 1.0126 | 1.0156 | 1.0193 | 1.0103 | 1.0023 | 1.0038 | 0.9664 | 1.0031 | 1.0047 | 0.96837 | 1.005 | 1.0029 | 1.024
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 48.21% | 32.67% | 27.94% | 53.1% | 36.06% | 30.81% | 55.29% | 37.44% | 32.11% | 54.96% | 37.22% | 31.92% | 55.88% | 37.91% | 32.43%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 124.3794 | 96.377 | 75.9978 | 136.999 | 106.3719 | 83.7978 | 142.6465 | 110.4463 | 87.3335 | 141.8017 | 109.8021 | 86.8257 | 144.1595 | 111.826 | 88.2
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 14.9461 | 11.6269 | 9.1666 | 16.4451 | 12.7809 | 10.067 | 17.1504 | 13.32 | 10.4872 | 17.0501 | 13.2427 | 10.4266 | 17.3502 | 13.4751 | 10.6081
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 14.8818 | 11.6068 | 9.1633 | 16.3313 | 12.7355 | 10.0531 | 16.9979 | 13.2543 | 10.4623 | 16.9003 | 13.1783 | 10.4024 | 17.193 | 13.4063 | 10.582
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.9957 | 0.99827 | 0.99965 | 0.99308 | 0.99645 | 0.99861 | 0.99111 | 0.99507 | 0.99762 | 0.99121 | 0.99514 | 0.99767 | 0.99094 | 0.99489 | 0.99754
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0511 | 1.0553 | 1.0551 | 1.05 | 1.051 | 1.0509 | 1.0517 | 1.055 | 1.0504 | 1.0518 | 1.055 | 1.0505 | 1.0528 | 1.0541 | 1.0521
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Contingency Outage | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 42.92% | 41.42% | 92.51% | 42.25% | 41.32% | 92.09% | 56.4% | 54.35% | 112.6% | 55.74% | 53.62% | 111.7% | 56.6% | 54.2% | 44.68%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 76.8232 | 78.293 | 155.4102 | 75.6295 | 78.0946 | 154.7107 | 100.9538 | 102.7123 | 189.1036 | 99.7688 | 101.3369 | 187.6586 | 101.3192 | 102.4304 | 75.0657
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 8.434 | 8.5417 | 17.0353 | 8.3042 | 8.5617 | 16.9503 | 10.6124 | 10.7564 | 18.0251 | 10.5139 | 10.6428 | 18.0143 | 10.6676 | 10.7147 | 8.3791
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 8.1983 | 8.3319 | 13.62 | 8.0495 | 8.3776 | 13.4671 | 10.4461 | 10.6504 | 16.8532 | 10.3406 | 10.5303 | 16.7537 | 10.5197 | 10.6139 | 7.9097
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.97205 | 0.97545 | 0.79664 | 0.96933 | 0.9785 | 0.7916 | 0.9841 | 0.98996 | 0.93264 | 0.9833 | 0.98925 | 0.92761 | 0.98592 | 0.99041 | 0.94398
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95882 | 0.95276 | 0.95791 | 0.95901 | 0.95739 | 0.95749 | 0.91737 | 0.91374 | 0.83079 | 0.91969 | 0.91641 | 0.83682 | 0.91878 | 0.9127 | 0.97518
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV
SW | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 11.3% | 13.14% | 9.211% | 11.3% | 13.14% | 9.21% | 11.3% | 13.14% | 9.211% | 11.3% | 13.14% | 9.207% | 11.3% | 13.14% | 9.212%
SW | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 73.4651 | 86.5809 | 52.9616 | 73.4686 | 86.5853 | 52.9563 | 73.4717 | 86.5891 | 52.966 | 73.4706 | 86.5862 | 52.9414 | 73.4745 | 86.5912 | 52.9663
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 17.8298 | 20.9883 | 12.727 | 17.8295 | 20.9881 | 12.7283 | 17.8293 | 20.988 | 12.7259 | 17.8294 | 20.9881 | 12.7318 | 17.8291 | 20.9879 | 12.7259
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 17.1864 | 20.5966 | 11.4303 | 17.1864 | 20.5966 | 11.4303 | 17.1864 | 20.5966 | 11.4303 | 17.1864 | 20.5966 | 11.4302 | 17.1864 | 20.5967 | 11.4303
SW | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.96391 | 0.98134 | 0.89812 | 0.96393 | 0.98135 | 0.89802 | 0.96394 | 0.98135 | 0.89819 | 0.96394 | 0.98135 | 0.89777 | 0.96395 | 0.98136 | 0.8982
SW | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575
SW | 7235_Bulli Creek - Waggamba 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 7235_Bulli Creek - Waggamba 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0615 | 1.0603 | 1.0511 | 1.0615 | 1.0602 | 1.0513 | 1.0614 | 1.0602 | 1.0509 | 1.0614 | 1.0602 | 1.0519 | 1.0614 | 1.0601 | 1.0509
SW | 7235_Bulli Creek - Waggamba 132 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | 3196_Tara 33 kV | % of Rated A | 18.48% | 15.48% | 9.844% | 18.82% | 15.76% | 10.08% | 18.82% | 15.76% | 10.08% | 18.81% | 15.74% | 10.08% | 18.49% | 15.48% | 9.844%
SW | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1
SW | 3196_Tara 33 kV | Loading (A) | 17.1859 | 17.9568 | 11.4188 | 17.5009 | 18.2778 | 11.6958 | 17.502 | 18.2785 | 11.6969 | 17.4891 | 18.2635 | 11.6961 | 17.1914 | 17.9603 | 11.4186
SW | 3196_Tara 33 kV | Loading (MVA) | 0.96986 | 1.0134 | 0.64966 | 0.98839 | 1.0324 | 0.66276 | 0.98836 | 1.0323 | 0.66512 | 0.98877 | 1.0327 | 0.66308 | 0.96973 | 1.0133 | 0.64902
SW | 3196_Tara 33 kV | Loading (MW) | 0.93269 | 0.97771 | 0.51326 | 0.93947 | 0.9848 | 0.5168 | 0.93947 | 0.9848 | 0.51683 | 0.93943 | 0.98476 | 0.5168 | 0.93271 | 0.97773 | 0.51324
SW | 3196_Tara 33 kV | Power Factor | 0.96168 | 0.96478 | 0.79004 | 0.9505 | 0.95394 | 0.77977 | 0.95054 | 0.95396 | 0.77705 | 0.9501 | 0.95357 | 0.7794 | 0.96182 | 0.9649 | 0.7908
SW | 3196_Tara 33 kV | Rating (A) | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116
SW | 3196_Tara 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 3196_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98728 | 0.98736 | 0.99538 | 0.98804 | 0.98816 | 0.9914 | 0.98795 | 0.9881 | 0.99484 | 0.98909 | 0.98928 | 0.99186 | 0.98684 | 0.98706 | 0.99441
SW | 3196_Tara 33 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV
SW | 3203_Miles 33 kV | % of Rated A | 64.47% | 66.62% | 41.6% | 64.48% | 66.64% | 41.6% | 64.48% | 66.65% | 41.61% | 63.38% | 65.48% | 40.93% | 64.5% | 66.66% | 41.62%
SW | 3203_Miles 33 kV | Limiting Line Name | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1
SW | 3203_Miles 33 kV | Loading (A) | 228.864 | 236.5089 | 147.6669 | 228.89 | 236.5836 | 147.6677 | 228.9174 | 236.6112 | 147.7307 | 225.0034 | 232.4632 | 145.3149 | 228.9636 | 236.6502 | 147.7398
SW | 3203_Miles 33 kV | Loading (MVA) | 12.9015 | 13.3154 | 8.4608 | 12.8994 | 13.3158 | 8.4608 | 12.8996 | 13.316 | 8.4624 | 12.6955 | 13.1011 | 8.3307 | 12.8998 | 13.3162 | 8.4624
SW | 3203_Miles 33 kV | Loading (MW) | 12.7203 | 13.1358 | 8.4225 | 12.7188 | 13.136 | 8.4225 | 12.7189 | 13.1361 | 8.4232 | 12.5227 | 12.9301 | 8.2945 | 12.719 | 13.1362 | 8.4232
SW | 3203_Miles 33 kV | Power Factor | 0.98589 | 0.98646 | 0.99542 | 0.98594 | 0.98644 | 0.99542 | 0.98593 | 0.98643 | 0.99532 | 0.98633 | 0.98689 | 0.9956 | 0.98592 | 0.98643 | 0.99531
SW | 3203_Miles 33 kV | Rating (A) | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355
SW | 3203_Miles 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 3203_Miles 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98622 | 0.98495 | 1.0024 | 0.98595 | 0.98467 | 1.0024 | 0.98584 | 0.98457 | 1.0022 | 0.98712 | 0.98597 | 1.003 | 0.98566 | 0.98442 | 1.0021
SW | 3203_Miles 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F217R_St George 66 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F217R_St George 66 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F217R_St George 66 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F217R_St George 66 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F217R_St George 66 kV
SW | F060T_Tara 33 kV | % of Rated A | 18.36% | 14.65% | 9.765% | 18.7% | 14.91% | 10% | 18.7% | 14.91% | 10% | 18.69% | 14.9% | 10% | 18.37% | 14.65% | 9.765%
SW | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1
SW | F060T_Tara 33 kV | Loading (A) | 17.0754 | 17.8674 | 11.4255 | 17.3879 | 18.1899 | 11.7007 | 17.389 | 18.1926 | 11.7047 | 17.3786 | 18.1825 | 11.7009 | 17.0808 | 17.8775 | 11.4255
SW | F060T_Tara 33 kV | Loading (MVA) | 0.96983 | 1.0132 | 0.65715 | 0.98839 | 1.032 | 0.66989 | 0.98836 | 1.032 | 0.67343 | 0.98851 | 1.0322 | 0.67004 | 0.9697 | 1.013 | 0.65711
SW | F060T_Tara 33 kV | Loading (MW) | 0.93253 | 0.9777 | 0.51331 | 0.9393 | 0.9848 | 0.51686 | 0.9393 | 0.9848 | 0.5169 | 0.93929 | 0.98478 | 0.51686 | 0.93255 | 0.97772 | 0.51331
SW | F060T_Tara 33 kV | Power Factor | 0.96154 | 0.965 | 0.78111 | 0.95033 | 0.95428 | 0.77155 | 0.95037 | 0.9543 | 0.76756 | 0.95021 | 0.95409 | 0.77139 | 0.96168 | 0.96518 | 0.78116
SW | F060T_Tara 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | F060T_Tara 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F060T_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99366 | 0.99203 | 1.0063 | 0.99447 | 0.99254 | 1.0016 | 0.99438 | 0.99237 | 1.0066 | 0.99513 | 0.99312 | 1.0018 | 0.9932 | 0.9913 | 1.0062
SW | F060T_Tara 33 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F099D_Warra 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F069C_Brigalow 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV
SW | F067C_Kogan 33 kV | % of Rated A | 49.39% | 31.22% | 27.88% | 49.41% | 31.23% | 27.88% | 49.41% | 31.23% | 27.88% | 49.4% | 31.23% | 27.88% | 49.44% | 31.25% | 27.89%
SW | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1
SW | F067C_Kogan 33 kV | Loading (A) | 45.9326 | 38.0907 | 32.6181 | 45.9487 | 38.1023 | 32.6182 | 45.9542 | 38.1066 | 32.6244 | 45.9414 | 38.0947 | 32.6163 | 45.9812 | 38.1284 | 32.6308
SW | F067C_Kogan 33 kV | Loading (MVA) | 2.5622 | 2.1344 | 1.8256 | 2.5623 | 2.1345 | 1.8256 | 2.5623 | 2.1345 | 1.8257 | 2.5622 | 2.1345 | 1.8256 | 2.5625 | 2.1347 | 1.8257
SW | F067C_Kogan 33 kV | Loading (MW) | 2.1218 | 1.8037 | 1.5351 | 2.1218 | 1.8037 | 1.5351 | 2.1218 | 1.8037 | 1.5351 | 2.1218 | 1.8037 | 1.5351 | 2.1219 | 1.8037 | 1.5351
SW | F067C_Kogan 33 kV | Power Factor | 0.82534 | 0.84198 | 0.83727 | 0.82533 | 0.84197 | 0.83727 | 0.82532 | 0.84196 | 0.83726 | 0.82533 | 0.84198 | 0.83727 | 0.82529 | 0.84193 | 0.83724
SW | F067C_Kogan 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | F067C_Kogan 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F067C_Kogan 33 kV | Min Voltage at Constrained Conductor (pu) | 0.97034 | 0.97671 | 0.9772 | 0.97003 | 0.97644 | 0.97719 | 0.96992 | 0.97634 | 0.97702 | 0.97017 | 0.97662 | 0.97724 | 0.9694 | 0.97582 | 0.97684
SW | F067C_Kogan 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV
SW | F069C_Brigalow 33 kV | % of Rated A | 4.882% | 4.845% | 4.929% | 4.88% | 4.844% | 4.929% | 4.88% | 4.843% | 4.928% | 4.88% | 4.844% | 4.928% | 4.879% | 4.842% | 4.927%
SW | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1
SW | F069C_Brigalow 33 kV | Loading (A) | 4.296 | 4.2637 | 4.3371 | 4.2947 | 4.2626 | 4.3371 | 4.2943 | 4.2622 | 4.3363 | 4.2947 | 4.2626 | 4.337 | 4.2931 | 4.2612 | 4.3359
SW | F069C_Brigalow 33 kV | Loading (MVA) | 0.25 | 0.24823 | 0.25168 | 0.24986 | 0.24811 | 0.25168 | 0.24981 | 0.24806 | 0.25159 | 0.24985 | 0.24811 | 0.25167 | 0.24968 | 0.24794 | 0.25154
SW | F069C_Brigalow 33 kV | Loading (MW) | 0.044775 | 0.072579 | 0.033652 | 0.044774 | 0.072579 | 0.033652 | 0.044774 | 0.072579 | 0.033652 | 0.044774 | 0.072579 | 0.033652 | 0.044773 | 0.072578 | 0.033652
SW | F069C_Brigalow 33 kV | Power Factor | 0.1791 | 0.29239 | 0.13371 | 0.1792 | 0.29253 | 0.13371 | 0.17923 | 0.29258 | 0.13376 | 0.1792 | 0.29253 | 0.13372 | 0.17933 | 0.29273 | 0.13378
SW | F069C_Brigalow 33 kV | Rating (A) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
SW | F069C_Brigalow 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F069C_Brigalow 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0181 | 1.0186 | 1.0153 | 1.0178 | 1.0183 | 1.0152 | 1.0178 | 1.0182 | 1.0151 | 1.0178 | 1.0183 | 1.0152 | 1.0175 | 1.018 | 1.015
SW | F069C_Brigalow 33 kV | Contingency Outage | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV
SW | F073C_Fairymeadow 33 kV | % of Rated A | 4.092% | 4.483% | 2.408% | 4.093% | 4.483% | 2.408% | 4.093% | 4.483% | 2.408% | 4.092% | 4.482% | 2.408% | 4.094% | 4.472% | 2.408%
SW | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_LINE 177654_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 177654_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 177654_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 177654_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 177654_1 | TR_LINE 174241_1
SW | F073C_Fairymeadow 33 kV | Loading (A) | 3.8054 | 5.4248 | 2.7933 | 3.8062 | 5.4239 | 2.7933 | 3.8065 | 5.4245 | 2.7934 | 3.8058 | 5.4234 | 2.7933 | 3.8078 | 5.4113 | 2.7935
SW | F073C_Fairymeadow 33 kV | Loading (MVA) | 0.21939 | 0.30776 | 0.16043 | 0.21937 | 0.30776 | 0.16043 | 0.21937 | 0.30776 | 0.1604 | 0.21938 | 0.30776 | 0.16043 | 0.21934 | 0.30773 | 0.16038
SW | F073C_Fairymeadow 33 kV | Loading (MW) | 0.21502 | 0.30597 | 0.14146 | 0.21502 | 0.30597 | 0.14146 | 0.21502 | 0.30597 | 0.14146 | 0.21502 | 0.30597 | 0.14146 | 0.21501 | 0.30599 | 0.14146
SW | F073C_Fairymeadow 33 kV | Power Factor | 0.98007 | 0.99414 | 0.88177 | 0.98014 | 0.99415 | 0.88177 | 0.98016 | 0.99414 | 0.88188 | 0.98011 | 0.99415 | 0.88174 | 0.98028 | 0.99428 | 0.882
SW | F073C_Fairymeadow 33 kV | Rating (A) | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116
SW | F073C_Fairymeadow 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F073C_Fairymeadow 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0086 | 0.99254 | 1.0048 | 1.0083 | 0.99271 | 1.0048 | 1.0082 | 0.99261 | 1.0046 | 1.0085 | 0.9928 | 1.0048 | 1.0077 | 0.99495 | 1.0044
SW | F073C_Fairymeadow 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F071C RYWUNG | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV
SW | F074C_Miles-Condamine 33 kV | % of Rated A | 16.71% | 13.15% | 7.618% | 16.71% | 13.15% | 7.618% | 16.71% | 13.15% | 7.62% | 16.69% | 13.13% | 7.615% | 16.72% | 13.15% | 7.62%
SW | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1
SW | F074C_Miles-Condamine 33 kV | Loading (A) | 23.8885 | 38.7787 | 20.0362 | 23.8964 | 38.7901 | 20.0362 | 23.899 | 38.7943 | 20.04 | 23.8669 | 38.7352 | 20.0274 | 23.9039 | 38.8009 | 20.0409
SW | F074C_Miles-Condamine 33 kV | Loading (MVA) | 1.3498 | 2.1817 | 1.1395 | 1.3498 | 2.1817 | 1.1395 | 1.3498 | 2.1817 | 1.1395 | 1.3498 | 2.1816 | 1.1397 | 1.3498 | 2.1817 | 1.1395
SW | F074C_Miles-Condamine 33 kV | Loading (MW) | 1.3484 | 2.181 | 1.1072 | 1.3485 | 2.181 | 1.1072 | 1.3485 | 2.181 | 1.1072 | 1.3484 | 2.1809 | 1.1072 | 1.3485 | 2.1811 | 1.1072
SW | F074C_Miles-Condamine 33 kV | Power Factor | 0.999 | 0.99969 | 0.97165 | 0.99901 | 0.99969 | 0.97165 | 0.99901 | 0.9997 | 0.97171 | 0.99894 | 0.99967 | 0.97152 | 0.99902 | 0.9997 | 0.97172
SW | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263
SW | F074C_Miles-Condamine 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F074C_Miles-Condamine 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98811 | 0.98427 | 0.995 | 0.98778 | 0.98399 | 0.995 | 0.98767 | 0.98388 | 0.99476 | 0.989 | 0.98534 | 0.99556 | 0.98747 | 0.98372 | 0.9947
SW | F074C_Miles-Condamine 33 kV | Contingency Outage | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW | F075S_St George Town 33 kV | % of Rated A | 49.62% | 50.39% | 29.63% | 49.61% | 50.38% | 29.62% | 49.61% | 50.38% | 29.62% | 48.7% | 49.47% | 29.09% | 49.61% | 50.38% | 29.62%
SW | F075S_St George Town 33 kV | Limiting Line Name | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1 | TR_LINE 25567_1
SW | F075S_St George Town 33 kV | Loading (A) | 96.7525 | 96.7543 | 48.5871 | 96.735 | 96.7385 | 48.585 | 96.7358 | 96.7371 | 48.5839 | 94.9745 | 94.982 | 47.7101 | 96.7309 | 96.7348 | 48.5831
SW | F075S_St George Town 33 kV | Loading (MVA) | 5.5091 | 5.5179 | 2.7501 | 5.509 | 5.5178 | 2.7501 | 5.509 | 5.5178 | 2.7501 | 5.4075 | 5.4163 | 2.7003 | 5.509 | 5.5178 | 2.7501
SW | F075S_St George Town 33 kV | Loading (MW) | 5.3448 | 5.3536 | 2.6872 | 5.3448 | 5.3536 | 2.6872 | 5.3448 | 5.3536 | 2.6872 | 5.2476 | 5.2564 | 2.639 | 5.3448 | 5.3536 | 2.6872
SW | F075S_St George Town 33 kV | Power Factor | 0.97018 | 0.97023 | 0.97699 | 0.97019 | 0.97024 | 0.97699 | 0.97019 | 0.97024 | 0.97699 | 0.97043 | 0.97048 | 0.97713 | 0.97019 | 0.97024 | 0.977
SW | F075S_St George Town 33 kV | Rating (A) | 195 | 192 | 164 | 195 | 192 | 164 | 195 | 192 | 164 | 195 | 192 | 164 | 195 | 192 | 164
SW | F075S_St George Town 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F075S_St George Town 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99046 | 0.99203 | 0.98768 | 0.99063 | 0.99218 | 0.98772 | 0.99062 | 0.9922 | 0.98774 | 0.99051 | 0.99205 | 0.9877 | 0.99067 | 0.99222 | 0.98776
SW | F075S_St George Town 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV
SW | F077C_Wandoan 33 kV | % of Rated A | 40.63% | 26.11% | 14.16% | 40.65% | 26.12% | 14.16% | 40.65% | 26.12% | 14.16% | 39.52% | 25.34% | 13.78% | 40.66% | 26.13% | 14.16%
SW | F077C_Wandoan 33 kV | Limiting Line Name | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1
SW | F077C_Wandoan 33 kV | Loading (A) | 70.2944 | 72.5873 | 39.3575 | 70.322 | 72.6122 | 39.3577 | 70.3311 | 72.6214 | 39.3683 | 68.3696 | 70.4384 | 38.2957 | 70.3476 | 72.6358 | 39.3708
SW | F077C_Wandoan 33 kV | Loading (MVA) | 3.8609 | 3.9792 | 2.2254 | 3.8611 | 3.9793 | 2.2254 | 3.8611 | 3.9794 | 2.2254 | 3.7613 | 3.8714 | 2.1674 | 3.8612 | 3.9795 | 2.2254
SW | F077C_Wandoan 33 kV | Loading (MW) | 3.7547 | 3.8764 | 2.1932 | 3.7548 | 3.8765 | 2.1932 | 3.7548 | 3.8765 | 2.1932 | 3.6585 | 3.7728 | 2.137 | 3.7549 | 3.8766 | 2.1932
SW | F077C_Wandoan 33 kV | Power Factor | 0.97249 | 0.97419 | 0.98554 | 0.97247 | 0.97417 | 0.98554 | 0.97246 | 0.97416 | 0.98553 | 0.97267 | 0.97453 | 0.98595 | 0.97245 | 0.97415 | 0.98553
SW | F077C_Wandoan 33 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | F077C_Wandoan 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F077C_Wandoan 33 kV | Min Voltage at Constrained Conductor (pu) | 0.96087 | 0.95902 | 0.98922 | 0.96054 | 0.95873 | 0.98921 | 0.96042 | 0.95862 | 0.98897 | 0.96244 | 0.96151 | 0.99017 | 0.96022 | 0.95845 | 0.98891
SW | F077C_Wandoan 33 kV | Contingency Outage | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F069C_Brigalow 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW | F077S_Main Camp 33 kV | % of Rated A | 22.56% | 16.16% | 13.16% | 22.55% | 16.16% | 13.16% | 22.55% | 16.16% | 13.16% | 22.55% | 16.16% | 13.16% | 22.55% | 16.16% | 13.16%
SW | F077S_Main Camp 33 kV | Limiting Line Name | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26911_1 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26911_1 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26911_1 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26911_1 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26911_1
SW | F077S_Main Camp 33 kV | Loading (A) | 62.4777 | 47.6696 | 34.6127 | 62.4654 | 47.6614 | 34.6112 | 62.4644 | 47.6607 | 34.6104 | 62.472 | 47.6667 | 34.615 | 62.461 | 47.6583 | 34.6098
SW | F077S_Main Camp 33 kV | Loading (MVA) | 3.5555 | 2.7161 | 1.9366 | 3.5554 | 2.716 | 1.9366 | 3.5553 | 2.716 | 1.9366 | 3.5554 | 2.7161 | 1.9366 | 3.5553 | 2.716 | 1.9366
SW | F077S_Main Camp 33 kV | Loading (MW) | 3.2339 | 2.5489 | 1.6253 | 3.2339 | 2.5489 | 1.6253 | 3.2339 | 2.5489 | 1.6253 | 3.2339 | 2.5489 | 1.6253 | 3.2339 | 2.5489 | 1.6253
SW | F077S_Main Camp 33 kV | Power Factor | 0.90956 | 0.93845 | 0.83919 | 0.90959 | 0.93847 | 0.8392 | 0.90959 | 0.93848 | 0.8392 | 0.90958 | 0.93846 | 0.83919 | 0.9096 | 0.93848 | 0.8392
SW | F077S_Main Camp 33 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
SW | F077S_Main Camp 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F077S_Main Camp 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99557 | 0.99681 | 0.9789 | 0.99573 | 0.99695 | 0.97894 | 0.99574 | 0.99696 | 0.97896 | 0.99565 | 0.99686 | 0.97883 | 0.99579 | 0.997 | 0.97898
SW | F077S_Main Camp 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV
SW | F079S_St George Meatworks 33 kV | % of Rated A | 12.45% | 11.28% | 10.08% | 12.45% | 11.28% | 10.08% | 12.45% | 11.28% | 10.08% | 12.45% | 11.28% | 10.08% | 12.45% | 11.28% | 10.08%
SW | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1
SW | F079S_St George Meatworks 33 kV | Loading (A) | 7.5954 | 8.6884 | 7.3609 | 7.5965 | 8.6886 | 7.3612 | 7.5966 | 8.6886 | 7.3614 | 7.5945 | 8.6881 | 7.3601 | 7.5969 | 8.6887 | 7.3615
SW | F079S_St George Meatworks 33 kV | Loading (MVA) | 0.43593 | 0.49916 | 0.41871 | 0.43608 | 0.49926 | 0.41875 | 0.43609 | 0.49927 | 0.41877 | 0.43581 | 0.49905 | 0.41862 | 0.43613 | 0.49929 | 0.41878
SW | F079S_St George Meatworks 33 kV | Loading (MW) | 0.24855 | 0.40205 | 0.1745 | 0.24855 | 0.40206 | 0.1745 | 0.24855 | 0.40206 | 0.1745 | 0.24854 | 0.40205 | 0.17449 | 0.24856 | 0.40206 | 0.1745
SW | F079S_St George Meatworks 33 kV | Power Factor | 0.57015 | 0.80546 | 0.41675 | 0.56998 | 0.80532 | 0.41671 | 0.56996 | 0.8053 | 0.4167 | 0.5703 | 0.80563 | 0.41682 | 0.56992 | 0.80526 | 0.41669
SW | F079S_St George Meatworks 33 kV | Rating (A) | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73
SW | F079S_St George Meatworks 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F079S_St George Meatworks 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0041 | 1.0051 | 0.99519 | 1.0043 | 1.0053 | 0.99524 | 1.0043 | 1.0053 | 0.99526 | 1.004 | 1.0049 | 0.99509 | 1.0044 | 1.0053 | 0.99528
SW | F079S_St George Meatworks 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F083C_Chinchilla 33 kV | % of Rated A | 68.7% | 71.54% | 35.13% | 68.72% | 71.56% | 35.13% | 68.72% | 71.57% | 35.13% | 68.71% | 71.56% | 35.13% | 69.72% | 72.62% | 35.62%
SW | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1
SW | F083C_Chinchilla 33 kV | Loading (A) | 229.4448 | 241.0971 | 102.5723 | 229.5151 | 241.1627 | 102.5727 | 229.5389 | 241.187 | 102.59 | 229.5002 | 241.1404 | 102.5702 | 232.849 | 244.7355 | 104.0102
SW | F083C_Chinchilla 33 kV | Loading (MVA) | 13.2366 | 13.8994 | 5.8918 | 13.2368 | 13.8996 | 5.8918 | 13.2368 | 13.8996 | 5.8918 | 13.2367 | 13.8995 | 5.8918 | 13.42 | 14.0959 | 5.9722
SW | F083C_Chinchilla 33 kV | Loading (MW) | 12.9495 | 13.5883 | 5.8005 | 12.9496 | 13.5884 | 5.8005 | 12.9496 | 13.5884 | 5.8005 | 12.9496 | 13.5883 | 5.8005 | 13.1263 | 13.7773 | 5.8792
SW | F083C_Chinchilla 33 kV | Power Factor | 0.97831 | 0.97762 | 0.9845 | 0.9783 | 0.97761 | 0.9845 | 0.9783 | 0.97761 | 0.9845 | 0.9783 | 0.97761 | 0.9845 | 0.97811 | 0.9774 | 0.98443
SW | F083C_Chinchilla 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | F083C_Chinchilla 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F083C_Chinchilla 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0087 | 1.008 | 1.0047 | 1.0084 | 1.0077 | 1.0047 | 1.0083 | 1.0076 | 1.0045 | 1.0085 | 1.0078 | 1.0047 | 1.0077 | 1.007 | 1.0043
SW | F083C_Chinchilla 33 kV | Contingency Outage | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG
SW | F106R_Roma East 33 kV | % of Rated A | 83.13% | 76.89% | 42.82% | 87.72% | 81.16% | 45.13% | 87.52% | 81.16% | 45.13% | 86.09% | 79.72% | 44.34% | 87.56% | 80.95% | 45.14%
SW | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2
SW | F106R_Roma East 33 kV | Loading (A) | 212.8156 | 196.064 | 93.7676 | 224.5739 | 206.9464 | 98.8274 | 224.0472 | 206.969 | 98.8441 | 220.3948 | 203.2886 | 97.0965 | 224.148 | 206.4305 | 98.8584
SW | F106R_Roma East 33 kV | Loading (MVA) | 11.6711 | 10.7784 | 5.2454 | 12.3006 | 11.3586 | 5.5235 | 12.2992 | 11.3587 | 5.5236 | 12.0899 | 11.165 | 5.4307 | 12.2995 | 11.3574 | 5.5236
SW | F106R_Roma East 33 kV | Loading (MW) | 11.2935 | 10.4452 | 5.1223 | 11.8904 | 10.9973 | 5.3918 | 11.8901 | 10.9973 | 5.3918 | 11.6913 | 10.8132 | 5.302 | 11.8902 | 10.997 | 5.3918
SW | F106R_Roma East 33 kV | Power Factor | 0.96765 | 0.96909 | 0.97652 | 0.96665 | 0.96818 | 0.97615 | 0.96674 | 0.96818 | 0.97615 | 0.96703 | 0.96849 | 0.97628 | 0.96672 | 0.96827 | 0.97615
SW | F106R_Roma East 33 kV | Rating (A) | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219
SW | F106R_Roma East 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F106R_Roma East 33 kV | Min Voltage at Constrained Conductor (pu) | 0.95841 | 0.96082 | 0.97826 | 0.95716 | 0.95924 | 0.97737 | 0.9593 | 0.95914 | 0.97721 | 0.95862 | 0.95987 | 0.97809 | 0.95889 | 0.96153 | 0.97707
SW | F106R_Roma East 33 kV | Contingency Outage | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | 790_Warwick-Stanthorpe 110 kV | F077S_Main Camp 33 kV | F081S_Noondoo 33 kV | 790_Warwick-Stanthorpe 110 kV | F049R_Roma North 33 kV | F081S_Noondoo 33 kV | 790_Warwick-Stanthorpe 110 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F069C_Brigalow 33 kV | F049R_Roma North 33 kV | F049R_Roma North 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F127R_Roma West 33 kV | % of Rated A | 79.29% | 59.09% | 31.1% | 77.75% | 57.97% | 30.52% | 77.57% | 57.98% | 30.52% | 77.66% | 57.95% | 30.5% | 79.16% | 58.99% | 31.13%
SW | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1
SW | F127R_Roma West 33 kV | Loading (A) | 91.9774 | 94.5513 | 48.5172 | 90.1943 | 92.7581 | 47.608 | 89.9869 | 92.7681 | 47.616 | 90.0872 | 92.7277 | 47.5794 | 91.8244 | 94.3788 | 48.556
SW | F127R_Roma West 33 kV | Loading (MVA) | 5.0315 | 5.1739 | 2.7064 | 4.9351 | 5.0748 | 2.655 | 4.9347 | 5.0748 | 2.655 | 4.9349 | 5.0748 | 2.6549 | 5.0312 | 5.1736 | 2.7064
SW | F127R_Roma West 33 kV | Loading (MW) | 4.9372 | 5.0756 | 2.6674 | 4.8436 | 4.9793 | 2.6169 | 4.8435 | 4.9793 | 2.6169 | 4.8435 | 4.9793 | 2.6169 | 4.9372 | 5.0755 | 2.6674
SW | F127R_Roma West 33 kV | Power Factor | 0.98127 | 0.98099 | 0.98559 | 0.98147 | 0.98118 | 0.98568 | 0.98151 | 0.98118 | 0.98567 | 0.98149 | 0.98119 | 0.98568 | 0.9813 | 0.98103 | 0.98558
SW | F127R_Roma West 33 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
SW | F127R_Roma West 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F127R_Roma West 33 kV | Min Voltage at Constrained Conductor (pu) | 0.95703 | 0.95734 | 0.97592 | 0.95725 | 0.95715 | 0.97566 | 0.95939 | 0.95705 | 0.97549 | 0.95836 | 0.95745 | 0.97623 | 0.95858 | 0.95903 | 0.97515
SW | F127R_Roma West 33 kV | Contingency Outage | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | 790_Warwick-Stanthorpe 110 kV | F077S_Main Camp 33 kV | F081S_Noondoo 33 kV | 790_Warwick-Stanthorpe 110 kV | F049R_Roma North 33 kV | F081S_Noondoo 33 kV | 790_Warwick-Stanthorpe 110 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F069C_Brigalow 33 kV | F049R_Roma North 33 kV | F049R_Roma North 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F217R_St George 66 kV | % of Rated A | 33.13% | 34.68% | 25.68% | 33.23% | 34.77% | 25.71% | 33.24% | 34.78% | 25.72% | 32.9% | 34.44% | 25.54% | 33.27% | 34.8% | 25.73%
SW | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW | F217R_St George 66 kV | Loading (A) | 148.0886 | 157.457 | 101.6985 | 148.5411 | 157.854 | 101.798 | 148.5779 | 157.8907 | 101.8461 | 147.06 | 156.3358 | 101.1303 | 148.6992 | 158.0059 | 101.881
SW | F217R_St George 66 kV | Loading (MVA) | 16.7197 | 17.7685 | 11.6543 | 16.7514 | 17.7957 | 11.6622 | 16.754 | 17.7982 | 11.666 | 16.5976 | 17.6388 | 11.5907 | 16.7625 | 17.8061 | 11.6688
SW | F217R_St George 66 kV | Loading (MW) | 15.4647 | 16.5403 | 10.5982 | 15.4786 | 16.5533 | 10.6001 | 15.4797 | 16.5545 | 10.6011 | 15.3329 | 16.4032 | 10.5374 | 15.4834 | 16.5583 | 10.6017
SW | F217R_St George 66 kV | Power Factor | 0.9249 | 0.93084 | 0.90937 | 0.92398 | 0.93014 | 0.90892 | 0.9239 | 0.93008 | 0.90871 | 0.92377 | 0.92991 | 0.90912 | 0.92366 | 0.92988 | 0.90855
SW | F217R_St George 66 kV | Rating (A) | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396
SW | F217R_St George 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F217R_St George 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98764 | 0.98714 | 1.0025 | 0.9865 | 0.98617 | 1.0022 | 0.98641 | 0.98608 | 1.002 | 0.98729 | 0.98696 | 1.0026 | 0.9861 | 0.98579 | 1.0019
SW | F217R_St George 66 kV | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F7164 | % of Rated A | 76.5% | 48.19% | 36.61% | 77.17% | 48.57% | 36.76% | 77.18% | 48.57% | 36.77% | 76.6% | 48.21% | 36.61% | 77.32% | 48.66% | 36.81%
SW | F7164 | Limiting Line Name | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1
SW | F7164 | Loading (A) | 132.3443 | 133.9607 | 101.7822 | 133.5108 | 135.0164 | 102.2011 | 133.5271 | 135.0327 | 102.2208 | 132.5215 | 134.0114 | 101.787 | 133.7668 | 135.2743 | 102.3272
SW | F7164 | Loading (MVA) | 31.7369 | 32.1122 | 24.4745 | 31.9976 | 32.3487 | 24.5724 | 31.9984 | 32.3495 | 24.5732 | 31.7722 | 32.1205 | 24.4806 | 32.0489 | 32.4013 | 24.5971
SW | F7164 | Loading (MW) | 31.3564 | 31.7252 | 23.2357 | 31.6446 | 31.9841 | 23.3533 | 31.6455 | 31.985 | 23.354 | 31.3995 | 31.7376 | 23.2474 | 31.7004 | 32.0415 | 23.3816
SW | F7164 | Power Factor | 0.98801 | 0.98795 | 0.94938 | 0.98897 | 0.98873 | 0.95039 | 0.98897 | 0.98873 | 0.95038 | 0.98827 | 0.98808 | 0.94962 | 0.98913 | 0.9889 | 0.95059
SW | F7164 | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | F7164 | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F7164 | Min Voltage at Constrained Conductor (pu) | 1.021 | 1.0204 | 1.0386 | 1.0197 | 1.0193 | 1.0382 | 1.0196 | 1.0192 | 1.0381 | 1.0206 | 1.0202 | 1.0387 | 1.0193 | 1.0189 | 1.0379
SW | F7164 | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F7174 | % of Rated A | 76.53% | 48.21% | 36.63% | 77.21% | 48.59% | 36.78% | 77.22% | 48.59% | 36.79% | 76.64% | 48.23% | 36.63% | 77.36% | 48.68% | 36.82%
SW | F7174 | Limiting Line Name | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1)
SW | F7174 | Loading (A) | 132.4038 | 134.0209 | 101.8257 | 133.5708 | 135.0771 | 102.2449 | 133.5872 | 135.0934 | 102.2646 | 132.5811 | 134.0716 | 101.8306 | 133.827 | 135.3352 | 102.3711
SW | F7174 | Loading (MVA) | 31.7512 | 32.1267 | 24.485 | 32.012 | 32.3632 | 24.5829 | 32.0128 | 32.3641 | 24.5838 | 31.7865 | 32.135 | 24.4911 | 32.0633 | 32.4159 | 24.6076
SW | F7174 | Loading (MW) | 31.3709 | 31.7398 | 23.2465 | 31.6592 | 31.9989 | 23.3641 | 31.6601 | 31.9998 | 23.3648 | 31.414 | 31.7523 | 23.2581 | 31.7151 | 32.0563 | 23.3924
SW | F7174 | Power Factor | 0.98802 | 0.98796 | 0.94942 | 0.98898 | 0.98874 | 0.95042 | 0.98898 | 0.98875 | 0.95042 | 0.98828 | 0.98809 | 0.94966 | 0.98914 | 0.98891 | 0.95062
SW | F7174 | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | F7174 | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F7174 | Min Voltage at Constrained Conductor (pu) | 1.021 | 1.0204 | 1.0386 | 1.0197 | 1.0193 | 1.0382 | 1.0196 | 1.0192 | 1.0381 | 1.0206 | 1.0202 | 1.0387 | 1.0193 | 1.0189 | 1.0379
SW | F7174 | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F7490 | % of Rated A | 34.35% | 34.77% | 26.99% | 34.63% | 35.02% | 27.09% | 34.64% | 35.03% | 27.1% | 34.39% | 34.78% | 26.99% | 34.7% | 35.08% | 27.12%
SW | F7490 | Limiting Line Name | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b
SW | F7490 | Loading (A) | 134.3251 | 135.9393 | 105.5448 | 135.4211 | 136.9373 | 105.9301 | 135.437 | 136.9531 | 105.9491 | 134.4837 | 135.9806 | 105.5431 | 135.6643 | 137.1822 | 106.0484
SW | F7490 | Loading (MVA) | 32.518 | 32.9003 | 25.4444 | 32.7742 | 33.1338 | 25.537 | 32.775 | 33.1346 | 25.5375 | 32.5514 | 32.9075 | 25.4496 | 32.8248 | 33.1858 | 25.5602
SW | F7490 | Loading (MW) | 31.8747 | 32.2558 | 23.5524 | 32.1715 | 32.5226 | 23.6723 | 32.1726 | 32.5237 | 23.6732 | 31.9191 | 32.2686 | 23.5641 | 32.2293 | 32.582 | 23.7014
SW | F7490 | Power Factor | 0.98022 | 0.98041 | 0.92564 | 0.98161 | 0.98156 | 0.92698 | 0.98162 | 0.98157 | 0.927 | 0.98058 | 0.98058 | 0.92591 | 0.98186 | 0.98181 | 0.92728
SW | F7490 | Rating (A) | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SW | F7490 | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F7490 | Min Voltage at Constrained Conductor (pu) | 1.0489 | 1.0485 | 1.0517 | 1.0483 | 1.0479 | 1.0516 | 1.0482 | 1.0478 | 1.0515 | 1.0486 | 1.0484 | 1.052 | 1.0479 | 1.0476 | 1.0514
SW | F7490 | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F7491 | % of Rated A | 34.31% | 34.73% | 26.96% | 34.59% | 34.98% | 27.06% | 34.6% | 34.98% | 27.07% | 34.35% | 34.74% | 26.96% | 34.66% | 35.04% | 27.09%
SW | F7491 | Limiting Line Name | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1
SW | F7491 | Loading (A) | 134.1651 | 135.7772 | 105.4219 | 135.2597 | 136.774 | 105.8067 | 135.2755 | 136.7898 | 105.8256 | 134.3235 | 135.8186 | 105.4202 | 135.5025 | 137.0186 | 105.9248
SW | F7491 | Loading (MVA) | 32.4792 | 32.8611 | 25.4148 | 32.7351 | 33.0942 | 25.5072 | 32.7359 | 33.095 | 25.5078 | 32.5126 | 32.8683 | 25.42 | 32.7856 | 33.1462 | 25.5304
SW | F7491 | Loading (MW) | 31.8361 | 32.2168 | 23.5239 | 32.1326 | 32.4833 | 23.6437 | 32.1336 | 32.4844 | 23.6445 | 31.8805 | 32.2296 | 23.5355 | 32.1903 | 32.5426 | 23.6727
SW | F7491 | Power Factor | 0.9802 | 0.98039 | 0.9256 | 0.98159 | 0.98154 | 0.92694 | 0.9816 | 0.98155 | 0.92695 | 0.98056 | 0.98057 | 0.92587 | 0.98184 | 0.98179 | 0.92724
SW | F7491 | Rating (A) | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SW | F7491 | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F7491 | Min Voltage at Constrained Conductor (pu) | 1.0489 | 1.0485 | 1.0517 | 1.0483 | 1.0479 | 1.0516 | 1.0482 | 1.0478 | 1.0515 | 1.0486 | 1.0484 | 1.052 | 1.0479 | 1.0476 | 1.0514
SW | F7491 | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | 3153_Cecil Plains Road 33 kV | % of Rated A | 53.76% | 42.91% | 44.36% | 53.76% | 42.9% | 44.67% | 53.77% | 42.91% | 44.42% | 53.72% | 43.02% | 44.64% | 53.78% | 42.92% | 44.42%
SW | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2
SW | 3153_Cecil Plains Road 33 kV | Loading (A) | 50.0011 | 51.9251 | 51.4622 | 49.9982 | 51.9143 | 51.8131 | 50.0073 | 51.9193 | 51.5217 | 49.9568 | 52.0582 | 51.7799 | 50.0164 | 51.9388 | 51.5321
SW | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 2.8753 | 2.9943 | 2.9845 | 2.8752 | 2.9943 | 2.9857 | 2.8753 | 2.9943 | 2.9847 | 2.8751 | 2.9948 | 2.9856 | 2.8753 | 2.9944 | 2.9847
SW | 3153_Cecil Plains Road 33 kV | Loading (MW) | 2.7664 | 2.8891 | 2.8916 | 2.7664 | 2.8891 | 2.8917 | 2.7664 | 2.8891 | 2.8916 | 2.7663 | 2.8892 | 2.8917 | 2.7664 | 2.8891 | 2.8916
SW | 3153_Cecil Plains Road 33 kV | Power Factor | 0.96213 | 0.96485 | 0.96888 | 0.96213 | 0.96486 | 0.96852 | 0.96212 | 0.96486 | 0.96881 | 0.96218 | 0.96471 | 0.96855 | 0.96211 | 0.96484 | 0.9688
SW | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116
SW | 3153_Cecil Plains Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 3153_Cecil Plains Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.006 | 1.0088 | 1.0146 | 1.006 | 1.009 | 1.0081 | 1.0059 | 1.0089 | 1.0135 | 1.0068 | 1.0064 | 1.0087 | 1.0057 | 1.0086 | 1.0133
SW | 3153_Cecil Plains Road 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV
SW | 3154_Central Dalby 1 33 kV | % of Rated A | 60.84% | 55.03% | 28.07% | 60.4% | 54.61% | 28.08% | 60.17% | 54.39% | 27.83% | 59.28% | 53.59% | 27.57% | 60.39% | 54.62% | 27.92%
SW | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1
SW | 3154_Central Dalby 1 33 kV | Loading (A) | 278.0487 | 256.9898 | 115.0981 | 276.0244 | 255.0363 | 115.1203 | 274.987 | 253.994 | 114.0943 | 270.9218 | 250.2698 | 113.0302 | 275.9769 | 255.0591 | 114.4697
SW | 3154_Central Dalby 1 33 kV | Loading (MVA) | 15.6263 | 14.5161 | 6.7136 | 15.5166 | 14.4093 | 6.6691 | 15.4574 | 14.3504 | 6.6441 | 15.2495 | 14.1571 | 6.5513 | 15.5039 | 14.4039 | 6.6648
SW | 3154_Central Dalby 1 33 kV | Loading (MW) | 15.1275 | 14.0558 | 6.583 | 15.0234 | 13.9543 | 6.5382 | 14.9677 | 13.8989 | 6.5149 | 14.7746 | 13.7134 | 6.4257 | 15.0118 | 13.9498 | 6.5351
SW | 3154_Central Dalby 1 33 kV | Power Factor | 0.96808 | 0.96829 | 0.98055 | 0.96822 | 0.96843 | 0.98037 | 0.96832 | 0.96854 | 0.98056 | 0.96886 | 0.96866 | 0.98083 | 0.96826 | 0.96847 | 0.98054
SW | 3154_Central Dalby 1 33 kV | Rating (A) | 457 | 467 | 410 | 457 | 467 | 410 | 457 | 467 | 410 | 457 | 467 | 410 | 457 | 467 | 410
SW | 3154_Central Dalby 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 3154_Central Dalby 1 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98318 | 0.98818 | 1.0205 | 0.98344 | 0.98842 | 1.0135 | 0.98338 | 0.98842 | 1.0188 | 0.98471 | 0.98962 | 1.014 | 0.9828 | 0.98797 | 1.0186
SW | 3154_Central Dalby 1 33 kV | Contingency Outage | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV
SW | 3178_Wilkie Creek 33 kV | % of Rated A | 3.696% | 2.791% | 2.955% | 3.696% | 2.791% | 2.941% | 3.695% | 2.82% | 2.955% | 3.697% | 2.793% | 2.941% | 3.694% | 2.82% | 2.955%
SW | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1
SW | 3178_Wilkie Creek 33 kV | Loading (A) | 3.9174 | 3.8518 | 3.9299 | 3.918 | 3.8522 | 3.9111 | 3.9171 | 3.892 | 3.9306 | 3.9185 | 3.8537 | 3.9119 | 3.9151 | 3.8916 | 3.9297
SW | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.22674 | 0.2208 | 0.22743 | 0.22681 | 0.22085 | 0.22527 | 0.22671 | 0.22536 | 0.2275 | 0.22687 | 0.22103 | 0.22536 | 0.22648 | 0.22531 | 0.2274
SW | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0097368 | 0.015359 | 0.0071396 | 0.0097373 | 0.015359 | 0.0071245 | 0.0097366 | 0.01539 | 0.0071401 | 0.0097377 | 0.01536 | 0.0071252 | 0.009735 | 0.01539 | 0.0071394
SW | 3178_Wilkie Creek 33 kV | Power Factor | 0.042942 | 0.069558 | 0.031393 | 0.042932 | 0.069545 | 0.031626 | 0.042948 | 0.068293 | 0.031385 | 0.042923 | 0.069496 | 0.031616 | 0.042984 | 0.068305 | 0.031396
SW | 3178_Wilkie Creek 33 kV | Rating (A) | 106 | 138 | 133 | 106 | 138 | 133 | 106 | 138 | 133 | 106 | 138 | 133 | 106 | 138 | 133
SW | 3178_Wilkie Creek 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 3178_Wilkie Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0126 | 1.0029 | 1.0125 | 1.0128 | 1.003 | 1.0077 | 1.0126 | 1.0131 | 1.0126 | 1.0129 | 1.0034 | 1.0079 | 1.0121 | 1.013 | 1.0124
SW | 3178_Wilkie Creek 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F097D_Jandowae 33 kV | F099D_Warra 33 kV | F069C_Brigalow 33 kV | F097D_Jandowae 33 kV | 3153_Cecil Plains Road 33 kV | F069C_Brigalow 33 kV | 3900_Peranga 33 kV | 3153_Cecil Plains Road 33 kV | F095D_Kaimkillenbun 33 kV | F097D_Jandowae 33 kV | 3153_Cecil Plains Road 33 kV | F069C_Brigalow 33 kV | F3910_Perseverence Creek 1 33 kV | 3153_Cecil Plains Road 33 kV
SW | 3900_Peranga 33 kV | % of Rated A | 20.85% | 14.92% | 11.53% | 19.66% | 14.07% | 10.78% | 19.66% | 14.07% | 10.87% | 19.66% | 14.07% | 10.74% | 20.87% | 14.93% | 11.53%
SW | 3900_Peranga 33 kV | Limiting Line Name | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1 | TR_LINE 24117_1
SW | 3900_Peranga 33 kV | Loading (A) | 26.4832 | 26.8601 | 20.1797 | 24.9657 | 25.3198 | 18.866 | 24.9731 | 25.3263 | 19.0198 | 24.9695 | 25.3202 | 18.8014 | 26.5055 | 26.8782 | 20.1702
SW | 3900_Peranga 33 kV | Loading (MVA) | 1.5139 | 1.5346 | 1.1518 | 1.429 | 1.4486 | 1.0874 | 1.429 | 1.4486 | 1.0875 | 1.429 | 1.4486 | 1.0874 | 1.5139 | 1.5347 | 1.1518
SW | 3900_Peranga 33 kV | Loading (MW) | 1.4084 | 1.4276 | 1.0726 | 1.3298 | 1.3479 | 1.0128 | 1.3298 | 1.3479 | 1.0128 | 1.3298 | 1.3479 | 1.0127 | 1.4084 | 1.4276 | 1.0726
SW | 3900_Peranga 33 kV | Power Factor | 0.92662 | 0.92651 | 0.92843 | 0.92707 | 0.92697 | 0.92874 | 0.92707 | 0.92696 | 0.92871 | 0.92707 | 0.92696 | 0.92878 | 0.92661 | 0.9265 | 0.92844
SW | 3900_Peranga 33 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 3900_Peranga 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 3900_Peranga 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0001 | 0.9996 | 0.99861 | 1.0014 | 1.0009 | 1.0084 | 1.0011 | 1.0007 | 1.0003 | 1.0013 | 1.0009 | 1.0118 | 0.99929 | 0.99894 | 0.99908
SW | 3900_Peranga 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 48.05% | 48.41% | 28.45% | 51.13% | 51.19% | 29.73% | 54.32% | 54% | 30.89% | 54.48% | 53.04% | 30.79% | 55.7% | 54.32% | 31.13%
SW | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 421.855 | 466.6923 | 242.9947 | 448.9308 | 493.4555 | 253.9328 | 476.973 | 520.6013 | 263.8347 | 478.3571 | 511.2783 | 262.9076 | 489.0743 | 523.6344 | 265.8858
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 83.5782 | 92.1902 | 48.239 | 88.7799 | 97.2919 | 50.5707 | 94.1568 | 102.4652 | 52.9816 | 94.4381 | 100.7164 | 52.3384 | 96.4675 | 103.0448 | 53.3868
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 80.4163 | 88.0439 | 47.7216 | 84.7545 | 92.1837 | 49.8925 | 89.3105 | 96.5174 | 52.1717 | 89.6039 | 95.1497 | 51.5548 | 91.3641 | 97.1228 | 52.5612
SW | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.96217 | 0.95502 | 0.98927 | 0.95466 | 0.9475 | 0.98659 | 0.94853 | 0.94195 | 0.98471 | 0.94881 | 0.94473 | 0.98503 | 0.9471 | 0.94253 | 0.98454
SW | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 7233_Middle Ridge-Torrington 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 7233_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0312 | 1.0267 | 1.0387 | 1.0283 | 1.0236 | 1.0417 | 1.0253 | 1.0208 | 1.0501 | 1.0254 | 1.022 | 1.041 | 1.0241 | 1.0205 | 1.0499
SW | 7233_Middle Ridge-Torrington 110 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 47.94% | 48.27% | 28.44% | 51.04% | 51.01% | 29.71% | 54.15% | 53.8% | 30.87% | 54.31% | 52.9% | 30.76% | 55.53% | 54.13% | 31.11%
SW | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 420.9158 | 465.3157 | 242.8497 | 448.1512 | 491.7694 | 253.7558 | 475.4701 | 518.6373 | 263.6394 | 476.8498 | 509.9745 | 262.7066 | 487.5621 | 521.8445 | 265.714
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 83.4149 | 91.9509 | 48.215 | 88.6461 | 96.9985 | 50.5408 | 93.8943 | 102.1239 | 52.9483 | 94.1751 | 100.4923 | 52.3042 | 96.2037 | 102.734 | 53.3577
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 80.4084 | 88.0264 | 47.7227 | 84.7666 | 92.1625 | 49.8936 | 89.2931 | 96.4905 | 52.1742 | 89.5865 | 95.1539 | 51.5559 | 91.3438 | 97.0968 | 52.565
SW | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.96396 | 0.95732 | 0.98979 | 0.95624 | 0.95014 | 0.98719 | 0.951 | 0.94484 | 0.98538 | 0.95128 | 0.94688 | 0.98569 | 0.94948 | 0.94513 | 0.98514
SW | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 7234_Middle Ridge-Torrington 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 7234_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0317 | 1.0272 | 1.0388 | 1.0286 | 1.0242 | 1.0418 | 1.0259 | 1.0215 | 1.0503 | 1.026 | 1.0226 | 1.0412 | 1.0247 | 1.0212 | 1.0501
SW | 7234_Middle Ridge-Torrington 110 kV | Contingency Outage | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV
SW | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 47.35% | 44.47% | 28.32% | 47.38% | 44.51% | 28.28% | 47.48% | 44.62% | 28.07% | 47.43% | 44.59% | 28.26% | 47.96% | 44.92% | 28.24%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 487.2398 | 472.2888 | 269.8869 | 487.5207 | 472.7361 | 269.4848 | 488.5853 | 473.82 | 267.4632 | 488.0192 | 473.5454 | 269.3194 | 493.552 | 477.0141 | 269.1621
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 97.518 | 94.3957 | 53.8475 | 97.511 | 94.4244 | 53.9613 | 97.6652 | 94.5916 | 54.0193 | 97.5636 | 94.5713 | 53.9231 | 98.6173 | 95.2119 | 54.3583
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 97.1149 | 93.9576 | 47.7285 | 97.1129 | 93.996 | 47.7084 | 97.2794 | 94.1602 | 47.7495 | 97.1738 | 94.1377 | 47.6731 | 98.2641 | 94.7882 | 48.1131
SW | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.99554 | 0.99503 | 0.88597 | 0.99559 | 0.99513 | 0.88373 | 0.99573 | 0.99511 | 0.88355 | 0.99568 | 0.99508 | 0.8837 | 0.99611 | 0.99522 | 0.88472
SW | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 728_Middle Ridge-South Toowoomba 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 728_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0501 | 1.0487 | 1.047 | 1.0495 | 1.048 | 1.0508 | 1.0488 | 1.0475 | 1.0599 | 1.0489 | 1.0479 | 1.0507 | 1.0484 | 1.0473 | 1.0598
SW | 728_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 47.35% | 44.47% | 28.32% | 47.38% | 44.52% | 28.28% | 47.48% | 44.62% | 28.07% | 47.43% | 44.59% | 28.26% | 47.97% | 44.92% | 28.24%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 487.251 | 472.303 | 269.8939 | 487.5319 | 472.7504 | 269.4917 | 488.5967 | 473.8342 | 267.4702 | 488.0308 | 473.5598 | 269.3266 | 493.564 | 477.0293 | 269.1695
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 97.5205 | 94.3989 | 53.8489 | 97.5136 | 94.4276 | 53.9628 | 97.6678 | 94.5947 | 54.0208 | 97.5662 | 94.5746 | 53.9246 | 98.62 | 95.2153 | 54.3599
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 97.1162 | 93.9592 | 47.7287 | 97.1142 | 93.9976 | 47.7086 | 97.2807 | 94.1618 | 47.7498 | 97.1751 | 94.1393 | 47.6734 | 98.2655 | 94.7899 | 48.1133
SW | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.99553 | 0.99501 | 0.88595 | 0.99558 | 0.99512 | 0.88371 | 0.99571 | 0.99509 | 0.88352 | 0.99567 | 0.99506 | 0.88368 | 0.99609 | 0.9952 | 0.8847
SW | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 730_Middle Ridge-South Toowoomba 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 730_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0501 | 1.0487 | 1.047 | 1.0495 | 1.048 | 1.0508 | 1.0488 | 1.0475 | 1.0599 | 1.0489 | 1.0479 | 1.0507 | 1.0484 | 1.0473 | 1.0598
SW | 730_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW | 7314_Dalby East 110 kV | % of Rated A | 4.675% | 4.399% | 4.939% | 4.749% | 4.47% | 4.972% | 4.748% | 4.502% | 4.997% | 4.749% | 4.472% | 4.973% | 4.673% | 4.43% | 4.956%
SW | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW | 7314_Dalby East 110 kV | Loading (A) | 12.9502 | 12.9766 | 12.9898 | 13.1538 | 13.1872 | 13.0751 | 13.1511 | 13.2804 | 13.141 | 13.1553 | 13.1918 | 13.0778 | 12.9432 | 13.0688 | 13.0331
SW | 7314_Dalby East 110 kV | Loading (MVA) | 2.5239 | 2.5418 | 2.5648 | 2.5634 | 2.5827 | 2.6065 | 2.5623 | 2.5887 | 2.6325 | 2.564 | 2.5846 | 2.6076 | 2.5211 | 2.5478 | 2.6106
SW | 7314_Dalby East 110 kV | Loading (MW) | 1.0298 | 1.0674 | 0.5748 | 1.0369 | 1.0749 | 0.57844 | 1.0369 | 1.0748 | 0.57859 | 1.0369 | 1.0749 | 0.57845 | 1.0298 | 1.0673 | 0.57479
SW | 7314_Dalby East 110 kV | Power Factor | 0.40801 | 0.41995 | 0.22411 | 0.40452 | 0.41619 | 0.22192 | 0.40469 | 0.41517 | 0.21979 | 0.40442 | 0.41588 | 0.22183 | 0.40847 | 0.41889 | 0.22018
SW | 7314_Dalby East 110 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
SW | 7314_Dalby East 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 7314_Dalby East 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0229 | 1.0281 | 1.0363 | 1.0228 | 1.028 | 1.0463 | 1.0226 | 1.0231 | 1.0514 | 1.023 | 1.0284 | 1.0465 | 1.0223 | 1.0232 | 1.0513
SW | 7314_Dalby East 110 kV | Contingency Outage | F069C_Brigalow 33 kV | F097D_Jandowae 33 kV | F099D_Warra 33 kV | F069C_Brigalow 33 kV | F097D_Jandowae 33 kV | 3153_Cecil Plains Road 33 kV | F069C_Brigalow 33 kV | 3900_Peranga 33 kV | 3153_Cecil Plains Road 33 kV | F095D_Kaimkillenbun 33 kV | F097D_Jandowae 33 kV | 3153_Cecil Plains Road 33 kV | F069C_Brigalow 33 kV | F3910_Perseverence Creek 1 33 kV | 3153_Cecil Plains Road 33 kV
SW | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 26.62% | 30.37% | 21.94% | 26.63% | 30.39% | 21.91% | 26.64% | 30.4% | 21.85% | 26.62% | 30.34% | 21.91% | 27.22% | 31.14% | 22.15%
SW | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1
SW | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 63.6189 | 76.2281 | 48.6999 | 63.6449 | 76.2687 | 48.6471 | 63.6672 | 76.299 | 48.5093 | 63.6284 | 76.165 | 48.6413 | 65.0646 | 78.1724 | 49.1723
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 11.7954 | 13.87 | 9.5247 | 11.7942 | 13.8699 | 9.5519 | 11.7932 | 13.8698 | 9.6218 | 11.7949 | 13.8702 | 9.555 | 12.0177 | 14.1712 | 9.7421
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 11.5461 | 13.8099 | 8.4572 | 11.5465 | 13.8106 | 8.4561 | 11.5469 | 13.8112 | 8.4536 | 11.5463 | 13.8088 | 8.456 | 11.8085 | 14.1228 | 8.6412
SW | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.97887 | 0.99567 | 0.88793 | 0.979 | 0.99573 | 0.88528 | 0.97912 | 0.99577 | 0.87859 | 0.97892 | 0.99557 | 0.88498 | 0.98259 | 0.99658 | 0.88699
SW | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 239 | 251 | 222 | 239 | 251 | 222 | 239 | 251 | 222 | 239 | 251 | 222 | 239 | 251 | 222
SW | 790_Warwick-Stanthorpe 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | 790_Warwick-Stanthorpe 110 kV | Min Voltage at Constrained Conductor (pu) | 0.97309 | 0.95495 | 1.0265 | 0.9726 | 0.95443 | 1.0306 | 0.97217 | 0.95405 | 1.0411 | 0.97291 | 0.95575 | 1.031 | 0.9694 | 0.95142 | 1.0399
SW | 790_Warwick-Stanthorpe 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | EB10_Acland 33 kV | % of Rated A | 3.703% | 2.758% | 2.474% | 3.703% | 2.759% | 2.452% | 3.705% | 2.76% | 2.473% | 3.704% | 2.759% | 2.443% | 3.706% | 2.76% | 2.473%
SW | EB10_Acland 33 kV | Limiting Line Name | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1
SW | EB10_Acland 33 kV | Loading (A) | 8.2569 | 6.0406 | 4.6271 | 8.2588 | 6.0418 | 4.5852 | 8.2614 | 6.0434 | 4.6243 | 8.2601 | 6.0419 | 4.5689 | 8.2643 | 6.0448 | 4.6248
SW | EB10_Acland 33 kV | Loading (MVA) | 0.48197 | 0.35291 | 0.2685 | 0.48198 | 0.35292 | 0.26831 | 0.482 | 0.35293 | 0.26849 | 0.48199 | 0.35292 | 0.26823 | 0.48202 | 0.35293 | 0.26849
SW | EB10_Acland 33 kV | Loading (MW) | 0.40373 | 0.2991 | 0.22962 | 0.40373 | 0.2991 | 0.22959 | 0.40374 | 0.2991 | 0.22961 | 0.40373 | 0.2991 | 0.22958 | 0.40374 | 0.2991 | 0.22961
SW | EB10_Acland 33 kV | Power Factor | 0.83761 | 0.84747 | 0.85514 | 0.8376 | 0.84746 | 0.85566 | 0.83758 | 0.84745 | 0.85518 | 0.83759 | 0.84746 | 0.85586 | 0.83755 | 0.84743 | 0.85517
SW | EB10_Acland 33 kV | Rating (A) | 223 | 219 | 187 | 223 | 219 | 187 | 223 | 219 | 187 | 223 | 219 | 187 | 223 | 219 | 187
SW | EB10_Acland 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | EB10_Acland 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0212 | 1.0221 | 1.0152 | 1.021 | 1.022 | 1.0238 | 1.0208 | 1.0217 | 1.0158 | 1.0209 | 1.0219 | 1.0271 | 1.0204 | 1.0215 | 1.0157
SW | EB10_Acland 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F008D_Central Dalby 2 33 kV | % of Rated A | 53.27% | 48.11% | 24.53% | 52.88% | 47.75% | 24.53% | 52.69% | 47.55% | 24.31% | 51.91% | 46.82% | 24.09% | 52.87% | 47.75% | 24.39%
SW | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1
SW | F008D_Central Dalby 2 33 kV | Loading (A) | 283.9354 | 262.6822 | 117.7231 | 281.8747 | 260.6883 | 117.7449 | 280.8187 | 259.6239 | 116.6972 | 276.678 | 255.6355 | 115.6094 | 281.8234 | 260.7174 | 117.0861
SW | F008D_Central Dalby 2 33 kV | Loading (MVA) | 16.3292 | 15.1522 | 6.9214 | 16.2118 | 15.0381 | 6.8759 | 16.1485 | 14.9752 | 6.8493 | 15.9251 | 14.7595 | 6.7534 | 16.1985 | 15.0329 | 6.8712
SW | F008D_Central Dalby 2 33 kV | Loading (MW) | 15.5173 | 14.4044 | 6.7166 | 15.4094 | 14.2995 | 6.6708 | 15.3519 | 14.2423 | 6.6469 | 15.152 | 14.0489 | 6.5561 | 15.3977 | 14.2951 | 6.6676
SW | F008D_Central Dalby 2 33 kV | Power Factor | 0.95028 | 0.95065 | 0.97041 | 0.95051 | 0.95089 | 0.97017 | 0.95067 | 0.95106 | 0.97045 | 0.95145 | 0.95185 | 0.97079 | 0.95056 | 0.95092 | 0.97038
SW | F008D_Central Dalby 2 33 kV | Rating (A) | 533 | 546 | 480 | 533 | 546 | 480 | 533 | 546 | 480 | 533 | 546 | 480 | 533 | 546 | 480
SW | F008D_Central Dalby 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F008D_Central Dalby 2 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98583 | 0.99044 | 1.0215 | 0.98607 | 0.99066 | 1.0146 | 0.986 | 0.99065 | 1.0198 | 0.9873 | 0.99199 | 1.0151 | 0.98544 | 0.9902 | 1.0197
SW | F008D_Central Dalby 2 33 kV | Contingency Outage | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV
SW | F019D_West Dalby No 1 33 kV | % of Rated A | 63.3% | 51.06% | 28.8% | 62.81% | 50.66% | 28.79% | 62.82% | 50.49% | 28.63% | 61.88% | 49.74% | 28.33% | 63.31% | 50.75% | 28.84%
SW | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1
SW | F019D_West Dalby No 1 33 kV | Loading (A) | 237.3902 | 208.8418 | 105.9867 | 235.524 | 207.2068 | 105.9567 | 235.5641 | 206.5022 | 105.3704 | 232.0659 | 203.4325 | 104.2548 | 237.3941 | 207.5783 | 106.1273
SW | F019D_West Dalby No 1 33 kV | Loading (MVA) | 13.5901 | 11.9879 | 6.2222 | 13.4847 | 11.8954 | 6.1782 | 13.4848 | 11.854 | 6.1754 | 13.2979 | 11.6888 | 6.0812 | 13.5822 | 11.9111 | 6.2188
SW | F019D_West Dalby No 1 33 kV | Loading (MW) | 12.9585 | 11.3576 | 6.0214 | 12.8596 | 11.2725 | 5.9764 | 12.8596 | 11.2346 | 5.9758 | 12.6938 | 11.0825 | 5.8885 | 12.9498 | 11.2865 | 6.0169
SW | F019D_West Dalby No 1 33 kV | Power Factor | 0.95352 | 0.94742 | 0.96773 | 0.95364 | 0.94764 | 0.96732 | 0.95364 | 0.94775 | 0.96768 | 0.95457 | 0.94813 | 0.96831 | 0.95344 | 0.94756 | 0.96754
SW | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368
SW | F019D_West Dalby No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F019D_West Dalby No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99669 | 0.99992 | 1.0252 | 0.99684 | 1.0001 | 1.0182 | 0.99667 | 1 | 1.0235 | 0.99777 | 1.001 | 1.0187 | 0.99609 | 0.99959 | 1.0233
SW | F019D_West Dalby No 1 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV
SW | F039D_West Dalby No 2 33 kV | % of Rated A | 71.2% | 59.98% | 37.4% | 70.64% | 59.45% | 37.39% | 70.65% | 59.45% | 37.19% | 69.59% | 58.47% | 36.79% | 71.19% | 60.06% | 37.45%
SW | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2
SW | F039D_West Dalby No 2 33 kV | Loading (A) | 238.5306 | 199.1428 | 106.2222 | 236.644 | 197.3683 | 106.186 | 236.6654 | 197.3734 | 105.6057 | 233.1374 | 194.1284 | 104.4888 | 238.4898 | 199.4027 | 106.3606
SW | F039D_West Dalby No 2 33 kV | Loading (MVA) | 13.4013 | 11.25 | 6.194 | 13.2989 | 11.1525 | 6.1496 | 13.2989 | 11.1525 | 6.1478 | 13.1185 | 10.9844 | 6.0544 | 13.3932 | 11.2616 | 6.1906
SW | F039D_West Dalby No 2 33 kV | Loading (MW) | 12.8417 | 10.7851 | 5.9977 | 12.7446 | 10.6925 | 5.9527 | 12.7446 | 10.6925 | 5.9524 | 12.5821 | 10.5405 | 5.8656 | 12.833 | 10.7947 | 5.9932
SW | F039D_West Dalby No 2 33 kV | Power Factor | 0.95824 | 0.95867 | 0.96831 | 0.95832 | 0.95875 | 0.96799 | 0.95832 | 0.95875 | 0.96822 | 0.95911 | 0.95958 | 0.96882 | 0.95818 | 0.95853 | 0.9681
SW | F039D_West Dalby No 2 33 kV | Rating (A) | 335 | 332 | 284 | 335 | 332 | 284 | 335 | 332 | 284 | 335 | 332 | 284 | 335 | 332 | 284
SW | F039D_West Dalby No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F039D_West Dalby No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98011 | 0.98601 | 1.019 | 0.9804 | 0.98628 | 1.0121 | 0.98031 | 0.98625 | 1.0173 | 0.9817 | 0.98767 | 1.0126 | 0.97968 | 0.98574 | 1.0171
SW | F039D_West Dalby No 2 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV
SW | F095D_Kaimkillenbun 33 kV | % of Rated A | 23.91% | 20.71% | 13.05% | 23.91% | 20.71% | 13.13% | 23.92% | 20.71% | 13.06% | 23.89% | 20.77% | 13.12% | 23.92% | 20.72% | 13.06%
SW | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_LINE 23016_1 | TR_LINE 23016_1 | TR_LINE 81370_2 | TR_LINE 23016_1 | TR_LINE 23016_1 | TR_LINE 81370_2 | TR_LINE 23016_1 | TR_LINE 23016_1 | TR_LINE 81370_2 | TR_LINE 23016_1 | TR_LINE 23016_1 | TR_LINE 81370_2 | TR_LINE 23016_1 | TR_LINE 23016_1 | TR_LINE 81370_2
SW | F095D_Kaimkillenbun 33 kV | Loading (A) | 22.2395 | 25.063 | 15.1328 | 22.2382 | 25.0577 | 15.2285 | 22.2422 | 25.0602 | 15.149 | 22.2199 | 25.1281 | 15.2194 | 22.2463 | 25.0697 | 15.1516
SW | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 1.2762 | 1.4419 | 0.87763 | 1.2762 | 1.4418 | 0.87756 | 1.2762 | 1.4418 | 0.87761 | 1.2761 | 1.4421 | 0.87757 | 1.2762 | 1.4419 | 0.8776
SW | F095D_Kaimkillenbun 33 kV | Loading (MW) | 1.2748 | 1.4389 | 0.87539 | 1.2748 | 1.4389 | 0.87556 | 1.2748 | 1.4389 | 0.87542 | 1.2747 | 1.4391 | 0.87554 | 1.2748 | 1.439 | 0.87541
SW | F095D_Kaimkillenbun 33 kV | Power Factor | 0.99874 | 0.9978 | 0.99745 | 0.99874 | 0.99781 | 0.99772 | 0.99874 | 0.9978 | 0.9975 | 0.99876 | 0.99773 | 0.99769 | 0.99874 | 0.99779 | 0.9975
SW | F095D_Kaimkillenbun 33 kV | Rating (A) | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116
SW | F095D_Kaimkillenbun 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F095D_Kaimkillenbun 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0029 | 1.0053 | 1.0146 | 1.0029 | 1.0055 | 1.0081 | 1.0028 | 1.0054 | 1.0135 | 1.0037 | 1.0029 | 1.0087 | 1.0026 | 1.005 | 1.0133
SW | F095D_Kaimkillenbun 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5545_7245 Tangkam-Dalby 110 kV
SW | F097D_Jandowae 33 kV | % of Rated A | 39.43% | 27.74% | 15.11% | 39.42% | 27.73% | 15.21% | 39.42% | 27.74% | 15.12% | 38.39% | 27.11% | 14.79% | 40.62% | 28.66% | 15.48%
SW | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3
SW | F097D_Jandowae 33 kV | Loading (A) | 56.3886 | 58.8153 | 31.5695 | 56.3699 | 58.7971 | 31.7932 | 56.3753 | 58.7987 | 31.6055 | 54.9047 | 57.4636 | 30.9157 | 58.0804 | 60.7538 | 32.3549
SW | F097D_Jandowae 33 kV | Loading (MVA) | 3.1498 | 3.3053 | 1.8152 | 3.1496 | 3.3052 | 1.8163 | 3.1497 | 3.3052 | 1.8153 | 3.0721 | 3.235 | 1.7676 | 3.2427 | 3.4131 | 1.858
SW | F097D_Jandowae 33 kV | Loading (MW) | 2.9889 | 3.1575 | 1.7486 | 2.9888 | 3.1575 | 1.7488 | 2.9888 | 3.1575 | 1.7486 | 2.9241 | 3.0984 | 1.7071 | 3.0764 | 3.2588 | 1.7893
SW | F097D_Jandowae 33 kV | Power Factor | 0.9488 | 0.95522 | 0.96255 | 0.94882 | 0.95524 | 0.96204 | 0.94881 | 0.95524 | 0.96247 | 0.95169 | 0.95769 | 0.96498 | 0.94864 | 0.95476 | 0.96226
SW | F097D_Jandowae 33 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
SW | F097D_Jandowae 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F097D_Jandowae 33 kV | Min Voltage at Constrained Conductor (pu) | 0.97558 | 0.9814 | 1.0058 | 0.97587 | 0.98167 | 0.9993 | 0.97579 | 0.98165 | 1.0047 | 0.97732 | 0.9832 | 1.0001 | 0.97502 | 0.98098 | 1.0044
SW | F097D_Jandowae 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV
SW | F099D_Warra 33 kV | % of Rated A | 44.93% | 22.19% | 16.86% | 44.91% | 22.18% | 16.97% | 44.92% | 22.18% | 16.88% | 44.85% | 22.15% | 16.96% | 44.95% | 22.19% | 16.88%
SW | F099D_Warra 33 kV | Limiting Line Name | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1
SW | F099D_Warra 33 kV | Loading (A) | 74.1284 | 39.2728 | 26.4719 | 74.1053 | 39.2612 | 26.6472 | 74.1119 | 39.2622 | 26.5017 | 74.0006 | 39.2051 | 26.6257 | 74.1627 | 39.2846 | 26.506
SW | F099D_Warra 33 kV | Loading (MVA) | 4.1485 | 2.2119 | 1.5248 | 4.1484 | 2.2118 | 1.525 | 4.1484 | 2.2118 | 1.5249 | 4.1481 | 2.2118 | 1.5249 | 4.1486 | 2.2119 | 1.5248
SW | F099D_Warra 33 kV | Loading (MW) | 4.0063 | 2.1256 | 1.4869 | 4.0063 | 2.1256 | 1.4869 | 4.0063 | 2.1256 | 1.4869 | 4.0062 | 2.1256 | 1.4869 | 4.0063 | 2.1256 | 1.4869
SW | F099D_Warra 33 kV | Power Factor | 0.96572 | 0.96094 | 0.97508 | 0.96574 | 0.96096 | 0.97491 | 0.96573 | 0.96096 | 0.97499 | 0.9658 | 0.96098 | 0.97497 | 0.9657 | 0.96092 | 0.97504
SW | F099D_Warra 33 kV | Rating (A) | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157
SW | F099D_Warra 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F099D_Warra 33 kV | Min Voltage at Constrained Conductor (pu) | 0.97846 | 0.98509 | 1.0076 | 0.97875 | 0.98536 | 1.0012 | 0.97866 | 0.98534 | 1.0066 | 0.98006 | 0.98676 | 1.0019 | 0.97803 | 0.98482 | 1.0063
SW | F099D_Warra 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F5545_7245 Tangkam-Dalby 110 kV
SW | F2060_Sladevale 1 33kV | % of Rated A | 13.68% | 15.75% | 9.582% | 13.69% | 15.76% | 9.555% | 13.7% | 15.77% | 9.563% | 13.69% | 15.73% | 9.445% | 14.02% | 16.16% | 9.718%
SW | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW | F2060_Sladevale 1 33kV | Loading (A) | 86.8886 | 100.0266 | 60.8437 | 86.9385 | 100.0932 | 60.6735 | 86.9804 | 100.1417 | 60.7227 | 86.9094 | 99.8899 | 59.9731 | 89.0341 | 102.6346 | 61.7114
SW | F2060_Sladevale 1 33kV | Loading (MVA) | 4.9438 | 5.7081 | 3.464 | 4.9442 | 5.7089 | 3.4664 | 4.9445 | 5.7094 | 3.4656 | 4.9439 | 5.7064 | 3.4778 | 5.0451 | 5.833 | 3.5226
SW | F2060_Sladevale 1 33kV | Loading (MW) | 4.9418 | 5.7047 | 3.3662 | 4.9423 | 5.7054 | 3.3652 | 4.9427 | 5.706 | 3.3657 | 4.942 | 5.7033 | 3.3599 | 5.0445 | 5.8267 | 3.4306
SW | F2060_Sladevale 1 33kV | Power Factor | 0.9996 | 0.99941 | 0.97177 | 0.99962 | 0.99939 | 0.97083 | 0.99963 | 0.99938 | 0.97116 | 0.99961 | 0.99945 | 0.9661 | 0.99989 | 0.9989 | 0.97387
SW | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | F2060_Sladevale 1 33kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2060_Sladevale 1 33kV | Min Voltage at Constrained Conductor (pu) | 0.99545 | 0.99839 | 0.99607 | 0.99496 | 0.99786 | 0.99954 | 0.99455 | 0.99748 | 0.99852 | 0.99524 | 0.99946 | 1.0145 | 0.99137 | 0.99431 | 0.99869
SW | F2060_Sladevale 1 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F2325_Broxburn 33 kV | % of Rated A | 64.97% | 59.98% | 39.71% | 64.65% | 59.71% | 39.43% | 64.71% | 59.75% | 39.02% | 63.86% | 58.96% | 39.01% | 65.51% | 60.44% | 39.43%
SW | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1
SW | F2325_Broxburn 33 kV | Loading (A) | 217.0118 | 202.1213 | 115.9585 | 215.9249 | 201.2244 | 115.1463 | 216.1349 | 201.3616 | 113.9519 | 213.3006 | 198.6846 | 113.923 | 218.8038 | 203.6856 | 115.145
SW | F2325_Broxburn 33 kV | Loading (MVA) | 10.8461 | 10.1305 | 6.3671 | 10.8212 | 10.1092 | 6.3611 | 10.8217 | 10.1095 | 6.3616 | 10.7172 | 10.0121 | 6.3014 | 10.9259 | 10.2062 | 6.4213
SW | F2325_Broxburn 33 kV | Loading (MW) | 10.0929 | 9.4447 | 5.9961 | 10.1881 | 9.5337 | 6.0527 | 10.1881 | 9.5337 | 6.0528 | 10.0937 | 9.4454 | 5.9967 | 10.2824 | 9.622 | 6.1088
SW | F2325_Broxburn 33 kV | Power Factor | 0.93055 | 0.9323 | 0.94172 | 0.94149 | 0.94308 | 0.95151 | 0.94144 | 0.94305 | 0.95146 | 0.94182 | 0.9434 | 0.95164 | 0.9411 | 0.94277 | 0.95133
SW | F2325_Broxburn 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | F2325_Broxburn 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2325_Broxburn 33 kV | Min Voltage at Constrained Conductor (pu) | 0.87418 | 0.87667 | 0.96053 | 0.87657 | 0.87873 | 0.9664 | 0.87576 | 0.87816 | 0.97661 | 0.87883 | 0.88142 | 0.96761 | 0.8734 | 0.87644 | 0.97556
SW | F2325_Broxburn 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F2450_Carrington Road 33 kV | % of Rated A | 26.41% | 31.73% | 17.95% | 26.52% | 31.84% | 18.02% | 26.95% | 32.39% | 18.28% | 26.49% | 31.84% | 17.91% | 27.42% | 32.92% | 18.58%
SW | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW | F2450_Carrington Road 33 kV | Loading (A) | 89.0057 | 106.937 | 60.4786 | 89.3748 | 107.3053 | 60.7214 | 90.8103 | 109.1391 | 61.5982 | 89.283 | 107.3019 | 60.3591 | 92.413 | 110.9237 | 62.6036
SW | F2450_Carrington Road 33 kV | Loading (MVA) | 5.1638 | 6.1822 | 3.5206 | 5.1627 | 6.1829 | 3.5208 | 5.2484 | 6.286 | 3.5795 | 5.1626 | 6.1805 | 3.5205 | 5.3343 | 6.3891 | 3.637
SW | F2450_Carrington Road 33 kV | Loading (MW) | 4.9988 | 5.9729 | 3.4199 | 4.9987 | 5.973 | 3.4199 | 5.0807 | 6.0711 | 3.476 | 4.9986 | 5.9726 | 3.4199 | 5.1628 | 6.1693 | 3.532
SW | F2450_Carrington Road 33 kV | Power Factor | 0.96798 | 0.96607 | 0.97132 | 0.96816 | 0.96598 | 0.97126 | 0.96799 | 0.96575 | 0.97101 | 0.96818 | 0.9663 | 0.97134 | 0.96779 | 0.96553 | 0.97107
SW | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337
SW | F2450_Carrington Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2450_Carrington Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.015 | 1.0114 | 1.0185 | 1.0106 | 1.0081 | 1.0144 | 1.0111 | 1.0077 | 1.0167 | 1.0116 | 1.0077 | 1.0204 | 1.0099 | 1.0077 | 1.0164
SW | F2450_Carrington Road 33 kV | Contingency Outage | F3820_Boundary Road 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7233_Middle Ridge-Torrington 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F3980_Purrawunda 33 kV
SW | F2460_Cecil Plains 33 kV | % of Rated A | 28.07% | 19.86% | 18.29% | 28.08% | 19.68% | 18.25% | 28.07% | 19.86% | 18.69% | 28.11% | 19.7% | 18.26% | 28.04% | 20.05% | 18.69%
SW | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW | F2460_Cecil Plains 33 kV | Loading (A) | 40.142 | 41.907 | 38.036 | 40.1573 | 41.5252 | 37.9699 | 40.1378 | 41.9044 | 38.881 | 40.1904 | 41.5632 | 37.9745 | 40.1019 | 42.3031 | 38.8759
SW | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.2162 | 2.3008 | 2.2949 | 2.2184 | 2.2815 | 2.2859 | 2.2156 | 2.3004 | 2.411 | 2.2232 | 2.2879 | 2.2865 | 2.2105 | 2.3222 | 2.4103
SW | F2460_Cecil Plains 33 kV | Loading (MW) | 1.087 | 1.2791 | 0.86808 | 1.087 | 1.2788 | 0.86803 | 1.087 | 1.2791 | 0.86874 | 1.087 | 1.2789 | 0.86804 | 1.087 | 1.2794 | 0.86874
SW | F2460_Cecil Plains 33 kV | Power Factor | 0.48855 | 0.55393 | 0.37722 | 0.48807 | 0.5587 | 0.37871 | 0.48869 | 0.55403 | 0.35912 | 0.48703 | 0.55715 | 0.3786 | 0.48983 | 0.54872 | 0.35923
SW | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
SW | F2460_Cecil Plains 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2460_Cecil Plains 33 kV | Min Voltage at Constrained Conductor (pu) | 0.96592 | 0.96054 | 1.0556 | 0.96652 | 0.96125 | 1.0533 | 0.96576 | 0.96042 | 1.0849 | 0.96779 | 0.96306 | 1.0534 | 0.96437 | 0.96042 | 1.0847
SW | F2460_Cecil Plains 33 kV | Contingency Outage | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2325_Broxburn 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F3867_Pampas 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F3867_Pampas 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F3867_Pampas 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F3867_Pampas 33 kV
SW | F2520_Clifton 33 kV | % of Rated A | 53.6% | 63.89% | 36.26% | 53.63% | 63.94% | 36.31% | 52.49% | 62.46% | 35.64% | 52.49% | 62.43% | 35.59% | 53.01% | 62.82% | 35.92%
SW | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1
SW | F2520_Clifton 33 kV | Loading (A) | 65.3894 | 77.9419 | 44.2314 | 65.4334 | 78.0057 | 44.2925 | 64.0431 | 76.2027 | 43.4865 | 64.0327 | 76.1657 | 43.4153 | 64.6726 | 76.6443 | 43.8163
SW | F2520_Clifton 33 kV | Loading (MVA) | 3.6733 | 4.2544 | 2.5697 | 3.6725 | 4.2539 | 2.5649 | 3.598 | 4.1634 | 2.5286 | 3.5982 | 4.1637 | 2.535 | 3.6715 | 4.2569 | 2.5615
SW | F2520_Clifton 33 kV | Loading (MW) | 3.539 | 4.1699 | 2.2694 | 3.539 | 4.17 | 2.2694 | 3.4562 | 4.0721 | 2.2165 | 3.4561 | 4.0721 | 2.2164 | 3.5385 | 4.1687 | 2.2692
SW | F2520_Clifton 33 kV | Power Factor | 0.9634 | 0.9801 | 0.88313 | 0.96361 | 0.98025 | 0.88478 | 0.96053 | 0.97804 | 0.87654 | 0.96048 | 0.97794 | 0.87433 | 0.96372 | 0.97926 | 0.88586
SW | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
SW | F2520_Clifton 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2520_Clifton 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98267 | 0.9548 | 1.0164 | 0.98181 | 0.95389 | 1.0131 | 0.98279 | 0.9557 | 1.0173 | 0.983 | 0.95625 | 1.0215 | 0.9931 | 0.97153 | 1.0227
SW | F2520_Clifton 33 kV | Contingency Outage | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 7449 South Toowoomba-TWCE 110 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 790_Warwick-Stanthorpe 110 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 7449 South Toowoomba-TWCE 110 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 7449 South Toowoomba-TWCE 110 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 7449 South Toowoomba-TWCE 110 kV
SW | F2777_East Stanthorpe 33 kV | % of Rated A | 146.7% | 111.1% | 77.1% | 148.2% | 112.2% | 77.89% | 149.7% | 113.3% | 78.66% | 151.2% | 114.4% | 79.45% | 152.7% | 115.6% | 80.25%
SW | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_2 | TR_LINE 140241_3 | TR_LINE 140241_4 | TR_LINE 140241_5 | TR_LINE 140241_6 | TR_LINE 140241_7 | TR_LINE 140241_8 | TR_LINE 140241_9 | TR_LINE 140241_10 | TR_LINE 140241_11 | TR_LINE 140241_12
SW | F2777_East Stanthorpe 33 kV | Loading (A) | 226 | 231 | 155 | 228.26 | 233.31 | 156.55 | 230.5426 | 235.6431 | 158.1155 | 232.848 | 237.9995 | 159.6967 | 235.1765 | 240.3795 | 161.2936
SW | F2777_East Stanthorpe 33 kV | Loading (MVA) | 13.2 | 13.5 | 9.2 | 13.2947 | 13.6022 | 9.3324 | 13.4276 | 13.7382 | 9.4257 | 13.5619 | 13.8756 | 9.52 | 13.6975 | 14.0143 | 9.6152
SW | F2777_East Stanthorpe 33 kV | Loading (MW) | 13.1 | 13.4 | 9.2 | 13.1883 | 13.4933 | 9.3324 | 13.3202 | 13.6283 | 9.4257 | 13.4534 | 13.7646 | 9.52 | 13.588 | 13.9022 | 9.6152
SW | F2777_East Stanthorpe 33 kV | Power Factor | 0.992 | 0.992 | 1 | 0.992 | 0.992 | 1 | 0.992 | 0.992 | 1 | 0.992 | 0.992 | 1 | 0.992 | 0.992 | 1
SW | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201
SW | F2777_East Stanthorpe 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2777_East Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.019 | 1.02 | 1.043 | 1.019 | 1.02 | 1.043 | 1.019 | 1.02 | 1.043 | 1.019 | 1.02 | 1.043 | 1.019 | 1.02 | 1.043
SW | F2777_East Stanthorpe 33 kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F2780_East Warwick No 1 33 kV | % of Rated A | 63.06% | 59.13% | 72.17% | 62.78% | 58.87% | 72.27% | 62.49% | 58.6% | 72.12% | 61.79% | 57.97% | 38.25% | 62.88% | 58.95% | 72.09%
SW | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 50897_2 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 50897_2 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 50897_2 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 50897_2
SW | F2780_East Warwick No 1 33 kV | Loading (A) | 334.2025 | 321.0646 | 344.2616 | 332.708 | 319.6438 | 344.7193 | 331.1978 | 318.1961 | 344.0271 | 327.4955 | 314.7629 | 182.4738 | 333.2454 | 320.1168 | 343.8565
SW | F2780_East Warwick No 1 33 kV | Loading (MVA) | 19.5689 | 18.8759 | 19.327 | 19.4702 | 18.7813 | 19.4198 | 19.3717 | 18.6868 | 19.3615 | 19.1581 | 18.5012 | 10.8136 | 19.4679 | 18.7787 | 19.3572
SW | F2780_East Warwick No 1 33 kV | Loading (MW) | 19.4249 | 18.6969 | 16.4051 | 19.3235 | 18.5994 | 16.4529 | 19.2222 | 18.5019 | 16.405 | 19.02 | 18.3063 | 10.0102 | 19.3241 | 18.5999 | 16.457
SW | F2780_East Warwick No 1 33 kV | Power Factor | 0.99259 | 0.99046 | 0.84882 | 0.99241 | 0.99026 | 0.84722 | 0.99223 | 0.99004 | 0.8473 | 0.99274 | 0.9894 | 0.92562 | 0.99256 | 0.99042 | 0.85018
SW | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | F2780_East Warwick No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2780_East Warwick No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0243 | 1.0285 | 0.98091 | 1.0237 | 1.0279 | 0.98431 | 1.0232 | 1.0274 | 0.98333 | 1.0233 | 1.0282 | 1.0368 | 1.0219 | 1.0262 | 0.98361
SW | F2780_East Warwick No 1 33 kV | Contingency Outage | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | 790_Warwick-Stanthorpe 110 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | 790_Warwick-Stanthorpe 110 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | 790_Warwick-Stanthorpe 110 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F2785_East Warwick No 2 33 kV | % of Rated A | 63.06% | 59.13% | 71.82% | 62.78% | 58.87% | 71.91% | 62.49% | 58.6% | 71.77% | 61.79% | 57.97% | 38.25% | 62.88% | 58.95% | 71.73%
SW | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 65763_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 65763_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 65763_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 65763_1
SW | F2785_East Warwick No 2 33 kV | Loading (A) | 334.2058 | 321.0661 | 342.5609 | 332.7111 | 319.6451 | 343.0163 | 331.2007 | 318.1972 | 342.3276 | 327.4985 | 314.7635 | 182.4583 | 333.2487 | 320.1182 | 342.1578
SW | F2785_East Warwick No 2 33 kV | Loading (MVA) | 19.5688 | 18.8757 | 19.3414 | 19.4701 | 18.7811 | 19.4343 | 19.3716 | 18.6867 | 19.3758 | 19.1581 | 18.501 | 10.8126 | 19.4678 | 18.7786 | 19.371
SW | F2785_East Warwick No 2 33 kV | Loading (MW) | 19.4253 | 18.6973 | 16.3716 | 19.324 | 18.5998 | 16.4192 | 19.2226 | 18.5023 | 16.3714 | 19.0204 | 18.3068 | 10.0103 | 19.3246 | 18.6003 | 16.4232
SW | F2785_East Warwick No 2 33 kV | Power Factor | 0.99261 | 0.99048 | 0.84645 | 0.99243 | 0.99028 | 0.84486 | 0.99225 | 0.99006 | 0.84494 | 0.99275 | 0.98943 | 0.9257 | 0.99258 | 0.99044 | 0.84782
SW | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | F2785_East Warwick No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F2785_East Warwick No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0243 | 1.0284 | 0.98089 | 1.0237 | 1.0278 | 0.98429 | 1.0231 | 1.0273 | 0.98331 | 1.0233 | 1.0282 | 1.0368 | 1.0219 | 1.0262 | 0.98358
SW | F2785_East Warwick No 2 33 kV | Contingency Outage | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | 790_Warwick-Stanthorpe 110 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | 790_Warwick-Stanthorpe 110 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | 790_Warwick-Stanthorpe 110 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F3040 Hampton Street | % of Rated A | 0.3089% | 0.3089% | 0.3073% | 0.3087% | 0.3087% | 0.3074% | 0.3085% | 0.3085% | 0.3072% | 0.3086% | 0.3086% | 0.3074% | 0.3085% | 0.3083% | 0.3072%
SW | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW | F3040 Hampton Street | Loading (A) | 1.5447 | 1.5443 | 1.5365 | 1.5437 | 1.5433 | 1.5369 | 1.5427 | 1.5424 | 1.536 | 1.5429 | 1.543 | 1.5368 | 1.5424 | 1.5414 | 1.5362
SW | F3040 Hampton Street | Loading (MVA) | 0.093477 | 0.093426 | 0.092476 | 0.093345 | 0.093305 | 0.092534 | 0.093228 | 0.093195 | 0.092421 | 0.093257 | 0.093268 | 0.092519 | 0.093192 | 0.093068 | 0.092442
SW | F3040 Hampton Street | Loading (MW) | 0.0013174 | 0.0013166 | 0.0013033 | 0.0013155 | 0.0013149 | 0.0013041 | 0.0013139 | 0.0013134 | 0.0013025 | 0.0013143 | 0.0013144 | 0.0013039 | 0.0013133 | 0.0013116 | 0.0013028
SW | F3040 Hampton Street | Power Factor | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534
SW | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | F3040 Hampton Street | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3040 Hampton Street | Min Voltage at Constrained Conductor (pu) | 1.0587 | 1.0584 | 1.053 | 1.058 | 1.0577 | 1.0533 | 1.0573 | 1.0571 | 1.0527 | 1.0575 | 1.0575 | 1.0533 | 1.0571 | 1.0564 | 1.0528
SW | F3040 Hampton Street | Contingency Outage | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 790_Warwick-Stanthorpe 110 kV | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 728_Middle Ridge-South Toowoomba 110 kV | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 790_Warwick-Stanthorpe 110 kV | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 728_Middle Ridge-South Toowoomba 110 kV | F3867_Pampas 33 kV | F2520_Clifton 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F3095_Highfields 33 kV | % of Rated A | 19.06% | 13.64% | 8.61% | 21.54% | 15.44% | 9.434% | 21.55% | 15.45% | 9.47% | 21.55% | 15.45% | 9.435% | 22.18% | 15.9% | 9.687%
SW | F3095_Highfields 33 kV | Limiting Line Name | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1
SW | F3095_Highfields 33 kV | Loading (A) | 47.2566 | 49.2477 | 27.7245 | 53.4206 | 55.7448 | 30.3772 | 53.455 | 55.766 | 30.4922 | 53.4491 | 55.7585 | 30.3799 | 55.0179 | 57.3977 | 31.192
SW | F3095_Highfields 33 kV | Loading (MVA) | 2.7731 | 2.8847 | 1.6232 | 3.1303 | 3.2605 | 1.7844 | 3.1304 | 3.2599 | 1.7847 | 3.1303 | 3.2606 | 1.7844 | 3.2201 | 3.3542 | 1.8254
SW | F3095_Highfields 33 kV | Loading (MW) | 2.6674 | 2.7789 | 1.4972 | 3.0244 | 3.1539 | 1.6648 | 3.0244 | 3.1538 | 1.6648 | 3.0244 | 3.1539 | 1.6648 | 3.1137 | 3.2477 | 1.7067
SW | F3095_Highfields 33 kV | Power Factor | 0.96182 | 0.96325 | 0.92218 | 0.96611 | 0.96726 | 0.93273 | 0.9661 | 0.96741 | 0.93256 | 0.9661 | 0.96725 | 0.93273 | 0.96694 | 0.9682 | 0.93474
SW | F3095_Highfields 33 kV | Rating (A) | 248 | 361 | 322 | 248 | 361 | 322 | 248 | 361 | 322 | 248 | 361 | 322 | 248 | 361 | 322
SW | F3095_Highfields 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3095_Highfields 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0266 | 1.0245 | 1.0243 | 1.025 | 1.0229 | 1.0277 | 1.0244 | 1.0223 | 1.024 | 1.0245 | 1.0226 | 1.0276 | 1.0238 | 1.0219 | 1.0239
SW | F3095_Highfields 33 kV | Contingency Outage | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | % of Rated A | 127% | 107.8% | 47.94% | 130.6% | 110.7% | 48.83% | 132.2% | 112.4% | 49.5% | 61.68% | 46.44% | 27.92% | 62.45% | 47.07% | 28.39%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 216737_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (A) | 315.0109 | 389.1947 | 154.38 | 323.823 | 399.7911 | 157.2467 | 327.9788 | 405.6161 | 159.4017 | 104.2423 | 111.465 | 65.3383 | 105.5446 | 112.9639 | 66.437
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 17.9033 | 21.6868 | 8.8765 | 18.3616 | 22.2106 | 9.0714 | 18.5705 | 22.4894 | 9.1597 | 5.7644 | 6.1405 | 3.6937 | 5.8277 | 6.212 | 3.731
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MW) | 17.5368 | 21.1384 | 8.7635 | 17.9797 | 21.6377 | 8.9566 | 18.1792 | 21.8976 | 9.043 | 5.68 | 6.049 | 3.6395 | 5.7431 | 6.12 | 3.6766
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Power Factor | 0.97953 | 0.97471 | 0.98727 | 0.9792 | 0.9742 | 0.98734 | 0.97893 | 0.97369 | 0.98727 | 0.98537 | 0.9851 | 0.98531 | 0.98549 | 0.98519 | 0.98543
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Rating (A) | 248 | 361 | 322 | 248 | 361 | 322 | 248 | 361 | 322 | 169 | 240 | 234 | 169 | 240 | 234
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99266 | 0.9708 | 1.0045 | 0.99031 | 0.96776 | 1.0078 | 0.98885 | 0.96576 | 1.0038 | 0.96745 | 0.96379 | 0.98906 | 0.966 | 0.96208 | 0.98251
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Contingency Outage | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F3255_Jennings Street 33 kV | % of Rated A | 77.66% | 73.09% | 34.48% | 77.81% | 73.45% | 34.47% | 78.18% | 73.79% | 34.74% | 78.16% | 73.75% | 34.6% | 80.42% | 75.63% | 35.63%
SW | F3255_Jennings Street 33 kV | Limiting Line Name | TR_LINE 120572_1 | TR_CABLE 3441_1 | TR_CABLE 3441_1 | TR_LINE 120572_1 | TR_CABLE 3441_1 | TR_CABLE 3441_1 | TR_LINE 120572_1 | TR_CABLE 3441_1 | TR_CABLE 3441_1 | TR_LINE 120572_1 | TR_CABLE 3441_1 | TR_CABLE 3441_1 | TR_LINE 120572_1 | TR_CABLE 3441_1 | TR_CABLE 3441_1
SW | F3255_Jennings Street 33 kV | Loading (A) | 479.1357 | 456.8192 | 215.5027 | 480.0823 | 459.047 | 215.4448 | 482.3796 | 461.1918 | 217.1017 | 482.275 | 460.9432 | 216.2477 | 496.2012 | 472.6579 | 222.6858
SW | F3255_Jennings Street 33 kV | Loading (MVA) | 28.2622 | 27.3749 | 12.882 | 28.3068 | 27.4883 | 12.9261 | 28.4206 | 27.601 | 12.9771 | 28.4196 | 27.5981 | 12.9736 | 29.1989 | 28.294 | 13.3102
SW | F3255_Jennings Street 33 kV | Loading (MW) | 26.9434 | 26.0334 | 12.6414 | 27.0312 | 26.1295 | 12.6858 | 27.129 | 26.2254 | 12.7323 | 27.1289 | 26.2248 | 12.7313 | 27.8111 | 26.8806 | 13.0508
SW | F3255_Jennings Street 33 kV | Power Factor | 0.95334 | 0.95088 | 0.98123 | 0.95494 | 0.95045 | 0.98132 | 0.95456 | 0.95005 | 0.98105 | 0.95458 | 0.95012 | 0.98123 | 0.95247 | 0.94994 | 0.98042
SW | F3255_Jennings Street 33 kV | Rating (A) | 617 | 625 | 625 | 617 | 625 | 625 | 617 | 625 | 625 | 617 | 625 | 625 | 617 | 625 | 625
SW | F3255_Jennings Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3255_Jennings Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0319 | 1.0484 | 1.0458 | 1.0314 | 1.0476 | 1.0497 | 1.0307 | 1.047 | 1.0458 | 1.0309 | 1.0475 | 1.0496 | 1.0294 | 1.0472 | 1.0457
SW | F3255_Jennings Street 33 kV | Contingency Outage | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV
SW | F3315_Sladevale 2 33kV | % of Rated A | 7.548% | 8.08% | 7.075% | 7.546% | 8.079% | 7.097% | 7.561% | 8.081% | 7.149% | 7.561% | 8.08% | 7.098% | 7.557% | 8.08% | 7.145%
SW | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW | F3315_Sladevale 2 33kV | Loading (A) | 47.9296 | 51.3101 | 44.927 | 47.9157 | 51.303 | 45.0666 | 48.0111 | 51.3112 | 45.3975 | 48.0139 | 51.3071 | 45.0745 | 47.9893 | 51.3081 | 45.372
SW | F3315_Sladevale 2 33kV | Loading (MVA) | 2.827 | 3.036 | 2.6836 | 2.8244 | 3.0338 | 2.7027 | 2.8419 | 3.0363 | 2.7472 | 2.8425 | 3.035 | 2.7037 | 2.8379 | 3.0346 | 2.7437
SW | F3315_Sladevale 2 33kV | Loading (MW) | 1.7115 | 2.1222 | 1.1097 | 1.7116 | 2.1223 | 1.1096 | 1.7112 | 2.1222 | 1.1094 | 1.7112 | 2.1222 | 1.1096 | 1.7113 | 2.1222 | 1.1094
SW | F3315_Sladevale 2 33kV | Power Factor | 0.60542 | 0.69901 | 0.41352 | 0.60599 | 0.69954 | 0.41056 | 0.60212 | 0.69893 | 0.40382 | 0.60201 | 0.69924 | 0.41039 | 0.603 | 0.69933 | 0.40433
SW | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | F3315_Sladevale 2 33kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3315_Sladevale 2 33kV | Min Voltage at Constrained Conductor (pu) | 1.0319 | 1.0352 | 1.045 | 1.0313 | 1.0346 | 1.0492 | 1.0356 | 1.0353 | 1.0587 | 1.0357 | 1.0349 | 1.0494 | 1.0346 | 1.0348 | 1.058
SW | F3315_Sladevale 2 33kV | Contingency Outage | F3970_Pozieres 33 kV | F4245_Stanthorpe 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F3970_Pozieres 33 kV | F4245_Stanthorpe 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV | 3283_Allora 33kV | F2060_Sladevale 1 33kV | F5560_735(Middle Ridge-Warwick) 110 kV | 3283_Allora 33kV | F4245_Stanthorpe 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV | 3283_Allora 33kV | F3970_Pozieres 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV
SW | F3530_Millmerran 33 kV | % of Rated A | 52.84% | 41.63% | 21.87% | 52.8% | 41.6% | 21.75% | 52.85% | 41.63% | 21.81% | 51.28% | 40.37% | 21.18% | 52.98% | 41.71% | 21.83%
SW | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1
SW | F3530_Millmerran 33 kV | Loading (A) | 67.1111 | 74.9269 | 38.2739 | 67.0573 | 74.8841 | 38.0616 | 67.1249 | 74.9397 | 38.1622 | 65.1287 | 72.6684 | 37.0654 | 67.2902 | 75.0715 | 38.2097
SW | F3530_Millmerran 33 kV | Loading (MVA) | 3.7702 | 4.1725 | 2.193 | 3.7699 | 4.1722 | 2.1922 | 3.7703 | 4.1726 | 2.1926 | 3.6723 | 4.0637 | 2.1381 | 3.7713 | 4.1735 | 2.1927
SW | F3530_Millmerran 33 kV | Loading (MW) | 3.7073 | 4.0948 | 2.1727 | 3.7071 | 4.0946 | 2.1722 | 3.7073 | 4.0949 | 2.1724 | 3.6178 | 3.9953 | 2.1213 | 3.708 | 4.0955 | 2.1726
SW | F3530_Millmerran 33 kV | Power Factor | 0.98332 | 0.98138 | 0.98738 | 0.98334 | 0.9814 | 0.98743 | 0.98331 | 0.98138 | 0.98741 | 0.98517 | 0.98318 | 0.98871 | 0.98323 | 0.98131 | 0.9874
SW | F3530_Millmerran 33 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | F3530_Millmerran 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3530_Millmerran 33 kV | Min Voltage at Constrained Conductor (pu) | 0.947 | 0.9332 | 0.9863 | 0.94775 | 0.93372 | 0.99174 | 0.94681 | 0.93304 | 0.98915 | 0.952 | 0.93887 | 0.99382 | 0.94453 | 0.93144 | 0.98794
SW | F3530_Millmerran 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F3815 North Street No 1 33 kV | % of Rated A | 61.73% | 42.51% | 23.57% | 77.78% | 53.38% | 29.04% | 94.61% | 64.76% | 34.97% | 94.26% | 64.44% | 34.69% | 95.5% | 65.33% | 35.25%
SW | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1 | TR_LINE 23887_1
SW | F3815 North Street No 1 33 kV | Loading (A) | 327.7883 | 300.945 | 159.8296 | 412.9983 | 377.959 | 196.8863 | 502.3764 | 458.4683 | 237.082 | 500.5254 | 456.222 | 235.2248 | 507.106 | 462.5633 | 238.9915
SW | F3815 North Street No 1 33 kV | Loading (MVA) | 18.4671 | 17.0136 | 9.3051 | 22.7889 | 20.9743 | 11.4733 | 27.1798 | 25.0039 | 13.735 | 27.0894 | 24.9054 | 13.6763 | 27.3946 | 25.1995 | 13.8427
SW | F3815 North Street No 1 33 kV | Loading (MW) | 18.1236 | 16.7133 | 9.1718 | 22.1116 | 20.3827 | 11.2047 | 26.3045 | 24.2447 | 13.3813 | 26.2052 | 24.1525 | 13.3269 | 26.505 | 24.4287 | 13.4841
SW | F3815 North Street No 1 33 kV | Power Factor | 0.9814 | 0.98235 | 0.98567 | 0.97028 | 0.9718 | 0.9766 | 0.9678 | 0.96964 | 0.97425 | 0.96736 | 0.96977 | 0.97446 | 0.96753 | 0.96941 | 0.9741
SW | F3815 North Street No 1 33 kV | Rating (A) | 531 | 708 | 678 | 531 | 708 | 678 | 531 | 708 | 678 | 531 | 708 | 678 | 531 | 708 | 678
SW | F3815 North Street No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3815 North Street No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 0.97406 | 0.97849 | 1.0025 | 0.95006 | 0.95694 | 0.99869 | 0.92774 | 0.93711 | 0.98816 | 0.92812 | 0.93812 | 0.99203 | 0.92613 | 0.9359 | 0.98773
SW | F3815 North Street No 1 33 kV | Contingency Outage | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV
SW | F3820_Boundary Road 33 kV | % of Rated A | 45.45% | 42% | 22.5% | 56.41% | 51.92% | 27.69% | 67.25% | 61.95% | 32.92% | 66.96% | 61.72% | 32.68% | 67.85% | 62.41% | 33.18%
SW | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW | F3820_Boundary Road 33 kV | Loading (A) | 313.6266 | 289.7865 | 155.2371 | 389.2024 | 358.2533 | 191.0338 | 464.0138 | 427.4392 | 227.1697 | 462.0447 | 425.8542 | 225.4652 | 468.1841 | 430.6461 | 228.9346
SW | F3820_Boundary Road 33 kV | Loading (MVA) | 18.3856 | 16.9345 | 9.0907 | 22.6808 | 20.8656 | 11.1429 | 27.0596 | 24.8906 | 13.2803 | 26.9532 | 24.7944 | 13.2275 | 27.2736 | 25.0834 | 13.3814
SW | F3820_Boundary Road 33 kV | Loading (MW) | 18.1291 | 16.7212 | 9.0512 | 22.1042 | 20.3803 | 11.0154 | 26.272 | 24.2258 | 13.0984 | 26.1726 | 24.1346 | 13.0488 | 26.4712 | 24.4083 | 13.1964
SW | F3820_Boundary Road 33 kV | Power Factor | 0.9857 | 0.98707 | 0.99541 | 0.9742 | 0.97636 | 0.9883 | 0.97058 | 0.97295 | 0.98602 | 0.97072 | 0.97305 | 0.98621 | 0.97027 | 0.97275 | 0.98589
SW | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | F3820_Boundary Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3820_Boundary Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0256 | 1.0224 | 1.0245 | 1.0195 | 1.019 | 1.0205 | 1.0201 | 1.0187 | 1.0228 | 1.0204 | 1.0185 | 1.0264 | 1.019 | 1.0189 | 1.0226
SW | F3820_Boundary Road 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7233_Middle Ridge-Torrington 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F3980_Purrawunda 33 kV
SW | F3830_Norwin 33 kV | % of Rated A | 28.86% | 26.92% | 20.75% | 28.84% | 26.91% | 20.64% | 28.87% | 26.93% | 20.41% | 27.31% | 25.45% | 19.55% | 28.91% | 26.96% | 20.42%
SW | F3830_Norwin 33 kV | Limiting Line Name | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1 | TR_LINE 23945_1
SW | F3830_Norwin 33 kV | Loading (A) | 33.4788 | 39.8475 | 29.2566 | 33.4547 | 39.8273 | 29.0998 | 33.4849 | 39.8535 | 28.7715 | 31.6756 | 37.6731 | 27.5709 | 33.5411 | 39.8963 | 28.7923
SW | F3830_Norwin 33 kV | Loading (MVA) | 1.7818 | 2.1046 | 1.6434 | 1.7817 | 2.1045 | 1.6427 | 1.7818 | 2.1047 | 1.6406 | 1.6912 | 1.9973 | 1.5591 | 1.7822 | 2.1049 | 1.6408
SW | F3830_Norwin 33 kV | Loading (MW) | 1.4641 | 1.7156 | 1.3613 | 1.4641 | 1.7155 | 1.3611 | 1.4641 | 1.7156 | 1.3608 | 1.3934 | 1.6323 | 1.2956 | 1.4642 | 1.7156 | 1.3609
SW | F3830_Norwin 33 kV | Power Factor | 0.82162 | 0.81507 | 0.82822 | 0.82167 | 0.81511 | 0.8285 | 0.82161 | 0.81506 | 0.82936 | 0.82379 | 0.81719 | 0.83085 | 0.82149 | 0.81499 | 0.82931
SW | F3830_Norwin 33 kV | Rating (A) | 116 | 148 | 141 | 116 | 148 | 141 | 116 | 148 | 141 | 116 | 148 | 141 | 116 | 148 | 141
SW | F3830_Norwin 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3830_Norwin 33 kV | Min Voltage at Constrained Conductor (pu) | 0.93111 | 0.92398 | 0.98276 | 0.93171 | 0.9244 | 0.98764 | 0.93096 | 0.92386 | 0.99764 | 0.9341 | 0.9275 | 0.98938 | 0.92957 | 0.92298 | 0.99701
SW | F3830_Norwin 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | % of Rated A | 60.84% | 67.08% | 48.02% | 61.06% | 67.34% | 47.9% | 61.27% | 66.57% | 48.1% | 60.62% | 66.66% | 47.45% | 62.13% | 67.45% | 48.66%
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Loading (A) | 128.3622 | 141.5379 | 101.313 | 128.84 | 142.0842 | 101.0794 | 129.278 | 140.4697 | 101.4843 | 127.9015 | 140.6619 | 100.1152 | 131.0979 | 142.3168 | 102.6765
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Loading (MVA) | 7.5553 | 8.2914 | 5.9366 | 7.5566 | 8.295 | 5.9385 | 7.5609 | 8.2846 | 5.9354 | 7.4823 | 8.2012 | 5.8781 | 7.6591 | 8.3926 | 6.0039
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Loading (MW) | 7.5468 | 8.2912 | 5.87 | 7.5494 | 8.2945 | 5.8689 | 7.5515 | 8.2846 | 5.8708 | 7.4725 | 8.2012 | 5.798 | 7.6519 | 8.3925 | 5.9436
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Power Factor | 0.99888 | 0.99995 | 0.98879 | 0.99906 | 0.99991 | 0.98829 | 0.99875 | 1 | 0.98912 | 0.9987 | 0.99999 | 0.98637 | 0.99906 | 0.99997 | 0.98996
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0297 | 1.0248 | 1.0251 | 1.0261 | 1.0213 | 1.0278 | 1.0232 | 1.0318 | 1.0232 | 1.0234 | 1.02 | 1.0272 | 1.0221 | 1.0316 | 1.023
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Contingency Outage | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV
SW | F3855 Omaras Road 33 kV | % of Rated A | 16.98% | 17.42% | 16.77% | 17.05% | 17.48% | 16.83% | 17.04% | 17.48% | 16.8% | 17.04% | 17.48% | 16.74% | 17.06% | 17.47% | 16.8%
SW | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW | F3855 Omaras Road 33 kV | Loading (A) | 39.564 | 40.5844 | 39.0692 | 39.7352 | 40.718 | 39.2233 | 39.7084 | 40.7264 | 39.1334 | 39.6957 | 40.733 | 38.9932 | 39.7514 | 40.7165 | 39.1392
SW | F3855 Omaras Road 33 kV | Loading (MVA) | 2.3047 | 2.3606 | 2.2776 | 2.3047 | 2.3606 | 2.2776 | 2.3047 | 2.3606 | 2.2776 | 2.3047 | 2.3606 | 2.2776 | 2.3047 | 2.3606 | 2.2776
SW | F3855 Omaras Road 33 kV | Loading (MW) | 2.0631 | 2.1132 | 2.0388 | 2.0631 | 2.1132 | 2.0388 | 2.0631 | 2.1132 | 2.0388 | 2.0631 | 2.1132 | 2.0388 | 2.0631 | 2.1132 | 2.0388
SW | F3855 Omaras Road 33 kV | Power Factor | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895 | 0.895
SW | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
SW | F3855 Omaras Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3855 Omaras Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0192 | 1.0176 | 1.0199 | 1.0148 | 1.0143 | 1.0159 | 1.0155 | 1.0141 | 1.0183 | 1.0158 | 1.0139 | 1.0219 | 1.0144 | 1.0143 | 1.0181
SW | F3855 Omaras Road 33 kV | Contingency Outage | F3820_Boundary Road 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7233_Middle Ridge-Torrington 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F3980_Purrawunda 33 kV
SW | F3867_Pampas 33 kV | % of Rated A | 65.85% | 70.67% | 45.65% | 65.8% | 70.63% | 45.39% | 65.87% | 70.68% | 44.92% | 64.78% | 69.45% | 44.92% | 66.49% | 71.25% | 45.39%
SW | F3867_Pampas 33 kV | Limiting Line Name | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1
SW | F3867_Pampas 33 kV | Loading (A) | 197.5635 | 212.0088 | 134.1993 | 197.4096 | 211.8915 | 133.4582 | 197.603 | 212.0436 | 132.0715 | 194.352 | 208.3512 | 132.0688 | 199.4581 | 213.7579 | 133.4578
SW | F3867_Pampas 33 kV | Loading (MVA) | 10.0392 | 10.6777 | 7.3527 | 10.0386 | 10.6772 | 7.3506 | 10.0394 | 10.6778 | 7.3515 | 9.9107 | 10.5361 | 7.2835 | 10.1114 | 10.7475 | 7.42
SW | F3867_Pampas 33 kV | Loading (MW) | 9.2079 | 9.794 | 6.7225 | 9.2077 | 9.7938 | 6.7219 | 9.208 | 9.7941 | 6.7221 | 9.105 | 9.6797 | 6.6626 | 9.2748 | 9.8624 | 6.7796
SW | F3867_Pampas 33 kV | Power Factor | 0.91709 | 0.91712 | 0.91428 | 0.91712 | 0.91715 | 0.91447 | 0.91708 | 0.91712 | 0.91438 | 0.91859 | 0.91861 | 0.91475 | 0.91716 | 0.91752 | 0.91369
SW | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294
SW | F3867_Pampas 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3867_Pampas 33 kV | Min Voltage at Constrained Conductor (pu) | 0.88903 | 0.88115 | 0.95854 | 0.88967 | 0.88159 | 0.96358 | 0.88887 | 0.88102 | 0.97383 | 0.89216 | 0.88473 | 0.96483 | 0.88692 | 0.87965 | 0.97269
SW | F3867_Pampas 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F3910_Perseverence Creek 1 33 kV | % of Rated A | 98.01% | 73.92% | 43.99% | 96.54% | 73.98% | 43.8% | 96.61% | 74.03% | 43.98% | 95.55% | 73.11% | 43.37% | 96.67% | 74.04% | 43.98%
SW | F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1
SW | F3910_Perseverence Creek 1 33 kV | Loading (A) | 165.6422 | 177.397 | 102.9289 | 163.1529 | 177.5412 | 102.5027 | 163.2784 | 177.6754 | 102.9142 | 161.4812 | 175.4737 | 101.484 | 163.3639 | 177.7 | 102.9228
SW | F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 8.8578 | 9.5266 | 5.7133 | 8.8545 | 9.5268 | 5.7132 | 8.8547 | 9.5271 | 5.7133 | 8.7687 | 9.4269 | 5.6593 | 8.8552 | 9.5272 | 5.7133
SW | F3910_Perseverence Creek 1 33 kV | Loading (MW) | 8.7013 | 9.3527 | 5.6325 | 8.6995 | 9.3528 | 5.6324 | 8.6996 | 9.353 | 5.6325 | 8.6151 | 9.2549 | 5.579 | 8.6998 | 9.353 | 5.6325
SW | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.98233 | 0.98175 | 0.98586 | 0.9825 | 0.98173 | 0.98586 | 0.98249 | 0.98172 | 0.98586 | 0.98249 | 0.98176 | 0.98581 | 0.98245 | 0.98172 | 0.98586
SW | F3910_Perseverence Creek 1 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | F3910_Perseverence Creek 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor (pu) | 0.93556 | 0.93951 | 0.97111 | 0.94948 | 0.93878 | 0.97513 | 0.94877 | 0.9381 | 0.97124 | 0.95001 | 0.93987 | 0.97563 | 0.94832 | 0.93797 | 0.97116
SW | F3910_Perseverence Creek 1 33 kV | Contingency Outage | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV
SW | F3970_Pozieres 33 kV | % of Rated A | 40.32% | 31.48% | 20.89% | 40.34% | 31.5% | 20.8% | 40.36% | 31.52% | 20.57% | 40.33% | 31.45% | 20.79% | 41.74% | 32.22% | 21.22%
SW | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2
SW | F3970_Pozieres 33 kV | Loading (A) | 57.6524 | 65.4794 | 41.994 | 57.6871 | 65.5234 | 41.8066 | 57.7169 | 65.5567 | 41.3414 | 57.6649 | 65.4113 | 41.7855 | 59.6907 | 67.0158 | 42.65
SW | F3970_Pozieres 33 kV | Loading (MVA) | 3.1807 | 3.5742 | 2.5196 | 3.1807 | 3.5743 | 2.5191 | 3.1807 | 3.5744 | 2.5185 | 3.1807 | 3.574 | 2.5191 | 3.2722 | 3.6783 | 2.5924
SW | F3970_Pozieres 33 kV | Loading (MW) | 2.8189 | 3.1649 | 2.2475 | 2.8188 | 3.165 | 2.2474 | 2.8189 | 3.165 | 2.2471 | 2.8188 | 3.1649 | 2.2473 | 2.8994 | 3.256 | 2.3118
SW | F3970_Pozieres 33 kV | Power Factor | 0.88624 | 0.88551 | 0.89187 | 0.88623 | 0.88548 | 0.892 | 0.88622 | 0.88546 | 0.89213 | 0.88624 | 0.88554 | 0.89201 | 0.8861 | 0.8852 | 0.89165
SW | F3970_Pozieres 33 kV | Rating (A) | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201
SW | F3970_Pozieres 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor (pu) | 0.9652 | 0.95466 | 1.0497 | 0.96463 | 0.95405 | 1.0542 | 0.96414 | 0.9536 | 1.0657 | 0.96499 | 0.9556 | 1.0547 | 0.95905 | 0.95993 | 1.0633
SW | F3970_Pozieres 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | F3980_Purrawunda 33 kV | % of Rated A | 49.93% | 53.23% | 39.18% | 50.24% | 53.51% | 39.26% | 50.07% | 53.52% | 39.21% | 50.05% | 53.52% | 39.14% | 50.92% | 54.28% | 39.68%
SW | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | F3980_Purrawunda 33 kV | Loading (A) | 105.349 | 112.3219 | 82.6676 | 106.0148 | 112.8984 | 82.8479 | 105.6389 | 112.917 | 82.7376 | 105.6133 | 112.9317 | 82.5911 | 107.4381 | 114.5233 | 83.7292
SW | F3980_Purrawunda 33 kV | Loading (MVA) | 6.1681 | 6.5659 | 4.8443 | 6.1806 | 6.5782 | 4.8335 | 6.1628 | 6.5779 | 4.8401 | 6.1632 | 6.5778 | 4.8491 | 6.2676 | 6.6731 | 4.8971
SW | F3980_Purrawunda 33 kV | Loading (MW) | 5.968 | 6.4157 | 4.429 | 5.9704 | 6.4178 | 4.4296 | 5.9692 | 6.4179 | 4.4293 | 5.9691 | 6.418 | 4.4288 | 6.0676 | 6.523 | 4.5007
SW | F3980_Purrawunda 33 kV | Power Factor | 0.96757 | 0.97713 | 0.91428 | 0.96599 | 0.97562 | 0.91645 | 0.96859 | 0.97567 | 0.91513 | 0.9685 | 0.97571 | 0.91333 | 0.96809 | 0.9775 | 0.91905
SW | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SW | F3980_Purrawunda 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0243 | 1.0227 | 1.0252 | 1.0199 | 1.0194 | 1.0207 | 1.0206 | 1.0191 | 1.0234 | 1.0209 | 1.019 | 1.0272 | 1.0206 | 1.0194 | 1.0232
SW | F3980_Purrawunda 33 kV | Contingency Outage | F3820_Boundary Road 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7233_Middle Ridge-Torrington 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7449 South Toowoomba-TWCE 110 kV
SW | F4005_Racecourse 33 kV | % of Rated A | 45.24% | 44.92% | 23.84% | 45.17% | 44.83% | 23.66% | 44.84% | 44.48% | 23.52% | 44.36% | 43.96% | 23.19% | 44.89% | 44.49% | 23.52%
SW | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1
SW | F4005_Racecourse 33 kV | Loading (A) | 319.4086 | 317.1336 | 168.3417 | 318.9304 | 316.4683 | 167.0318 | 316.5637 | 314.0437 | 166.0468 | 313.1724 | 310.3664 | 163.7158 | 316.919 | 314.0761 | 166.0778
SW | F4005_Racecourse 33 kV | Loading (MVA) | 18.6336 | 18.4203 | 9.8255 | 18.5401 | 18.3209 | 9.7752 | 18.3506 | 18.1336 | 9.6758 | 18.1595 | 17.9443 | 9.5754 | 18.3512 | 18.1336 | 9.6758
SW | F4005_Racecourse 33 kV | Loading (MW) | 18.2674 | 18.0588 | 9.6803 | 18.1752 | 17.9663 | 9.6312 | 17.9905 | 17.7836 | 9.5334 | 17.8053 | 17.6005 | 9.4354 | 17.9906 | 17.7836 | 9.5334
SW | F4005_Racecourse 33 kV | Power Factor | 0.98021 | 0.98025 | 0.98513 | 0.98019 | 0.98051 | 0.98518 | 0.98024 | 0.98057 | 0.98519 | 0.98037 | 0.98071 | 0.98528 | 0.98022 | 0.98057 | 0.98519
SW | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
SW | F4005_Racecourse 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F4005_Racecourse 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0206 | 1.0162 | 1.0211 | 1.017 | 1.0128 | 1.0239 | 1.0142 | 1.0102 | 1.0195 | 1.0145 | 1.0115 | 1.0233 | 1.0131 | 1.0101 | 1.0193
SW | F4005_Racecourse 33 kV | Contingency Outage | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV
SW | F4015_Ramsay Street 33 kV | % of Rated A | 79.94% | 73.37% | 34.53% | 80.34% | 73.73% | 34.52% | 80.73% | 73.87% | 34.78% | 80.71% | 73.83% | 34.65% | 83.06% | 75.92% | 35.68%
SW | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_LINE 170027_1 | TR_CABLE 86_1 | TR_CABLE 86_1 | TR_LINE 170027_1 | TR_CABLE 86_1 | TR_CABLE 86_1 | TR_LINE 170027_1 | TR_CABLE 86_1 | TR_CABLE 86_1 | TR_LINE 170027_1 | TR_CABLE 86_1 | TR_CABLE 86_1 | TR_LINE 170027_1 | TR_CABLE 86_1 | TR_CABLE 86_1
SW | F4015_Ramsay Street 33 kV | Loading (A) | 479.6671 | 458.5458 | 215.7903 | 482.0301 | 460.7988 | 215.731 | 484.3553 | 461.6813 | 217.3942 | 484.2488 | 461.4322 | 216.5363 | 498.3386 | 474.5187 | 222.9956
SW | F4015_Ramsay Street 33 kV | Loading (MVA) | 28.2809 | 27.5308 | 12.9086 | 28.3961 | 27.6462 | 12.9526 | 28.5111 | 27.6901 | 13.0041 | 28.51 | 27.6871 | 13.0004 | 29.2969 | 28.4623 | 13.3388
SW | F4015_Ramsay Street 33 kV | Loading (MW) | 26.9714 | 26.1333 | 12.6636 | 27.0697 | 26.2304 | 12.708 | 27.1679 | 26.316 | 12.7548 | 27.1677 | 26.3153 | 12.7537 | 27.8524 | 26.9876 | 13.0745
SW | F4015_Ramsay Street 33 kV | Power Factor | 0.9537 | 0.94875 | 0.98063 | 0.95329 | 0.9483 | 0.98073 | 0.95289 | 0.94989 | 0.98044 | 0.95292 | 0.94997 | 0.98064 | 0.95069 | 0.94772 | 0.97979
SW | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 625 | 625 | 600 | 625 | 625 | 600 | 625 | 625 | 600 | 625 | 625 | 600 | 625 | 625
SW | F4015_Ramsay Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F4015_Ramsay Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0295 | 1.0502 | 1.0466 | 1.0286 | 1.0495 | 1.0504 | 1.0278 | 1.0491 | 1.0465 | 1.028 | 1.0496 | 1.0504 | 1.0264 | 1.0492 | 1.0465
SW | F4015_Ramsay Street 33 kV | Contingency Outage | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV
SW | F4132_Shirley Road 33 kV | % of Rated A | 61.8% | 48.31% | 14.84% | 62.8% | 49.02% | 15.07% | 63.79% | 49.83% | 15.27% | 65.87% | 46.84% | 14.11% | 68.06% | 48.3% | 14.6%
SW | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1
SW | F4132_Shirley Road 33 kV | Loading (A) | 259.541 | 328.0091 | 118.1374 | 263.7543 | 332.8312 | 119.9627 | 267.9156 | 338.3714 | 121.5849 | 276.6396 | 318.05 | 112.3141 | 285.8678 | 327.9455 | 116.1961
SW | F4132_Shirley Road 33 kV | Loading (MVA) | 14.9417 | 18.7405 | 6.8768 | 15.1136 | 18.9445 | 6.9548 | 15.3564 | 19.2458 | 7.0643 | 15.8585 | 18.1331 | 6.5536 | 16.3516 | 18.6888 | 6.7532
SW | F4132_Shirley Road 33 kV | Loading (MW) | 14.9054 | 18.6648 | 6.8764 | 15.0763 | 18.8659 | 6.9543 | 15.316 | 19.163 | 7.0637 | 15.8264 | 18.0827 | 6.5536 | 16.3156 | 18.6335 | 6.7531
SW | F4132_Shirley Road 33 kV | Power Factor | 0.99757 | 0.99596 | 0.99994 | 0.99753 | 0.99585 | 0.99992 | 0.99737 | 0.9957 | 0.99991 | 0.99798 | 0.99722 | 1 | 0.9978 | 0.99704 | 0.99998
SW | F4132_Shirley Road 33 kV | Rating (A) | 420 | 679 | 796 | 420 | 679 | 796 | 420 | 679 | 796 | 420 | 679 | 796 | 420 | 679 | 796
SW | F4132_Shirley Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F4132_Shirley Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0072 | 0.99958 | 1.0184 | 1.0025 | 0.99582 | 1.0143 | 1.0028 | 0.99509 | 1.0165 | 1.0029 | 0.99746 | 1.0209 | 1.0007 | 0.99701 | 1.0168
SW | F4132_Shirley Road 33 kV | Contingency Outage | F3820_Boundary Road 33 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7233_Middle Ridge-Torrington 110 kV | F3980_Purrawunda 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F3980_Purrawunda 33 kV
SW | F4245_Stanthorpe 33 kV | % of Rated A | 56.31% | 63.54% | 39.56% | 56.38% | 63.57% | 39.51% | 56.44% | 63.6% | 39.38% | 56.35% | 63.49% | 40.71% | 53.77% | 64.34% | 39.88%
SW | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1
SW | F4245_Stanthorpe 33 kV | Loading (A) | 164.4307 | 185.5362 | 115.511 | 164.6304 | 185.6325 | 115.3684 | 164.807 | 185.7046 | 114.9906 | 164.5552 | 185.3862 | 118.8824 | 157.0057 | 187.8634 | 116.4616
SW | F4245_Stanthorpe 33 kV | Loading (MVA) | 8.5376 | 10.282 | 7.0171 | 8.5352 | 10.281 | 7.0377 | 8.533 | 10.2802 | 7.0898 | 8.5361 | 10.2836 | 6.7221 | 8.8311 | 10.4715 | 7.1674
SW | F4245_Stanthorpe 33 kV | Loading (MW) | 8.3158 | 10.0818 | 6.03 | 8.316 | 10.0818 | 6.0298 | 8.316 | 10.0818 | 6.0296 | 8.316 | 10.0817 | 6.0311 | 8.4762 | 10.2765 | 6.146
SW | F4245_Stanthorpe 33 kV | Power Factor | 0.97403 | 0.98053 | 0.85922 | 0.97432 | 0.98063 | 0.85669 | 0.97457 | 0.9807 | 0.85036 | 0.97421 | 0.98037 | 0.8971 | 0.95981 | 0.98138 | 0.85739
SW | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
SW | F4245_Stanthorpe 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F4245_Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 0.90837 | 0.96952 | 1.0628 | 0.90701 | 0.96893 | 1.0672 | 0.90581 | 0.96848 | 1.0787 | 0.90753 | 0.97046 | 0.98922 | 0.98405 | 0.97516 | 1.0767
SW | F4245_Stanthorpe 33 kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | F4470 Vacy Street | % of Rated A | 0.4539% | 0.4537% | 0.4514% | 0.4535% | 0.4534% | 0.4516% | 0.4533% | 0.4532% | 0.4513% | 0.4533% | 0.4534% | 0.4515% | 0.4532% | 0.4529% | 0.4513%
SW | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW | F4470 Vacy Street | Loading (A) | 2.2693 | 2.2687 | 2.2571 | 2.2677 | 2.2672 | 2.2578 | 2.2663 | 2.2659 | 2.2565 | 2.2666 | 2.2668 | 2.2577 | 2.2659 | 2.2643 | 2.2567
SW | F4470 Vacy Street | Loading (MVA) | 0.13732 | 0.13725 | 0.13585 | 0.13713 | 0.13707 | 0.13594 | 0.13696 | 0.13691 | 0.13577 | 0.137 | 0.13702 | 0.13592 | 0.1369 | 0.13672 | 0.1358
SW | F4470 Vacy Street | Loading (MW) | 0.0023871 | 0.0023858 | 0.0023616 | 0.0023838 | 0.0023827 | 0.002363 | 0.0023808 | 0.0023799 | 0.0023602 | 0.0023815 | 0.0023818 | 0.0023627 | 0.0023798 | 0.0023767 | 0.0023607
SW | F4470 Vacy Street | Power Factor | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605
SW | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | F4470 Vacy Street | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F4470 Vacy Street | Min Voltage at Constrained Conductor (pu) | 1.0587 | 1.0584 | 1.053 | 1.058 | 1.0577 | 1.0533 | 1.0573 | 1.0571 | 1.0527 | 1.0575 | 1.0575 | 1.0533 | 1.0571 | 1.0564 | 1.0528
SW | F4470 Vacy Street | Contingency Outage | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 790_Warwick-Stanthorpe 110 kV | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 728_Middle Ridge-South Toowoomba 110 kV | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 790_Warwick-Stanthorpe 110 kV | F2520_Clifton 33 kV | F2520_Clifton 33 kV | 728_Middle Ridge-South Toowoomba 110 kV | F3867_Pampas 33 kV | F2520_Clifton 33 kV | 790_Warwick-Stanthorpe 110 kV
SW | F4605_West Warwick 33 kV | % of Rated A | 43.7% | 51.13% | 26.59% | 43.72% | 51.16% | 26.5% | 43.74% | 51.18% | 26.53% | 43.31% | 50.63% | 25.87% | 44.28% | 51.82% | 26.76%
SW | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW | F4605_West Warwick 33 kV | Loading (A) | 169.9799 | 200.4278 | 90.4194 | 170.068 | 200.5399 | 90.0967 | 170.142 | 200.6214 | 90.1911 | 168.4653 | 198.451 | 87.9573 | 172.2633 | 203.132 | 90.9828
SW | F4605_West Warwick 33 kV | Loading (MVA) | 9.6829 | 11.4572 | 5.1482 | 9.6832 | 11.4576 | 5.1476 | 9.6834 | 11.4579 | 5.1478 | 9.5947 | 11.3563 | 5.1005 | 9.7738 | 11.5658 | 5.1941
SW | F4605_West Warwick 33 kV | Loading (MW) | 9.4556 | 11.1568 | 5.0684 | 9.4557 | 11.157 | 5.0682 | 9.4558 | 11.1571 | 5.0683 | 9.3708 | 11.0573 | 5.0225 | 9.5413 | 11.2585 | 5.1134
SW | F4605_West Warwick 33 kV | Power Factor | 0.97652 | 0.97378 | 0.9845 | 0.9765 | 0.97376 | 0.98457 | 0.97649 | 0.97375 | 0.98455 | 0.97667 | 0.97367 | 0.98472 | 0.97622 | 0.97342 | 0.98447
SW | F4605_West Warwick 33 kV | Rating (A) | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340
SW | F4605_West Warwick 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F4605_West Warwick 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99642 | 0.99985 | 0.99604 | 0.99593 | 0.99933 | 0.99949 | 0.99552 | 0.99895 | 0.99848 | 0.99622 | 1.0009 | 1.0144 | 0.99243 | 0.99589 | 0.99869
SW | F4605_West Warwick 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F4685_Wyalla Street 33 kV | % of Rated A | 46.36% | 46.03% | 24.41% | 46.29% | 45.93% | 24.22% | 45.93% | 45.58% | 24.08% | 45.45% | 45.04% | 23.74% | 45.98% | 45.58% | 24.08%
SW | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1
SW | F4685_Wyalla Street 33 kV | Loading (A) | 319.8745 | 317.5858 | 168.4572 | 319.3968 | 316.9279 | 167.145 | 316.8838 | 314.4971 | 166.1273 | 313.5969 | 310.7757 | 163.8244 | 317.2404 | 314.5297 | 166.1583
SW | F4685_Wyalla Street 33 kV | Loading (MVA) | 18.6344 | 18.421 | 9.8256 | 18.5408 | 18.3216 | 9.7753 | 18.3445 | 18.1343 | 9.6742 | 18.1602 | 17.9449 | 9.5755 | 18.3451 | 18.1344 | 9.6743
SW | F4685_Wyalla Street 33 kV | Loading (MW) | 18.2681 | 18.0595 | 9.6805 | 18.1759 | 17.967 | 9.6315 | 17.9898 | 17.7843 | 9.5333 | 17.806 | 17.6012 | 9.4356 | 17.9899 | 17.7843 | 9.5333
SW | F4685_Wyalla Street 33 kV | Power Factor | 0.98018 | 0.98021 | 0.98512 | 0.98016 | 0.98048 | 0.98517 | 0.9805 | 0.98054 | 0.98531 | 0.98034 | 0.98069 | 0.98528 | 0.98048 | 0.98054 | 0.98531
SW | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | F4685_Wyalla Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F4685_Wyalla Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0192 | 1.0148 | 1.0205 | 1.0156 | 1.0114 | 1.0232 | 1.0128 | 1.0088 | 1.0188 | 1.0131 | 1.0102 | 1.0226 | 1.0117 | 1.0087 | 1.0186
SW | F4685_Wyalla Street 33 kV | Contingency Outage | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV
SW | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 68.43% | 62.84% | 36.08% | 67.97% | 62.41% | 35.59% | 67.76% | 62.21% | 35.32% | 66.86% | 61.44% | 35.12% | 68.02% | 62.47% | 35.41%
SW | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 180.6471 | 169.0291 | 84.7792 | 179.4374 | 167.8742 | 83.6457 | 178.8949 | 167.3368 | 82.9949 | 176.5197 | 165.2694 | 82.5394 | 179.5657 | 168.0476 | 83.2061
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 33.8004 | 31.7847 | 16.465 | 33.5844 | 31.5766 | 16.3821 | 33.4803 | 31.4737 | 16.3396 | 33.0793 | 31.1208 | 16.1734 | 33.5842 | 31.5909 | 16.3783
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 32.8218 | 30.9639 | 16.4325 | 32.6343 | 30.7823 | 16.3526 | 32.5392 | 30.6879 | 16.3134 | 32.1818 | 30.3555 | 16.1489 | 32.6227 | 30.7846 | 16.3504
SW | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.97105 | 0.97417 | 0.99802 | 0.97171 | 0.97485 | 0.99819 | 0.97189 | 0.97503 | 0.99838 | 0.97287 | 0.97541 | 0.99847 | 0.97137 | 0.97448 | 0.99828
SW | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235
SW | F5540_7244 Tangkam-Dalby 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F5540_7244 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 0.98192 | 0.98684 | 1.0193 | 0.98222 | 0.98713 | 1.0279 | 0.98215 | 0.98707 | 1.0333 | 0.98345 | 0.98822 | 1.0284 | 0.98152 | 0.98656 | 1.0331
SW | F5540_7244 Tangkam-Dalby 110 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV
SW | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 141.4% | 93.51% | 48.34% | 140.5% | 92.87% | 47.7% | 140.1% | 92.59% | 47.33% | 138.3% | 91.33% | 47.07% | 140.6% | 92.98% | 47.45%
SW | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 179.6351 | 168.3151 | 84.5956 | 178.4424 | 167.173 | 83.4666 | 177.907 | 166.6531 | 82.8235 | 175.6507 | 164.3917 | 82.3675 | 178.5674 | 167.3573 | 83.0385
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 33.8268 | 31.8318 | 16.4688 | 33.6105 | 31.6231 | 16.3856 | 33.5063 | 31.5218 | 16.3434 | 33.1176 | 31.1344 | 16.177 | 33.6103 | 31.6396 | 16.3828
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 32.8565 | 31.0074 | 16.441 | 32.6686 | 30.8254 | 16.3609 | 32.5733 | 30.7309 | 16.3215 | 32.218 | 30.3846 | 16.157 | 32.657 | 30.8281 | 16.3589
SW | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.97132 | 0.9741 | 0.99827 | 0.97198 | 0.97477 | 0.99846 | 0.97216 | 0.97491 | 0.99862 | 0.97284 | 0.97591 | 0.99873 | 0.97164 | 0.97435 | 0.9985
SW | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | F5545_7245 Tangkam-Dalby 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F5545_7245 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 0.98789 | 0.99219 | 1.0216 | 0.98814 | 0.99243 | 1.0302 | 0.98804 | 0.99233 | 1.0355 | 0.98913 | 0.99363 | 1.0307 | 0.98744 | 0.99185 | 1.0353
SW | F5545_7245 Tangkam-Dalby 110 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 66.52% | 67.65% | 36.1% | 66.19% | 67.38% | 35.9% | 66.23% | 67.38% | 41.81% | 65.37% | 66.48% | 35.41% | 66.71% | 67.77% | 42.14%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 190.9243 | 193.4777 | 89.1715 | 189.9609 | 192.7053 | 88.6607 | 190.0787 | 192.6984 | 103.2768 | 187.6246 | 190.1364 | 87.4517 | 191.4615 | 193.8332 | 104.0759
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 35.0477 | 35.4254 | 17.2223 | 34.8647 | 35.2755 | 17.1955 | 34.8618 | 35.2545 | 20.022 | 34.4577 | 34.8414 | 16.9688 | 35.0795 | 35.4393 | 20.1685
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 24.9609 | 25.3125 | 16.1861 | 25.0475 | 25.3935 | 16.2379 | 25.049 | 25.3957 | 16.5139 | 24.7476 | 25.0736 | 16.0467 | 25.2339 | 25.5742 | 16.635
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.71217 | 0.7145 | 0.93978 | 0.71839 | 0.71983 | 0.94426 | 0.71849 | 0.72032 | 0.82473 | 0.71817 | 0.71962 | 0.94561 | 0.7193 | 0.72161 | 0.82474
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 0.96337 | 0.9609 | 1.0137 | 0.9632 | 0.96066 | 1.018 | 0.96252 | 0.96013 | 1.0175 | 0.96381 | 0.96167 | 1.0184 | 0.96153 | 0.95951 | 1.0171
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 66.52% | 67.68% | 36.1% | 66.18% | 67.37% | 35.89% | 66.22% | 67.41% | 41.82% | 65.38% | 66.47% | 35.4% | 66.7% | 67.76% | 42.14%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 190.8998 | 193.5674 | 89.1685 | 189.9378 | 192.6797 | 88.6582 | 190.0553 | 192.7882 | 103.2961 | 187.6417 | 190.1138 | 87.4493 | 191.4369 | 193.8065 | 104.095
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 35.0995 | 35.4985 | 17.2214 | 34.916 | 35.3291 | 17.1948 | 34.9133 | 35.327 | 20.0243 | 34.5136 | 34.8932 | 16.9678 | 35.1321 | 35.4939 | 20.1707
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 25.0181 | 25.3705 | 16.1981 | 25.1042 | 25.4518 | 16.2498 | 25.1058 | 25.4533 | 16.5311 | 24.8034 | 25.1304 | 16.0583 | 25.2914 | 25.6332 | 16.6525
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.71232 | 0.71425 | 0.93985 | 0.71854 | 0.71999 | 0.94433 | 0.71864 | 0.72008 | 0.82465 | 0.7182 | 0.71977 | 0.94567 | 0.71946 | 0.72177 | 0.82467
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 0.96328 | 0.96074 | 1.0136 | 0.96311 | 0.96058 | 1.0179 | 0.96243 | 0.95997 | 1.0175 | 0.9637 | 0.96158 | 1.0184 | 0.96145 | 0.95942 | 1.017
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV
SW | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 99.23% | 88.41% | 53.66% | 99.07% | 88.29% | 53.4% | 98.91% | 88.16% | 53.08% | 98.23% | 87.52% | 53.1% | 100.3% | 89.46% | 53.55%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 255.0147 | 282.9043 | 157.768 | 254.6152 | 282.5353 | 156.984 | 254.1975 | 282.1272 | 156.0476 | 252.4486 | 280.0482 | 156.1026 | 257.6465 | 286.2642 | 157.445
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 51.0008 | 56.4808 | 31.4302 | 50.8883 | 56.3713 | 31.3868 | 50.7751 | 56.2594 | 31.4724 | 50.4332 | 55.8685 | 31.209 | 51.4411 | 57.0763 | 31.7498
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 51 | 56.3452 | 29.6195 | 50.8877 | 56.237 | 29.5487 | 50.7746 | 56.127 | 29.4696 | 50.4329 | 55.7546 | 29.3277 | 51.4353 | 56.9043 | 29.8469
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.99998 | 0.9976 | 0.93993 | 0.99999 | 0.99762 | 0.93942 | 0.99999 | 0.99765 | 0.93495 | 0.99999 | 0.99796 | 0.93794 | 0.99989 | 0.99699 | 0.9383
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0462 | 1.0438 | 1.0265 | 1.0455 | 1.0431 | 1.0306 | 1.0449 | 1.0426 | 1.041 | 1.0451 | 1.0431 | 1.031 | 1.0444 | 1.0423 | 1.0399
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 31.59% | 33.93% | 22.73% | 31.54% | 33.89% | 22.67% | 31.5% | 33.84% | 22.52% | 31.29% | 33.62% | 22.55% | 31.87% | 34.28% | 22.7%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141691_1 | TR_LINE 141692_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141692_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141692_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141699_1 | TR_LINE 141691_1
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 241.0394 | 264.2966 | 155.724 | 240.6817 | 263.9652 | 155.2671 | 240.3102 | 263.6003 | 154.2512 | 238.7754 | 261.9014 | 154.4602 | 243.1613 | 267.042 | 155.5207
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 48.1589 | 52.6443 | 31.1053 | 48.057 | 52.5453 | 31.1272 | 47.955 | 52.4452 | 31.1923 | 47.6559 | 52.1648 | 30.9639 | 48.4993 | 52.9184 | 31.4446
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 48.0704 | 52.6442 | 28.6313 | 47.9673 | 52.5452 | 28.5731 | 47.8641 | 52.4451 | 28.5075 | 47.5639 | 52.1648 | 28.364 | 48.4326 | 52.9182 | 28.8645
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.99809 | 1 | 0.92046 | 0.99806 | 1 | 0.91795 | 0.99803 | 1 | 0.91393 | 0.998 | 1 | 0.91603 | 0.99856 | 1 | 0.91795
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0482 | 1.0448 | 1.0484 | 1.0475 | 1.0441 | 1.0522 | 1.0469 | 1.0436 | 1.0614 | 1.0471 | 1.0447 | 1.0522 | 1.0464 | 1.0389 | 1.0612
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV
WB | 6112_Agnes Water 66 kV | % of Rated A | 16.54% | 11.72% | 6.612% | 16.81% | 11.9% | 6.706% | 16.81% | 11.9% | 6.706% | 16.81% | 11.9% | 6.706% | 17.08% | 12.06% | 6.801%
WB | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
WB | 6112_Agnes Water 66 kV | Loading (A) | 46.9844 | 56.4844 | 31.9343 | 47.7328 | 57.3493 | 32.3891 | 47.7535 | 57.3594 | 32.3915 | 47.747 | 57.3541 | 32.3906 | 48.5128 | 58.1387 | 32.8498
WB | 6112_Agnes Water 66 kV | Loading (MVA) | 5.4343 | 6.5406 | 3.7088 | 5.5166 | 6.641 | 3.7608 | 5.5165 | 6.641 | 3.7607 | 5.5166 | 6.641 | 3.7607 | 5.5989 | 6.6936 | 3.8127
WB | 6112_Agnes Water 66 kV | Loading (MW) | 5.353 | 6.4618 | 3.5336 | 5.4359 | 6.5623 | 3.5876 | 5.4358 | 6.5623 | 3.5876 | 5.4358 | 6.5623 | 3.5876 | 5.5187 | 6.6495 | 3.6415
WB | 6112_Agnes Water 66 kV | Power Factor | 0.98501 | 0.98792 | 0.95274 | 0.98532 | 0.98811 | 0.95393 | 0.98534 | 0.98812 | 0.95394 | 0.98534 | 0.98811 | 0.95394 | 0.98565 | 0.99337 | 0.9551
WB | 6112_Agnes Water 66 kV | Rating (A) | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483
WB | 6112_Agnes Water 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 6112_Agnes Water 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0118 | 1.0129 | 1.016 | 1.011 | 1.013 | 1.0157 | 1.0105 | 1.0128 | 1.0156 | 1.0107 | 1.0129 | 1.0157 | 1.0096 | 1.0071 | 1.0153
WB | 6112_Agnes Water 66 kV | Contingency Outage | 7315_Aramara 132 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 785_ISIS 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 8.006% | 7.152% | 4.642% | 8.099% | 7.25% | 4.692% | 8.102% | 7.253% | 4.693% | 8.101% | 7.252% | 4.693% | 8.196% | 7.339% | 4.744%
WB | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 30.2618 | 30.1825 | 17.917 | 30.6126 | 30.5936 | 18.1126 | 30.6242 | 30.6066 | 18.1134 | 30.6206 | 30.6038 | 18.1131 | 30.9811 | 30.9707 | 18.3107
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 7.2369 | 7.1804 | 4.2917 | 7.316 | 7.272 | 4.3378 | 7.3155 | 7.271 | 4.3376 | 7.3157 | 7.2712 | 4.3376 | 7.3945 | 7.3665 | 4.3836
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 7.0718 | 6.8631 | 3.8084 | 7.1557 | 6.9647 | 3.8627 | 7.1556 | 6.9648 | 3.8626 | 7.1557 | 6.9648 | 3.8627 | 7.2395 | 7.0663 | 3.917
WB | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.97719 | 0.95581 | 0.88739 | 0.97808 | 0.95775 | 0.89047 | 0.97815 | 0.95788 | 0.89051 | 0.97813 | 0.95785 | 0.8905 | 0.97903 | 0.95925 | 0.89354
WB | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386
WB | 7188_Gin Gin - Korenan QR 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7188_Gin Gin - Korenan QR 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0415 | 1.037 | 1.0459 | 1.0408 | 1.036 | 1.0456 | 1.0403 | 1.0354 | 1.0455 | 1.0405 | 1.0356 | 1.0456 | 1.0394 | 1.0366 | 1.0452
WB | 7188_Gin Gin - Korenan QR 132 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 785_ISIS 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 96.41% | 109.9% | 68.11% | 95.77% | 110.8% | 68.45% | 96.46% | 111.8% | 68.85% | 96.73% | 112.1% | 69.03% | 99.5% | 115.6% | 70.66%
WB | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 382.7333 | 479.3792 | 242.4636 | 380.2225 | 483.1101 | 243.6805 | 382.9388 | 487.3037 | 245.1069 | 384.001 | 488.8804 | 245.7514 | 394.996 | 504.0775 | 251.5394
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 42.8468 | 53.968 | 27.7166 | 43.0558 | 54.277 | 27.8333 | 43.2759 | 54.5826 | 27.9893 | 43.4224 | 54.7849 | 28.0671 | 44.5222 | 56.2094 | 28.6822
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 42.5926 | 53.9248 | 26.7212 | 42.8062 | 54.2326 | 26.8528 | 43.0389 | 54.5453 | 26.9847 | 43.1883 | 54.7495 | 27.0684 | 44.297 | 56.1863 | 27.743
WB | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.994 | 0.99917 | 0.96398 | 0.99414 | 0.99915 | 0.96467 | 0.99446 | 0.99929 | 0.964 | 0.99454 | 0.99932 | 0.96431 | 0.99488 | 0.99957 | 0.96715
WB | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 6205_East Bundaberg-BUCE 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 6205_East Bundaberg-BUCE 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97896 | 0.98432 | 0.99983 | 0.99024 | 0.98231 | 0.99902 | 0.98823 | 0.97933 | 0.99877 | 0.98884 | 0.97979 | 0.99892 | 0.98565 | 0.97493 | 0.99732
WB | 6205_East Bundaberg-BUCE 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 132.8% | 138.8% | 93.21% | 131.5% | 139.6% | 93.43% | 132% | 140.4% | 93.75% | 131.9% | 140.4% | 93.72% | 135.1% | 144.3% | 95.46%
WB | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 527.0774 | 605.0795 | 331.8182 | 522.0967 | 608.5413 | 332.6174 | 524.2065 | 612.2243 | 333.7494 | 523.6006 | 612.2745 | 333.6313 | 536.4929 | 629.1927 | 339.8423
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 59.537 | 68.8891 | 38.0322 | 59.6425 | 69.1426 | 38.0942 | 59.7683 | 69.3628 | 38.2138 | 59.7332 | 69.4002 | 38.2055 | 61.0296 | 71.008 | 38.8629
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 59.0446 | 68.6728 | 35.4845 | 59.1492 | 68.906 | 35.5656 | 59.291 | 69.1453 | 35.6476 | 59.2463 | 69.1805 | 35.6275 | 60.5811 | 70.8379 | 36.4159
WB | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.98935 | 0.99513 | 0.92894 | 0.9894 | 0.99476 | 0.92955 | 0.98971 | 0.9951 | 0.92873 | 0.98953 | 0.99506 | 0.9284 | 0.99038 | 0.99599 | 0.93297
WB | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 6302_Bundaberg Central - WEBU 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 6302_Bundaberg Central - WEBU 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97969 | 0.98529 | 1.0001 | 0.99096 | 0.98328 | 0.99928 | 0.98896 | 0.98031 | 0.99904 | 0.98956 | 0.98077 | 0.99919 | 0.9864 | 0.97596 | 0.9976
WB | 6302_Bundaberg Central - WEBU 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB | 6366_Gootchie 66 kV | % of Rated A | 2.572% | 43.49% | 18.69% | 372.6% | 46.82% | 20.02% | 48.33% | 46.82% | 20.02% | 372.6% | 46.82% | 20.02% | 49.8% | 48.22% | 20.55%
WB | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 7245_1 | TR_LINE 139374_1 | TR_LINE 50338_1 | TR_LINE 50338_1 | TR_LINE 139374_1 | TR_LINE 50338_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 50338_1 | TR_LINE 50338_1 | TR_LINE 139374_1 | TR_LINE 50338_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 50338_1
WB | 6366_Gootchie 66 kV | Loading (A) | 3.3952 | 72.6292 | 29.7136 | 491.8218 | 78.1891 | 31.832 | 63.7954 | 78.1813 | 31.8319 | 491.8229 | 78.1813 | 31.8319 | 65.7308 | 80.5305 | 32.681
WB | 6366_Gootchie 66 kV | Loading (MVA) | 0.39946 | 10.0857 | 4.3334 | 51.7252 | 10.8125 | 4.6391 | 8.9457 | 10.8115 | 4.6391 | 51.7255 | 10.8115 | 4.6391 | 9.199 | 11.1084 | 4.7603
WB | 6366_Gootchie 66 kV | Loading (MW) | 0.00013459 | 9.9911 | 4.317 | 29.7234 | 10.6976 | 4.6285 | 8.8789 | 10.6967 | 4.6285 | 29.7235 | 10.6967 | 4.6285 | 9.1265 | 10.9852 | 4.7517
WB | 6366_Gootchie 66 kV | Power Factor | 0.00033693 | 0.99057 | 0.9962 | 0.57448 | 0.98933 | 0.99773 | 0.99247 | 0.98933 | 0.99773 | 0.57448 | 0.98933 | 0.99773 | 0.99206 | 0.98886 | 0.99819
WB | 6366_Gootchie 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 6366_Gootchie 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 6366_Gootchie 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0292 | 1.2145 | 1.2757 | 0.9192 | 1.2094 | 1.2748 | 1.2264 | 1.2094 | 1.2748 | 0.9192 | 1.2094 | 1.2748 | 1.224 | 1.2064 | 1.2742
WB | 6366_Gootchie 66 kV | Contingency Outage | M018_Maryborough-Maryborough City 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 95.84% | 95.59% | 73.4% | 96.68% | 96.6% | 73.81% | 97.23% | 97.28% | 74.09% | 97.07% | 97.15% | 74.02% | 98.45% | 98.75% | 74.7%
WB | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_a | TR_LINE 6941_a | TR_LINE 6941_1
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 650.7868 | 698.7535 | 486.6285 | 656.4859 | 706.1553 | 489.3325 | 660.1649 | 711.142 | 491.2408 | 659.0752 | 710.1668 | 490.7491 | 668.4527 | 721.8684 | 495.2715
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 155.9234 | 166.9759 | 116.562 | 157.1995 | 168.6459 | 117.1895 | 158.0479 | 169.762 | 117.6359 | 157.7946 | 169.5478 | 117.5221 | 159.9091 | 172.1425 | 118.5692
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 155.8654 | 166.7213 | 114.7892 | 157.1035 | 168.3269 | 115.4896 | 157.9384 | 169.3859 | 115.9746 | 157.688 | 169.1873 | 115.8459 | 159.737 | 171.6133 | 117.016
WB | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99963 | 0.99848 | 0.98479 | 0.99939 | 0.99811 | 0.98549 | 0.99931 | 0.99778 | 0.98588 | 0.99932 | 0.99787 | 0.98574 | 0.99892 | 0.99693 | 0.9869
WB | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663
WB | 7187_Gin Gin - Bundaberg 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7187_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0479 | 1.0233 | 1.0477 | 1.028 | 1.022 | 1.0475 | 1.0275 | 1.021 | 1.0474 | 1.0276 | 1.0213 | 1.0474 | 1.0259 | 1.0188 | 1.0471
WB | 7187_Gin Gin - Bundaberg 132 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB | 7190_Woolooga-Mungar 132 kV | % of Rated A | 2.525% | 2.375% | 2.569% | 2.526% | 2.375% | 2.569% | 2.526% | 2.375% | 2.569% | 2.526% | 2.375% | 2.569% | 2.525% | 2.375% | 2.569%
WB | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2
WB | 7190_Woolooga-Mungar 132 kV | Loading (A) | 14.2438 | 14.2507 | 13.9233 | 14.2439 | 14.2508 | 13.9234 | 14.2439 | 14.2508 | 13.9234 | 14.2439 | 14.2508 | 13.9234 | 14.2438 | 14.2507 | 13.9234
WB | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 3.4403 | 3.4418 | 3.3634 | 3.4404 | 3.4419 | 3.3634 | 3.4404 | 3.4419 | 3.3634 | 3.4404 | 3.4419 | 3.3634 | 3.4403 | 3.4418 | 3.3634
WB | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 0.077771 | 0.070231 | 0.51921 | 0.077771 | 0.070231 | 0.51921 | 0.077771 | 0.070231 | 0.51921 | 0.077771 | 0.070231 | 0.51921 | 0.077771 | 0.070231 | 0.51921
WB | 7190_Woolooga-Mungar 132 kV | Power Factor | 0.022606 | 0.020405 | 0.15437 | 0.022605 | 0.020405 | 0.15437 | 0.022605 | 0.020405 | 0.15437 | 0.022605 | 0.020405 | 0.15437 | 0.022606 | 0.020405 | 0.15437
WB | 7190_Woolooga-Mungar 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 7190_Woolooga-Mungar 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7190_Woolooga-Mungar 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0564 | 1.0564 | 1.0566 | 1.0564 | 1.0564 | 1.0566 | 1.0564 | 1.0564 | 1.0566 | 1.0564 | 1.0564 | 1.0566 | 1.0564 | 1.0564 | 1.0566
WB | 7190_Woolooga-Mungar 132 kV | Contingency Outage | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV
WB | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 0.3423% | 0.2549% | 1.103% | 0.3423% | 0.2548% | 1.104% | 0.3423% | 0.2547% | 1.104% | 0.3423% | 0.2547% | 1.104% | 0.3422% | 0.2544% | 1.105%
WB | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 3.0329 | 2.5002 | 9.2567 | 3.0327 | 2.4991 | 9.2617 | 3.0326 | 2.4986 | 9.2644 | 3.0327 | 2.4989 | 9.2634 | 3.0321 | 2.4959 | 9.2723
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 0.71697 | 0.58547 | 2.2099 | 0.71644 | 0.58469 | 2.2096 | 0.71622 | 0.58429 | 2.2095 | 0.71646 | 0.58451 | 2.2095 | 0.71503 | 0.58238 | 2.209
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 0.40379 | 0.2341 | 1.9554 | 0.40379 | 0.2341 | 1.9554 | 0.40379 | 0.2341 | 1.9554 | 0.40379 | 0.2341 | 1.9554 | 0.40379 | 0.2341 | 1.9554
WB | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.56318 | 0.39984 | 0.88475 | 0.5636 | 0.40038 | 0.88487 | 0.56377 | 0.40065 | 0.88494 | 0.56358 | 0.4005 | 0.88491 | 0.56471 | 0.40197 | 0.88513
WB | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839
WB | 7204_Bundaberg - Clayton 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7204_Bundaberg - Clayton 132 kV | Min Voltage at Constrained Conductor (pu) | 1.034 | 1.0242 | 1.0442 | 1.0333 | 1.0233 | 1.0435 | 1.033 | 1.0228 | 1.0431 | 1.0333 | 1.0231 | 1.0433 | 1.0314 | 1.0205 | 1.042
WB | 7204_Bundaberg - Clayton 132 kV | Contingency Outage | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 103.3% | 66.46% | 61.64% | 104% | 67.03% | 61.88% | 103.9% | 66.92% | 61.88% | 103.9% | 66.95% | 61.88% | 104.3% | 67.27% | 62.01%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 256.1553 | 263.1918 | 242.2364 | 257.8194 | 265.4496 | 243.2036 | 257.6081 | 265.0123 | 243.1753 | 257.6495 | 265.1127 | 243.179 | 258.6288 | 266.4045 | 243.6999
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 60.0343 | 61.0292 | 57.9483 | 60.3546 | 61.442 | 58.1569 | 60.2512 | 61.2782 | 58.1339 | 60.2811 | 61.304 | 58.1386 | 60.4019 | 61.4473 | 58.2152
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 56.6792 | 58.0114 | 54.8928 | 57.1017 | 58.5068 | 55.1358 | 56.9644 | 58.3535 | 55.0674 | 57.0084 | 58.3547 | 55.0939 | 57.1597 | 58.5087 | 55.1442
WB | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.9362 | 0.94201 | 0.94183 | 0.9381 | 0.94353 | 0.94253 | 0.93739 | 0.9436 | 0.94168 | 0.93768 | 0.94317 | 0.94208 | 0.93817 | 0.94327 | 0.94159
WB | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 7215_Bundaberg - ISIS No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7215_Bundaberg - ISIS No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0251 | 1.0142 | 1.0463 | 1.0239 | 1.0124 | 1.0459 | 1.023 | 1.0113 | 1.0456 | 1.0233 | 1.0114 | 1.0457 | 1.0215 | 1.0089 | 1.0448
WB | 7215_Bundaberg - ISIS No 1 132 kV | Contingency Outage | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV
WB | 7315_Aramara 132 kV | % of Rated A | 39.87% | 44.13% | 13.67% | 40.87% | 45.33% | 14.14% | 41.41% | 45.96% | 14.37% | 41.28% | 45.86% | 14.32% | 42.83% | 46.16% | 15.08%
WB | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1
WB | 7315_Aramara 132 kV | Loading (A) | 435.3921 | 531.7754 | 151.2768 | 446.2512 | 546.1777 | 156.5332 | 452.2283 | 553.8115 | 159.0446 | 450.7285 | 552.5909 | 158.5132 | 467.7565 | 556.188 | 166.9839
WB | 7315_Aramara 132 kV | Loading (MVA) | 101.8564 | 122.6091 | 36.2282 | 104.2165 | 125.6353 | 37.4624 | 105.5118 | 127.2337 | 38.0592 | 105.1866 | 126.9814 | 37.934 | 108.8938 | 128.0121 | 39.9192
WB | 7315_Aramara 132 kV | Loading (MW) | 94.5796 | 112.717 | 34.8348 | 96.5924 | 115.2951 | 35.9579 | 97.697 | 116.6606 | 36.5687 | 97.4174 | 116.4562 | 36.4494 | 100.7086 | 118.4123 | 38.2596
WB | 7315_Aramara 132 kV | Power Factor | 0.92856 | 0.91932 | 0.96153 | 0.92684 | 0.9177 | 0.95983 | 0.92593 | 0.9169 | 0.96083 | 0.92614 | 0.91711 | 0.96085 | 0.92483 | 0.92501 | 0.95842
WB | 7315_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 7315_Aramara 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7315_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0231 | 1.0083 | 1.0475 | 1.0214 | 1.006 | 1.0468 | 1.0204 | 1.0047 | 1.0467 | 1.0206 | 1.0049 | 1.0467 | 1.0181 | 1.0066 | 1.0456
WB | 7315_Aramara 132 kV | Contingency Outage | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV
WB | 7316_Aramara 132 kV | % of Rated A | 39.87% | 44.13% | 13.67% | 40.86% | 45.33% | 14.14% | 41.41% | 45.96% | 14.37% | 41.27% | 45.86% | 14.32% | 42.83% | 46.16% | 15.08%
WB | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1
WB | 7316_Aramara 132 kV | Loading (A) | 435.3839 | 531.7666 | 151.2733 | 446.2429 | 546.1688 | 156.5297 | 452.2199 | 553.8027 | 159.0409 | 450.7202 | 552.582 | 158.5096 | 467.748 | 556.1791 | 166.9801
WB | 7316_Aramara 132 kV | Loading (MVA) | 101.8542 | 122.6066 | 36.2274 | 104.2143 | 125.6327 | 37.4615 | 105.5095 | 127.2311 | 38.0583 | 105.1843 | 126.9788 | 37.9331 | 108.8915 | 128.0095 | 39.9182
WB | 7316_Aramara 132 kV | Loading (MW) | 94.5773 | 112.7143 | 34.8339 | 96.5901 | 115.2924 | 35.957 | 97.6946 | 116.6578 | 36.5678 | 97.4151 | 116.4534 | 36.4485 | 100.7061 | 118.4095 | 38.2587
WB | 7316_Aramara 132 kV | Power Factor | 0.92856 | 0.91932 | 0.96153 | 0.92684 | 0.91769 | 0.95983 | 0.92593 | 0.9169 | 0.96083 | 0.92614 | 0.91711 | 0.96085 | 0.92483 | 0.92501 | 0.95841
WB | 7316_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 7316_Aramara 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7316_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0231 | 1.0083 | 1.0475 | 1.0214 | 1.006 | 1.0468 | 1.0204 | 1.0047 | 1.0467 | 1.0206 | 1.0049 | 1.0467 | 1.0181 | 1.0065 | 1.0456
WB | 7316_Aramara 132 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 103.2% | 66.41% | 61.6% | 103.9% | 66.98% | 61.84% | 103.8% | 66.87% | 61.83% | 103.8% | 66.9% | 61.83% | 104.2% | 67.23% | 61.97%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 255.974 | 263.003 | 242.0689 | 257.6364 | 265.2586 | 243.0352 | 257.4252 | 264.8215 | 243.007 | 257.4666 | 264.9218 | 243.0106 | 258.4448 | 266.2123 | 243.5311
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 59.9916 | 60.9854 | 57.908 | 60.3115 | 61.3978 | 58.1165 | 60.2082 | 61.234 | 58.0934 | 60.238 | 61.2598 | 58.0982 | 60.3587 | 61.403 | 58.1746
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 56.6408 | 57.9719 | 54.856 | 57.0629 | 58.4669 | 55.0987 | 56.9257 | 58.3136 | 55.0304 | 56.9697 | 58.3149 | 55.0569 | 57.1209 | 58.4687 | 55.1072
WB | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.94373 | 0.95015 | 0.94701 | 0.94572 | 0.95182 | 0.94778 | 0.94506 | 0.95186 | 0.94698 | 0.94532 | 0.95148 | 0.94736 | 0.94593 | 0.95175 | 0.94697
WB | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 7328_Bundaberg - ISIS No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7328_Bundaberg - ISIS No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0251 | 1.0142 | 1.0463 | 1.0239 | 1.0124 | 1.0459 | 1.023 | 1.0113 | 1.0456 | 1.0233 | 1.0114 | 1.0457 | 1.0215 | 1.0088 | 1.0448
WB | 7328_Bundaberg - ISIS No 2 132 kV | Contingency Outage | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV
WB | 7329_Maryborough 132 kV | % of Rated A | 90.38% | 99.91% | 51.56% | 91.57% | 100.3% | 52.13% | 92.14% | 101.1% | 52.37% | 92.2% | 101.2% | 52.41% | 94.75% | 104.5% | 53.66%
WB | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1
WB | 7329_Maryborough 132 kV | Loading (A) | 509.7151 | 599.4823 | 279.4729 | 516.482 | 602.0696 | 282.5461 | 519.6902 | 606.3973 | 283.8344 | 519.989 | 607.0303 | 284.0545 | 534.4162 | 627.1728 | 290.8286
WB | 7329_Maryborough 132 kV | Loading (MVA) | 119.0011 | 137.8762 | 66.9948 | 120.4268 | 139.5204 | 67.6971 | 121.0664 | 140.3597 | 67.9918 | 121.1494 | 140.5167 | 68.0468 | 124.2482 | 144.6508 | 69.6168
WB | 7329_Maryborough 132 kV | Loading (MW) | 117.4642 | 134.4705 | 66.892 | 118.7541 | 135.948 | 67.6202 | 119.2924 | 136.6379 | 67.9205 | 119.3649 | 136.7665 | 67.9769 | 122.2799 | 140.3296 | 69.5721
WB | 7329_Maryborough 132 kV | Power Factor | 0.98708 | 0.9753 | 0.99829 | 0.98611 | 0.9744 | 0.99871 | 0.98535 | 0.97348 | 0.9988 | 0.98527 | 0.97331 | 0.99882 | 0.98416 | 0.97013 | 0.99922
WB | 7329_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 7329_Maryborough 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7329_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 0.98736 | 0.96165 | 1.0464 | 0.98523 | 0.96879 | 1.0458 | 0.98382 | 0.96699 | 1.0456 | 0.98389 | 0.96696 | 1.0456 | 0.98034 | 0.96072 | 1.0447
WB | 7329_Maryborough 132 kV | Contingency Outage | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV
WB | 7330_Maryborough 132 kV | % of Rated A | 90.38% | 99.92% | 51.56% | 91.58% | 100.3% | 52.13% | 92.15% | 101.1% | 52.37% | 92.2% | 101.2% | 52.41% | 94.76% | 104.5% | 53.66%
WB | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1
WB | 7330_Maryborough 132 kV | Loading (A) | 509.7273 | 599.5058 | 279.4736 | 516.4948 | 602.0933 | 282.5469 | 519.7034 | 606.4219 | 283.8352 | 520.0023 | 607.055 | 284.0553 | 534.4308 | 627.2012 | 290.8296
WB | 7330_Maryborough 132 kV | Loading (MVA) | 119.0034 | 137.8803 | 66.9945 | 120.4292 | 139.5246 | 67.6968 | 121.0689 | 140.364 | 67.9915 | 121.1518 | 140.5211 | 68.0465 | 124.2508 | 144.6557 | 69.6165
WB | 7330_Maryborough 132 kV | Loading (MW) | 117.4656 | 134.4727 | 66.8917 | 118.7556 | 135.9503 | 67.6199 | 119.294 | 136.6402 | 67.9202 | 119.3664 | 136.7688 | 67.9766 | 122.2815 | 140.3321 | 69.5718
WB | 7330_Maryborough 132 kV | Power Factor | 0.98708 | 0.97529 | 0.99829 | 0.9861 | 0.97438 | 0.99871 | 0.98534 | 0.97347 | 0.9988 | 0.98526 | 0.9733 | 0.99882 | 0.98415 | 0.97011 | 0.99923
WB | 7330_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 7330_Maryborough 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 7330_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 0.98734 | 0.96162 | 1.0464 | 0.98521 | 0.96876 | 1.0458 | 0.9838 | 0.96695 | 1.0456 | 0.98387 | 0.96693 | 1.0456 | 0.98031 | 0.96068 | 1.0447
WB | 7330_Maryborough 132 kV | Contingency Outage | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV
WB | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 66.63% | 15.51% | 7.337% | 73.35% | 15.99% | 7.504% | 21.72% | 15.99% | 7.504% | 73.35% | 15.99% | 7.504% | 22.33% | 16.45% | 7.666%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 165.254 | 61.413 | 28.8337 | 181.9054 | 63.3393 | 29.4926 | 53.8745 | 63.3367 | 29.4925 | 181.9056 | 63.3367 | 29.4926 | 55.3705 | 65.1303 | 30.1274
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 38.8527 | 14.7766 | 6.9644 | 42.6317 | 15.2366 | 7.1235 | 12.9735 | 15.2361 | 7.1235 | 42.6319 | 15.2361 | 7.1235 | 13.3317 | 15.6643 | 7.2767
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 24.852 | 14.6081 | 6.7403 | 26.4485 | 15.0415 | 6.9173 | 12.8903 | 15.0409 | 6.9173 | 26.4485 | 15.0409 | 6.9173 | 13.2336 | 15.444 | 7.0877
WB | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.63374 | 0.98643 | 0.96782 | 0.61386 | 0.98495 | 0.97106 | 0.99168 | 0.98496 | 0.97106 | 0.61386 | 0.98496 | 0.97106 | 0.99069 | 0.98363 | 0.97402
WB | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 764_Woolooga-Kilkivan No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 764_Woolooga-Kilkivan No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0283 | 1.0524 | 1.0559 | 1.0251 | 1.0522 | 1.0559 | 1.0533 | 1.0522 | 1.0559 | 1.0251 | 1.0522 | 1.0559 | 1.0531 | 1.0519 | 1.0558
WB | 764_Woolooga-Kilkivan No 1 132 kV | Contingency Outage | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 66.63% | 15.51% | 7.337% | 73.35% | 15.99% | 7.504% | 21.72% | 15.99% | 7.504% | 73.35% | 15.99% | 7.504% | 22.33% | 16.45% | 7.666%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 165.2529 | 61.4127 | 28.8336 | 181.9044 | 63.3389 | 29.4925 | 53.8742 | 63.3363 | 29.4925 | 181.9046 | 63.3363 | 29.4925 | 55.3702 | 65.1299 | 30.1273
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 38.8525 | 14.7765 | 6.9644 | 42.6314 | 15.2365 | 7.1234 | 12.9734 | 15.236 | 7.1234 | 42.6316 | 15.236 | 7.1234 | 13.3316 | 15.6642 | 7.2767
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 24.8519 | 14.608 | 6.7403 | 26.4484 | 15.0414 | 6.9172 | 12.8902 | 15.0409 | 6.9172 | 26.4484 | 15.0409 | 6.9172 | 13.2336 | 15.4439 | 7.0876
WB | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.63374 | 0.98643 | 0.96782 | 0.61386 | 0.98496 | 0.97105 | 0.99168 | 0.98496 | 0.97105 | 0.61386 | 0.98496 | 0.97105 | 0.99069 | 0.98363 | 0.97402
WB | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 765_Woolooga-Kilkivan No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 765_Woolooga-Kilkivan No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0283 | 1.0524 | 1.0559 | 1.0251 | 1.0522 | 1.0559 | 1.0533 | 1.0522 | 1.0559 | 1.0251 | 1.0522 | 1.0559 | 1.0531 | 1.0519 | 1.0558
WB | 765_Woolooga-Kilkivan No 2 132 kV | Contingency Outage | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | 784_ISIS 132 kV | % of Rated A | 48.59% | 30.99% | 32.21% | 48.39% | 31.35% | 31.93% | 48.37% | 31.56% | 31.75% | 48.38% | 31.38% | 31.85% | 48.6% | 31.95% | 31.69%
WB | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB | 784_ISIS 132 kV | Loading (A) | 120.492 | 122.7258 | 126.6045 | 120.0187 | 124.1657 | 125.4693 | 119.9497 | 124.9814 | 124.7736 | 119.9814 | 124.2825 | 125.1693 | 120.5371 | 126.529 | 124.5525
WB | 784_ISIS 132 kV | Loading (MVA) | 28.1568 | 28.3341 | 30.2589 | 28.0096 | 28.6073 | 29.9677 | 27.9704 | 28.7573 | 29.7949 | 27.983 | 28.6061 | 29.8924 | 28.0564 | 29.0248 | 29.7184
WB | 784_ISIS 132 kV | Loading (MW) | 10.1875 | 7.169 | 24.419 | 9.4027 | 5.9963 | 23.9555 | 8.8015 | 5.2442 | 23.6235 | 9.1176 | 5.557 | 23.7901 | 8.5032 | 4.7839 | 23.4047
WB | 784_ISIS 132 kV | Power Factor | 0.36181 | 0.25302 | 0.807 | 0.33569 | 0.20961 | 0.79937 | 0.31467 | 0.1823 | 0.79287 | 0.32582 | 0.19426 | 0.79586 | 0.30308 | 0.16464 | 0.78755
WB | 784_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 784_ISIS 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 784_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0221 | 1.0098 | 1.0454 | 1.0208 | 1.0077 | 1.0447 | 1.0199 | 1.0064 | 1.0444 | 1.0201 | 1.0067 | 1.0445 | 1.0181 | 1.0033 | 1.0436
WB | 784_ISIS 132 kV | Contingency Outage | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV
WB | 785_ISIS 132 kV | % of Rated A | 48.77% | 31.1% | 32.34% | 48.57% | 31.47% | 32.05% | 48.55% | 31.67% | 31.87% | 48.56% | 31.5% | 31.97% | 48.79% | 32.06% | 31.81%
WB | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB | 785_ISIS 132 kV | Loading (A) | 120.9407 | 123.1707 | 127.0786 | 120.4636 | 124.6102 | 125.9399 | 120.3925 | 125.4251 | 125.242 | 120.4254 | 124.7253 | 125.639 | 120.9962 | 126.9746 | 125.0207
WB | 785_ISIS 132 kV | Loading (MVA) | 28.2592 | 28.4342 | 30.3701 | 28.111 | 28.707 | 30.078 | 28.0711 | 28.8567 | 29.9046 | 28.0841 | 28.7054 | 30.0025 | 28.1606 | 29.1243 | 29.828
WB | 785_ISIS 132 kV | Loading (MW) | 10.2458 | 7.2197 | 24.5162 | 9.4586 | 6.0439 | 24.0513 | 8.8557 | 5.2898 | 23.7182 | 9.1727 | 5.6034 | 23.8854 | 8.5563 | 4.8287 | 23.4989
WB | 785_ISIS 132 kV | Power Factor | 0.36257 | 0.25391 | 0.80725 | 0.33647 | 0.21054 | 0.79963 | 0.31547 | 0.18331 | 0.79313 | 0.32662 | 0.1952 | 0.79611 | 0.30384 | 0.16579 | 0.78781
WB | 785_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 785_ISIS 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 785_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 1.022 | 1.0097 | 1.0453 | 1.0207 | 1.0076 | 1.0446 | 1.0198 | 1.0063 | 1.0444 | 1.02 | 1.0066 | 1.0445 | 1.018 | 1.0032 | 1.0435
WB | 785_ISIS 132 kV | Contingency Outage | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV
WB | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 229.9% | 145.3% | 100.9% | 231.9% | 146.8% | 101.5% | 233.2% | 147.8% | 101.9% | 232.8% | 147.6% | 101.8% | 236.2% | 150.1% | 102.7%
WB | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 112963_1 | TR_LINE 112961_1 | TR_LINE 112961_1 | TR_LINE 112963_1
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 650.671 | 698.6827 | 486.3978 | 656.4044 | 706.0854 | 489.1036 | 660.08 | 711.0722 | 491.0131 | 658.8645 | 710.0972 | 490.5211 | 668.3646 | 721.7984 | 495.0466
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 155.8958 | 165.5317 | 116.5097 | 157.178 | 167.1453 | 117.1377 | 158.027 | 168.2189 | 117.5844 | 157.7556 | 168.0146 | 117.4705 | 158.6143 | 170.5008 | 118.5184
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 155.8406 | 165.4626 | 114.7276 | 157.0841 | 167.0436 | 115.4287 | 157.9198 | 168.0861 | 115.9141 | 157.6585 | 167.8906 | 115.7853 | 158.5779 | 170.2775 | 116.9566
WB | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99965 | 0.99958 | 0.98165 | 0.9994 | 0.99939 | 0.9824 | 0.99932 | 0.99921 | 0.9828 | 0.99938 | 0.99926 | 0.98265 | 0.99977 | 0.99869 | 0.9839
WB | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482
WB | 786_Gin Gin - Bundaberg 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | 786_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0403 | 1.0272 | 1.0462 | 1.0394 | 1.026 | 1.0459 | 1.0391 | 1.0252 | 1.0458 | 1.0393 | 1.0254 | 1.0458 | 1.0295 | 1.0231 | 1.0453
WB | 786_Gin Gin - Bundaberg 132 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 70.9% | 63.45% | 41.01% | 70.55% | 63.11% | 40.79% | 70.34% | 62.94% | 40.67% | 69.74% | 62.42% | 40.38% | 71.08% | 63.67% | 41.05%
WB | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1
WB | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 388.5456 | 367.3562 | 213.6474 | 386.6026 | 365.3817 | 212.4931 | 385.4827 | 364.398 | 211.9135 | 382.1974 | 361.3971 | 210.3764 | 389.535 | 368.6742 | 213.8934
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 45.4086 | 43.0121 | 25.3056 | 45.1848 | 42.7856 | 25.1703 | 45.0572 | 42.6726 | 25.1024 | 44.685 | 42.331 | 24.9226 | 45.5174 | 43.1568 | 25.3338
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 42.3165 | 40.3013 | 24.3417 | 42.1091 | 40.1094 | 24.2194 | 42.0026 | 40.0135 | 24.1582 | 41.6844 | 39.7172 | 23.9936 | 42.4281 | 40.4397 | 24.3742
WB | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.9319 | 0.93698 | 0.96191 | 0.93193 | 0.93745 | 0.96222 | 0.93221 | 0.93768 | 0.96239 | 0.93285 | 0.93825 | 0.96272 | 0.93213 | 0.93704 | 0.96212
WB | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M001_Tarong-Kingaroy East 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M001_Tarong-Kingaroy East 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95345 | 0.96031 | 1.0044 | 0.95388 | 0.96089 | 1.0047 | 0.95422 | 0.96117 | 1.0048 | 0.95523 | 0.96207 | 1.0052 | 0.95317 | 0.95986 | 1.0043
WB | M001_Tarong-Kingaroy East 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 70.9% | 63.44% | 41.01% | 70.54% | 63.1% | 40.78% | 70.34% | 62.93% | 40.67% | 69.74% | 62.41% | 40.38% | 71.08% | 63.67% | 41.05%
WB | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1
WB | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 388.5201 | 367.3345 | 213.6489 | 386.5774 | 365.3603 | 212.4882 | 385.4577 | 364.3772 | 211.9086 | 382.173 | 361.3764 | 210.3716 | 389.5094 | 368.6523 | 213.8883
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 42.3556 | 40.3335 | 24.5317 | 42.1628 | 40.1405 | 24.4061 | 42.0557 | 40.0442 | 24.3433 | 41.7413 | 39.7515 | 24.1768 | 42.4509 | 40.4592 | 24.558
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 40.5788 | 38.7481 | 23.8172 | 40.3887 | 38.5728 | 23.7004 | 40.2922 | 38.4851 | 23.642 | 40.003 | 38.214 | 23.4849 | 40.6815 | 38.8752 | 23.8482
WB | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.95805 | 0.96069 | 0.97087 | 0.95792 | 0.96094 | 0.97108 | 0.95807 | 0.96107 | 0.97119 | 0.95836 | 0.96132 | 0.97138 | 0.95832 | 0.96085 | 0.9711
WB | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M002_Tarong-Kingaroy West 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M002_Tarong-Kingaroy West 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95351 | 0.96037 | 1.0044 | 0.95394 | 0.96094 | 1.0047 | 0.95428 | 0.96122 | 1.0048 | 0.95529 | 0.96212 | 1.0053 | 0.95323 | 0.95992 | 1.0043
WB | M002_Tarong-Kingaroy West 66 kV | Contingency Outage | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV
WB | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 81.35% | 64.77% | 29.02% | 81.3% | 64.72% | 29.01% | 81.27% | 64.7% | 29.01% | 80.49% | 64.1% | 28.77% | 82.77% | 65.94% | 29.52%
WB | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1
WB | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 107.3778 | 108.1634 | 46.1446 | 107.3225 | 108.09 | 46.1303 | 107.2789 | 108.054 | 46.1226 | 106.2473 | 107.0449 | 45.7473 | 109.26 | 110.1162 | 46.9301
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 11.2963 | 11.4604 | 5.2274 | 11.296 | 11.46 | 5.2273 | 11.2958 | 11.4598 | 5.2273 | 11.2036 | 11.3678 | 5.1876 | 11.4832 | 11.6534 | 5.3146
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 11.147 | 11.3058 | 5.1997 | 11.1468 | 11.3056 | 5.1997 | 11.1467 | 11.3055 | 5.1996 | 11.0567 | 11.2157 | 5.1604 | 11.3296 | 11.4931 | 5.2858
WB | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.98678 | 0.98651 | 0.9947 | 0.98679 | 0.98653 | 0.9947 | 0.9868 | 0.98654 | 0.9947 | 0.98689 | 0.98662 | 0.99475 | 0.98663 | 0.98624 | 0.99457
WB | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M003_Kingaroy- Yarraman 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M003_Kingaroy- Yarraman 66 kV | Min Voltage at Constrained Conductor (pu) | 0.92024 | 0.92682 | 0.99095 | 0.92069 | 0.92742 | 0.99125 | 0.92104 | 0.92771 | 0.99141 | 0.92239 | 0.92894 | 0.99195 | 0.91934 | 0.92572 | 0.99063
WB | M003_Kingaroy- Yarraman 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M001_Tarong-Kingaroy East 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB | M004_Murgon-Kingaroy 66 kV | % of Rated A | 7.321% | 5.94% | 4.654% | 7.484% | 5.94% | 4.654% | 7.321% | 5.94% | 4.654% | 7.484% | 5.94% | 4.654% | 7.321% | 5.942% | 4.653%
WB | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB | M004_Murgon-Kingaroy 66 kV | Loading (A) | 12.3731 | 14.1963 | 10.8438 | 12.6483 | 14.1967 | 10.8438 | 12.3731 | 14.1967 | 10.8438 | 12.6482 | 14.1967 | 10.8438 | 12.3723 | 14.201 | 10.8422
WB | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 1.7902 | 2.0019 | 1.5857 | 1.502 | 2.0018 | 1.5857 | 1.7902 | 2.0018 | 1.5857 | 1.502 | 2.0018 | 1.5857 | 1.7892 | 2 | 1.5851
WB | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 1.311 | 1.7033 | 0.82902 | 1.317 | 1.7033 | 0.82902 | 1.311 | 1.7033 | 0.82902 | 1.317 | 1.7033 | 0.82902 | 1.311 | 1.7034 | 0.82903
WB | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.73235 | 0.85082 | 0.52282 | 0.87685 | 0.85089 | 0.52281 | 0.73234 | 0.85089 | 0.52281 | 0.87685 | 0.85089 | 0.52281 | 0.73274 | 0.85169 | 0.52301
WB | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | M004_Murgon-Kingaroy 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M004_Murgon-Kingaroy 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2656 | 1.2336 | 1.2792 | 1.0388 | 1.2335 | 1.2792 | 1.2656 | 1.2335 | 1.2792 | 1.0388 | 1.2335 | 1.2792 | 1.265 | 1.232 | 1.2789
WB | M004_Murgon-Kingaroy 66 kV | Contingency Outage | M011_Kilkivan-Maryborough 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M011_Kilkivan-Maryborough 66 kV | M010_Maryborough - Owanyilla 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M011_Kilkivan-Maryborough 66 kV | M010_Maryborough - Owanyilla 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M011_Kilkivan-Maryborough 66 kV | M011_Kilkivan-Maryborough 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M011_Kilkivan-Maryborough 66 kV
WB | M005 KINGAROY-BOONDOOMA | % of Rated A | 18.78% | 12.86% | 11.45% | 18.77% | 12.85% | 11.44% | 18.76% | 12.85% | 11.44% | 18.74% | 12.83% | 11.44% | 18.79% | 12.87% | 11.45%
WB | M005 KINGAROY-BOONDOOMA | Limiting Line Name | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1
WB | M005 KINGAROY-BOONDOOMA | Loading (A) | 25.1658 | 23.2721 | 20.0339 | 25.1541 | 23.2578 | 20.0275 | 25.1448 | 23.2508 | 20.0243 | 25.1174 | 23.2284 | 20.0158 | 25.1764 | 23.2862 | 20.0362
WB | M005 KINGAROY-BOONDOOMA | Loading (MVA) | 2.7269 | 2.5397 | 2.2918 | 2.7268 | 2.5397 | 2.2918 | 2.7268 | 2.5397 | 2.2918 | 2.7268 | 2.5396 | 2.2918 | 2.7269 | 2.5397 | 2.2918
WB | M005 KINGAROY-BOONDOOMA | Loading (MW) | 2.5641 | 2.3891 | 2.1567 | 2.564 | 2.3891 | 2.1567 | 2.564 | 2.3891 | 2.1567 | 2.564 | 2.389 | 2.1567 | 2.5641 | 2.3891 | 2.1567
WB | M005 KINGAROY-BOONDOOMA | Power Factor | 0.93998 | 0.9404 | 0.94081 | 0.93998 | 0.9404 | 0.94081 | 0.93998 | 0.94041 | 0.94081 | 0.93999 | 0.94041 | 0.94082 | 0.93997 | 0.94039 | 0.94081
WB | M005 KINGAROY-BOONDOOMA | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
WB | M005 KINGAROY-BOONDOOMA | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M005 KINGAROY-BOONDOOMA | Min Voltage at Constrained Conductor (pu) | 0.94786 | 0.95465 | 1.0007 | 0.9483 | 0.95522 | 1.001 | 0.94864 | 0.95551 | 1.0012 | 0.94966 | 0.95642 | 1.0016 | 0.94747 | 0.95408 | 1.0006
WB | M005 KINGAROY-BOONDOOMA | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB | M007_Proston 66 kV | % of Rated A | 9.783% | 9.686% | 5.648% | 11.41% | 9.687% | 5.648% | 9.783% | 9.687% | 5.648% | 11.41% | 9.687% | 5.648% | 9.791% | 9.7% | 5.648%
WB | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7264_1
WB | M007_Proston 66 kV | Loading (A) | 9.6851 | 12.3018 | 6.8338 | 11.2991 | 12.303 | 6.8338 | 9.6855 | 12.303 | 6.8338 | 11.2991 | 12.303 | 6.8338 | 9.6927 | 12.3186 | 6.8345
WB | M007_Proston 66 kV | Loading (MVA) | 1.374 | 1.7303 | 0.99028 | 1.3308 | 1.7303 | 0.99026 | 1.374 | 1.7303 | 0.99027 | 1.3308 | 1.7303 | 0.99027 | 1.3736 | 1.7301 | 0.98991
WB | M007_Proston 66 kV | Loading (MW) | 1.311 | 1.7026 | 0.82868 | 1.3165 | 1.7026 | 0.82868 | 1.311 | 1.7026 | 0.82868 | 1.3165 | 1.7026 | 0.82868 | 1.3111 | 1.7027 | 0.82869
WB | M007_Proston 66 kV | Power Factor | 0.95415 | 0.98156 | 0.83681 | 0.98135 | 0.98156 | 0.83683 | 0.95417 | 0.98156 | 0.83683 | 0.98135 | 0.98156 | 0.83683 | 0.95447 | 0.98154 | 0.83713
WB | M007_Proston 66 kV | Rating (A) | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121
WB | M007_Proston 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M007_Proston 66 kV | Min Voltage at Constrained Conductor (pu) | 1.241 | 1.2235 | 1.2676 | 1.0294 | 1.2234 | 1.2676 | 1.2409 | 1.2234 | 1.2676 | 1.0294 | 1.2234 | 1.2676 | 1.2396 | 1.2219 | 1.267
WB | M007_Proston 66 kV | Contingency Outage | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M010_Maryborough - Owanyilla 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M010_Maryborough - Owanyilla 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV
WB | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 48.28% | 38.72% | 20.15% | 48.29% | 38.72% | 20.15% | 48.29% | 38.72% | 20.15% | 48.29% | 38.72% | 20.15% | 49.36% | 39.6% | 20.54%
WB | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 87.3931 | 97.5634 | 49.3582 | 87.3997 | 97.5735 | 49.3594 | 87.3994 | 97.5732 | 49.3593 | 87.3995 | 97.5732 | 49.3593 | 89.3463 | 99.783 | 50.3208
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 12.7061 | 14.1433 | 7.2428 | 12.7062 | 14.1435 | 7.2428 | 12.7062 | 14.1435 | 7.2428 | 12.7062 | 14.1435 | 7.2428 | 12.9814 | 14.4532 | 7.3822
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 12.6284 | 14.0173 | 7.2324 | 12.6284 | 14.0174 | 7.2324 | 12.6284 | 14.0174 | 7.2324 | 12.6284 | 14.0174 | 7.2324 | 12.8953 | 14.3159 | 7.374
WB | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.99373 | 0.99096 | 0.99857 | 0.99373 | 0.99095 | 0.99857 | 0.99373 | 0.99095 | 0.99857 | 0.99373 | 0.99095 | 0.99857 | 0.99322 | 0.99038 | 0.9989
WB | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245
WB | M008_Kilkivan-Murgon No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M008_Kilkivan-Murgon No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2711 | 1.2673 | 1.2832 | 1.271 | 1.2671 | 1.2831 | 1.271 | 1.2671 | 1.2831 | 1.271 | 1.2671 | 1.2831 | 1.2702 | 1.2662 | 1.2828
WB | M008_Kilkivan-Murgon No 1 66 kV | Contingency Outage | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV
WB | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 48.39% | 37.97% | 20.06% | 48.4% | 37.97% | 20.06% | 48.4% | 37.97% | 20.06% | 48.4% | 37.97% | 20.06% | 49.21% | 38.6% | 20.36%
WB | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 81.7849 | 90.7392 | 46.7443 | 81.7911 | 90.7487 | 46.7454 | 81.7909 | 90.7483 | 46.7453 | 81.7909 | 90.7489 | 46.7453 | 83.1628 | 92.2564 | 47.4491
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 11.7741 | 13.0226 | 6.8472 | 11.7742 | 13.0228 | 6.8472 | 11.7742 | 13.0227 | 6.8472 | 11.7742 | 13.0228 | 6.8472 | 11.9641 | 13.2298 | 6.9488
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 11.7178 | 12.9251 | 6.8258 | 11.7179 | 12.9251 | 6.8258 | 11.7179 | 12.9251 | 6.8258 | 11.7179 | 12.9252 | 6.8258 | 11.9015 | 13.1237 | 6.9303
WB | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.98979 | 0.98762 | 0.99687 | 0.98979 | 0.98762 | 0.99687 | 0.98979 | 0.98762 | 0.99687 | 0.98979 | 0.98762 | 0.99687 | 0.98939 | 0.9872 | 0.99734
WB | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | M009_Kilkivan-Murgon No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M009_Kilkivan-Murgon No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.241 | 1.2336 | 1.2675 | 1.2409 | 1.2335 | 1.2675 | 1.2409 | 1.2335 | 1.2675 | 1.2409 | 1.2335 | 1.2675 | 1.2396 | 1.232 | 1.2669
WB | M009_Kilkivan-Murgon No 2 66 kV | Contingency Outage | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV
WB | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 14.82% | 12.5% | 5.629% | 16.75% | 13.95% | 6.324% | 16.77% | 13.98% | 6.326% | 16.77% | 13.98% | 6.326% | 17.09% | 14.27% | 6.436%
WB | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1
WB | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 36.9073 | 47.7575 | 20.8275 | 41.7153 | 53.3063 | 23.3976 | 41.7617 | 53.3999 | 23.4064 | 41.7586 | 53.3976 | 23.4066 | 42.5621 | 54.5111 | 23.8118
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 4.3129 | 5.5397 | 2.4382 | 4.8641 | 6.2476 | 2.7358 | 4.8644 | 6.2481 | 2.7358 | 4.8644 | 6.2481 | 2.7358 | 4.9424 | 6.3514 | 2.7784
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 4.273 | 5.4682 | 2.4247 | 4.8108 | 6.1564 | 2.7288 | 4.8108 | 6.1566 | 2.7288 | 4.8108 | 6.1566 | 2.7288 | 4.8874 | 6.2556 | 2.7724
WB | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.99073 | 0.98705 | 0.99448 | 0.98899 | 0.98537 | 0.99745 | 0.98896 | 0.98531 | 0.99746 | 0.98896 | 0.98531 | 0.99746 | 0.98883 | 0.98487 | 0.99782
WB | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | M010_Maryborough - Owanyilla 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M010_Maryborough - Owanyilla 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0222 | 1.0147 | 1.024 | 1.02 | 1.0252 | 1.0228 | 1.0189 | 1.0235 | 1.0224 | 1.019 | 1.0236 | 1.0224 | 1.0158 | 1.0193 | 1.0207
WB | M010_Maryborough - Owanyilla 66 kV | Contingency Outage | 6366_Gootchie 66 kV | 6366_Gootchie 66 kV | 7329_Maryborough 132 kV | 6366_Gootchie 66 kV | 6366_Gootchie 66 kV | 7329_Maryborough 132 kV | 6366_Gootchie 66 kV | 6366_Gootchie 66 kV | 7329_Maryborough 132 kV | 6366_Gootchie 66 kV | 6366_Gootchie 66 kV | 7329_Maryborough 132 kV | 6366_Gootchie 66 kV | 6366_Gootchie 66 kV | 7329_Maryborough 132 kV
WB | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 42.53% | 64.1% | 26.9% | 395.1% | 67.89% | 28.41% | 69.68% | 67.88% | 28.41% | 395.1% | 67.88% | 28.41% | 72% | 70.14% | 29.27%
WB | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42253_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42253_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42253_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42253_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42253_1
WB | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 56.1357 | 107.0537 | 42.7755 | 521.5597 | 113.3705 | 45.1745 | 91.9774 | 113.3624 | 45.1744 | 521.5606 | 113.3625 | 45.1744 | 95.0373 | 117.1349 | 46.5408
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 8.0683 | 15.191 | 6.2782 | 54.8884 | 16.0508 | 6.6286 | 13.1394 | 16.0498 | 6.6286 | 54.8886 | 16.0498 | 6.6286 | 13.5588 | 16.5559 | 6.8272
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 7.9858 | 15.0315 | 6.273 | 33.7585 | 15.863 | 6.6262 | 13.0371 | 15.862 | 6.6262 | 33.7586 | 15.862 | 6.6262 | 13.4457 | 16.3515 | 6.8259
WB | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.98976 | 0.9895 | 0.99917 | 0.61495 | 0.9883 | 0.99964 | 0.99221 | 0.9883 | 0.99964 | 0.61495 | 0.9883 | 0.99964 | 0.99165 | 0.98765 | 0.99981
WB | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M011_Kilkivan-Maryborough 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M011_Kilkivan-Maryborough 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2573 | 1.2412 | 1.2758 | 0.92002 | 1.2384 | 1.2749 | 1.2496 | 1.2384 | 1.2749 | 0.92002 | 1.2384 | 1.2749 | 1.2479 | 1.2363 | 1.2742
WB | M011_Kilkivan-Maryborough 66 kV | Contingency Outage | M004_Murgon-Kingaroy 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | M012_Maryborough-Rocky St 66 kV | % of Rated A | 55.01% | 53.64% | 32.81% | 55.2% | 53.89% | 32.81% | 55.23% | 53.23% | 32.81% | 54.94% | 52.95% | 32.67% | 56.26% | 54.3% | 33.38%
WB | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB | M012_Maryborough-Rocky St 66 kV | Loading (A) | 301.4429 | 310.5545 | 170.9395 | 302.5202 | 312.048 | 170.9608 | 302.6661 | 308.1834 | 170.9347 | 301.0606 | 306.609 | 170.2059 | 308.2898 | 314.3956 | 173.8927
WB | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 35.5697 | 36.4341 | 20.051 | 35.6305 | 36.4834 | 20.0376 | 35.6149 | 36.491 | 20.0289 | 35.4303 | 36.3059 | 19.9438 | 36.1716 | 37.0962 | 20.3597
WB | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 35.413 | 36.3119 | 18.8993 | 35.487 | 36.3969 | 18.9377 | 35.4744 | 36.3944 | 18.932 | 35.2841 | 36.2047 | 18.8354 | 36.0343 | 36.9821 | 19.2211
WB | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.99426 | 0.99542 | 0.94064 | 0.99468 | 0.99657 | 0.94323 | 0.99478 | 0.99628 | 0.94336 | 0.99458 | 0.99612 | 0.94255 | 0.99491 | 0.99573 | 0.9421
WB | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M012_Maryborough-Rocky St 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M012_Maryborough-Rocky St 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0281 | 1.0219 | 1.026 | 1.0261 | 1.0181 | 1.0251 | 1.0252 | 1.0313 | 1.0248 | 1.0253 | 1.0314 | 1.0248 | 1.0221 | 1.0276 | 1.024
WB | M012_Maryborough-Rocky St 66 kV | Contingency Outage | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV
WB | M014_Torquay-Pialba 66 kV | % of Rated A | 57.65% | 61.41% | 35.32% | 58.24% | 61.31% | 35.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
WB | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Loading (A) | 350.5353 | 412.706 | 194.6176 | 354.1274 | 412.0018 | 196.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Loading (MVA) | 39.0581 | 44.3773 | 22.4909 | 39.3125 | 44.6605 | 22.6318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Loading (MW) | 38.9763 | 44.3575 | 21.8975 | 39.2407 | 44.6453 | 22.0539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Power Factor | 0.9979 | 0.99955 | 0.9736 | 0.99817 | 0.99966 | 0.97445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 0:00 | 0:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97467 | 0.94058 | 1.0109 | 0.97107 | 0.9482 | 1.0096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
WB | M014_Torquay-SOPI 66 kV | % of Rated A | 0% | 0% | 0% | 0% | 0% | 0% | 58.71% | 61.95% | 35.97% | 59% | 62.27% | 36.12% | 61.08% | 64.79% | 37.13%
WB | M014_Torquay-SOPI 66 kV | Limiting Line Name | 0 | 0 | 0 | 0 | 0 | 0 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB | M014_Torquay-SOPI 66 kV | Loading (A) | 0 | 0 | 0 | 0 | 0 | 0 | 356.9268 | 416.3051 | 198.1707 | 358.7204 | 418.4604 | 199.034 | 371.3712 | 435.3789 | 204.5978
WB | M014_Torquay-SOPI 66 kV | Loading (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 39.5786 | 44.9546 | 22.8948 | 39.7487 | 45.1505 | 22.9903 | 40.8568 | 46.4346 | 23.5713
WB | M014_Torquay-SOPI 66 kV | Loading (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 39.5009 | 44.9446 | 22.211 | 39.6754 | 45.1422 | 22.315 | 40.8007 | 46.4329 | 22.9446
WB | M014_Torquay-SOPI 66 kV | Power Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0.99803 | 0.99977 | 0.97012 | 0.99815 | 0.99981 | 0.97061 | 0.99862 | 0.99996 | 0.9734
WB | M014_Torquay-SOPI 66 kV | Rating (A) | 0 | 0 | 0 | 0 | 0 | 0 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | M014_Torquay-SOPI 66 kV | Time | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 0:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M014_Torquay-SOPI 66 kV | Min Voltage at Constrained Conductor (pu) | 0 | 0 | 0 | 0 | 0 | 0 | 0.96997 | 0.94457 | 1.0106 | 0.96927 | 0.9438 | 1.0104 | 0.96235 | 0.93292 | 1.0078
WB | M014_Torquay-SOPI 66 kV | Contingency Outage | 0% | 0% | 0% | 0% | 0% | 0% | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.89% | 1.491% | 1.575% | 1.887% | 1.494% | 1.573% | 1.885% | 1.499% | 1.573% | 1.885% | 1.499% | 1.573% | 1.88% | 1.499% | 1.572%
WB | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1
WB | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.495 | 2.4907 | 2.5038 | 2.4903 | 2.4955 | 2.5016 | 2.488 | 2.5036 | 2.5017 | 2.4883 | 2.5037 | 2.5017 | 2.4812 | 2.5035 | 2.4989
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 0.2944 | 0.2934 | 0.2965 | 0.29331 | 0.29452 | 0.29598 | 0.29277 | 0.29644 | 0.29599 | 0.29284 | 0.29647 | 0.29599 | 0.29116 | 0.29641 | 0.29533
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 0.0011253 | 0.0011215 | 0.0011333 | 0.0011211 | 0.0011258 | 0.0011313 | 0.0011191 | 0.0011331 | 0.0011314 | 0.0011193 | 0.0011332 | 0.0011314 | 0.0011129 | 0.001133 | 0.0011289
WB | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224
WB | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M015_Maryborough-Howard No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M015_Maryborough-Howard No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0322 | 1.0305 | 1.0359 | 1.0303 | 1.0324 | 1.035 | 1.0294 | 1.0358 | 1.035 | 1.0295 | 1.0358 | 1.035 | 1.0265 | 1.0357 | 1.0339
WB | M015_Maryborough-Howard No 1 66 kV | Contingency Outage | M018_Maryborough-Maryborough City 66 kV | M020_Maryborough-Torquay 66 kV | M047_Mount Rawdon Tee 66 kV | M018_Maryborough-Maryborough City 66 kV | M027_ISIS - Childers 66 kV | M047_Mount Rawdon Tee 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M047_Mount Rawdon Tee 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M047_Mount Rawdon Tee 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M041_West Bundaberg-Meadowvale 66 kV
WB | M016_Maryborough-Howard No 2 66 kV | % of Rated A | 3.782% | 2.968% | 3.172% | 3.774% | 2.999% | 3.169% | 3.77% | 2.994% | 3.169% | 3.77% | 2.994% | 3.169% | 3.758% | 2.982% | 3.165%
WB | M016_Maryborough-Howard No 2 66 kV | Limiting Line Name | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2
WB | M016_Maryborough-Howard No 2 66 kV | Loading (A) | 4.9921 | 4.9566 | 5.0427 | 4.9816 | 5.0087 | 5.0382 | 4.9763 | 5.0004 | 5.0382 | 4.9767 | 5.0006 | 5.0383 | 4.9612 | 4.9797 | 5.0323
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MVA) | 0.5841 | 0.57583 | 0.59601 | 0.58166 | 0.588 | 0.59494 | 0.58043 | 0.58606 | 0.59495 | 0.58051 | 0.58609 | 0.59497 | 0.57689 | 0.5812 | 0.59356
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MW) | 0.00011306 | 0.00011148 | 0.00011534 | 0.00011259 | 0.00011384 | 0.00011513 | 0.00011235 | 0.00011346 | 0.00011513 | 0.00011237 | 0.00011347 | 0.00011514 | 0.00011167 | 0.00011252 | 0.00011487
WB | M016_Maryborough-Howard No 2 66 kV | Power Factor | 0.00018431 | 0.00018433 | 0.00018426 | 0.00018431 | 0.00018434 | 0.00018426 | 0.00018431 | 0.00018434 | 0.00018425 | 0.00018431 | 0.00018434 | 0.00018426 | 0.00018432 | 0.00018435 | 0.00018426
WB | M016_Maryborough-Howard No 2 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M016_Maryborough-Howard No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M016_Maryborough-Howard No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0235 | 1.0163 | 1.0339 | 1.0214 | 1.0269 | 1.033 | 1.0203 | 1.0252 | 1.033 | 1.0204 | 1.0253 | 1.033 | 1.0172 | 1.021 | 1.0318
WB | M016_Maryborough-Howard No 2 66 kV | Contingency Outage | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV
WB | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 35.24% | 36.6% | 19.5% | 35.46% | 36.35% | 19.59% | 35.64% | 36.57% | 19.65% | 35.49% | 36.42% | 19.59% | 36.47% | 37.48% | 20.01%
WB | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 39141_1 | TR_LINE 7924_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 7924_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 7924_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 7924_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 7924_1 | TR_LINE 39141_1
WB | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 193.0969 | 211.8879 | 101.6205 | 194.3277 | 210.4945 | 102.0477 | 195.3078 | 211.712 | 102.3946 | 194.501 | 210.8559 | 102.043 | 199.8703 | 217.0179 | 104.2388
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 22.3097 | 24.266 | 11.9627 | 22.3972 | 24.3613 | 12.0002 | 22.4848 | 24.4583 | 12.0411 | 22.3972 | 24.3621 | 12.0004 | 22.9241 | 24.9433 | 12.2421
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 22.3058 | 24.2653 | 11.5233 | 22.3944 | 24.3601 | 11.5686 | 22.4827 | 24.4565 | 11.614 | 22.3946 | 24.3607 | 11.5686 | 22.9238 | 24.9372 | 11.8405
WB | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.99982 | 0.99997 | 0.96326 | 0.99987 | 0.99995 | 0.96403 | 0.99991 | 0.99992 | 0.96453 | 0.99988 | 0.99994 | 0.96402 | 0.99999 | 0.99976 | 0.9672
WB | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M017_Rocky St - Maryborough City 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M017_Rocky St - Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0107 | 0.99923 | 1.0298 | 1.0082 | 1.0098 | 1.0287 | 1.0071 | 1.008 | 1.0287 | 1.0073 | 1.0081 | 1.0287 | 1.0033 | 1.0027 | 1.0274
WB | M017_Rocky St - Maryborough City 66 kV | Contingency Outage | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV
WB | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 66.07% | 65.04% | 39.86% | 66.48% | 64.62% | 40.02% | 66.54% | 64.74% | 40.01% | 66.22% | 64.45% | 39.86% | 67.8% | 66.09% | 40.62%
WB | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 70964_2 | TR_LINE 122162_1
WB | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 362.0461 | 376.574 | 207.6907 | 364.3076 | 374.1283 | 208.5047 | 364.6203 | 374.8428 | 208.4513 | 362.8926 | 373.1761 | 207.6569 | 371.5462 | 382.6453 | 211.6405
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 41.8363 | 43.1355 | 24.5334 | 41.9953 | 43.3086 | 24.6073 | 41.9841 | 43.3139 | 24.6012 | 41.7949 | 43.1259 | 24.5079 | 42.6219 | 43.9908 | 24.9479
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 41.8361 | 43.1249 | 24.2589 | 41.9922 | 43.2924 | 24.3634 | 41.9803 | 43.2962 | 24.3578 | 41.7919 | 43.1091 | 24.2606 | 42.617 | 43.9683 | 24.7113
WB | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.99999 | 0.99975 | 0.98775 | 0.99993 | 0.99963 | 0.98908 | 0.99991 | 0.99959 | 0.9891 | 0.99993 | 0.99961 | 0.9889 | 0.99989 | 0.99949 | 0.9895
WB | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M018_Maryborough-Maryborough City 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M018_Maryborough-Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0108 | 1.002 | 1.0312 | 1.0083 | 1.0126 | 1.0301 | 1.0072 | 1.0108 | 1.0302 | 1.0074 | 1.0109 | 1.0302 | 1.0034 | 1.0056 | 1.0289
WB | M018_Maryborough-Maryborough City 66 kV | Contingency Outage | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV
WB | M019_Maryborough City-Walkers 66 kV | % of Rated A | 0.277% | 0.2746% | 1.677% | 0.2763% | 0.2653% | 1.678% | 0.2759% | 0.2624% | 1.679% | 0.2759% | 0.2624% | 1.679% | 0.2784% | 0.2606% | 1.681%
WB | M019_Maryborough City-Walkers 66 kV | Limiting Line Name | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1
WB | M019_Maryborough City-Walkers 66 kV | Loading (A) | 1.5182 | 1.59 | 8.735 | 1.5143 | 1.536 | 8.7434 | 1.5117 | 1.5193 | 8.746 | 1.5118 | 1.5192 | 8.746 | 1.5257 | 1.5086 | 8.7577
WB | M019_Maryborough City-Walkers 66 kV | Loading (MVA) | 0.17632 | 0.1839 | 1.021 | 0.1754 | 0.18047 | 1.0207 | 0.1748 | 0.17658 | 1.0206 | 0.17483 | 0.17656 | 1.0206 | 0.17806 | 0.17412 | 1.0202
WB | M019_Maryborough City-Walkers 66 kV | Loading (MW) | 0.014922 | 0.015563 | 0.76372 | 0.014844 | 0.015273 | 0.76368 | 0.014793 | 0.014943 | 0.76367 | 0.014795 | 0.014942 | 0.76367 | 0.015068 | 0.014736 | 0.76362
WB | M019_Maryborough City-Walkers 66 kV | Power Factor | 0.084627 | 0.084627 | 0.74803 | 0.084627 | 0.084627 | 0.74821 | 0.084627 | 0.084627 | 0.74827 | 0.084627 | 0.084627 | 0.74827 | 0.084627 | 0.084633 | 0.74853
WB | M019_Maryborough City-Walkers 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M019_Maryborough City-Walkers 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M019_Maryborough City-Walkers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0159 | 1.0118 | 1.0225 | 1.0133 | 1.0278 | 1.0212 | 1.0116 | 1.0167 | 1.0208 | 1.0116 | 1.0166 | 1.0208 | 1.0209 | 1.0096 | 1.019
WB | M019_Maryborough City-Walkers 66 kV | Contingency Outage | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7329_Maryborough 132 kV | 7330_Maryborough 132 kV | M027_ISIS - Childers 66 kV | 7329_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7329_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7329_Maryborough 132 kV | 7330_Maryborough 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | 7329_Maryborough 132 kV
WB | M020_Maryborough-Torquay 66 kV | % of Rated A | 95.52% | 107.7% | 58.33% | 96.6% | 107.6% | 58.85% | 97.43% | 108.9% | 59.3% | 97.88% | 109.4% | 59.54% | 101.3% | 113.7% | 61.28%
WB | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1
WB | M020_Maryborough-Torquay 66 kV | Loading (A) | 580.7616 | 723.4591 | 321.3883 | 587.3569 | 723.0748 | 324.2361 | 592.3863 | 731.4885 | 326.7611 | 595.0877 | 734.8813 | 328.0736 | 615.8584 | 764.1431 | 337.652
WB | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 64.7154 | 77.7996 | 37.4685 | 65.2085 | 78.3882 | 37.7591 | 65.6928 | 78.9977 | 38.0793 | 65.9447 | 79.2994 | 38.228 | 67.7597 | 81.5072 | 39.2627
WB | M020_Maryborough-Torquay 66 kV | Loading (MW) | 64.6976 | 77.6766 | 37.4122 | 65.1865 | 78.2549 | 37.7082 | 65.6724 | 78.8475 | 38.0041 | 65.9222 | 79.1429 | 38.1556 | 67.7254 | 81.3109 | 39.2075
WB | M020_Maryborough-Torquay 66 kV | Power Factor | 0.99972 | 0.99842 | 0.99849 | 0.99966 | 0.9983 | 0.99865 | 0.99969 | 0.9981 | 0.99802 | 0.99966 | 0.99803 | 0.9981 | 0.99949 | 0.99759 | 0.99859
WB | M020_Maryborough-Torquay 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | M020_Maryborough-Torquay 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M020_Maryborough-Torquay 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97471 | 0.94062 | 1.0198 | 0.9711 | 0.94824 | 1.0187 | 0.97001 | 0.94462 | 1.0194 | 0.96931 | 0.94385 | 1.0193 | 0.96239 | 0.93297 | 1.0172
WB | M020_Maryborough-Torquay 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | % of Rated A | 56.16% | 58.59% | 35.08% | 56.67% | 58.32% | 35.33% | 57.11% | 58.83% | 35.64% | 57.37% | 59.1% | 35.8% | 59.24% | 61.15% | 36.74%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Limiting Line Name | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (A) | 339.7713 | 391.4074 | 191.8771 | 342.8495 | 389.558 | 193.2588 | 345.5365 | 392.9675 | 194.9752 | 347.066 | 394.7787 | 195.8046 | 358.4105 | 408.4888 | 200.9602
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MVA) | 39.0121 | 44.2918 | 22.5697 | 39.2745 | 44.5753 | 22.7102 | 39.5268 | 44.8598 | 22.9233 | 39.6966 | 45.0534 | 23.0193 | 40.7936 | 46.3195 | 23.5863
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MW) | 38.9194 | 44.2594 | 21.8825 | 39.1802 | 44.5431 | 22.0387 | 39.4386 | 44.8341 | 22.2003 | 39.6119 | 45.03 | 22.3041 | 40.731 | 46.3052 | 22.9321
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Power Factor | 0.99727 | 0.99902 | 0.969 | 0.99723 | 0.99903 | 0.96988 | 0.99741 | 0.99921 | 0.96788 | 0.99751 | 0.99927 | 0.96835 | 0.99815 | 0.99952 | 0.97169
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0028 | 0.98781 | 1.0286 | 1.0004 | 0.99888 | 1.0276 | 0.99899 | 0.99648 | 1.0281 | 0.99885 | 0.99617 | 1.0281 | 0.99384 | 0.98966 | 1.0263
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Contingency Outage | M014_Torquay-Pialba 66 kV | M014_Torquay-Pialba 66 kV | M020_Maryborough-Torquay 66 kV | M014_Torquay-Pialba 66 kV | M014_Torquay-Pialba 66 kV | M020_Maryborough-Torquay 66 kV | M014_Torquay-Pialba 66 kV | M014_Torquay-Pialba 66 kV | M020_Maryborough-Torquay 66 kV | M014_Torquay-Pialba 66 kV | M014_Torquay-Pialba 66 kV | M020_Maryborough-Torquay 66 kV | M014_Torquay-Pialba 66 kV | M014_Torquay-Pialba 66 kV | M020_Maryborough-Torquay 66 kV
WB | M022_Howard - ISIS 66 kV | % of Rated A | 13.91% | 18.36% | 8.208% | 15.61% | 20.66% | 9.215% | 15.73% | 20.84% | 9.284% | 15.74% | 20.84% | 9.283% | 16.09% | 21.26% | 9.496%
WB | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB | M022_Howard - ISIS 66 kV | Loading (A) | 76.2102 | 106.3232 | 42.764 | 85.5649 | 119.6037 | 48.0119 | 86.2093 | 120.6358 | 48.3705 | 86.252 | 120.6511 | 48.3647 | 88.179 | 123.0958 | 49.4731
WB | M022_Howard - ISIS 66 kV | Loading (MVA) | 8.7768 | 12.2326 | 4.9539 | 9.8558 | 13.7682 | 5.5526 | 9.9338 | 13.8608 | 5.5926 | 9.9287 | 13.8609 | 5.5926 | 10.1467 | 14.1676 | 5.7126
WB | M022_Howard - ISIS 66 kV | Loading (MW) | 8.6564 | 11.9814 | 4.9114 | 9.7032 | 13.4382 | 5.5026 | 9.774 | 13.534 | 5.542 | 9.7732 | 13.534 | 5.542 | 9.9831 | 13.8253 | 5.6604
WB | M022_Howard - ISIS 66 kV | Power Factor | 0.98412 | 0.97912 | 0.98895 | 0.98296 | 0.97603 | 0.98822 | 0.98236 | 0.97643 | 0.98817 | 0.98283 | 0.97642 | 0.98817 | 0.98249 | 0.97584 | 0.98801
WB | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M022_Howard - ISIS 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M022_Howard - ISIS 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0051 | 1.0004 | 1.0134 | 1.0041 | 0.9994 | 1.0117 | 1.0045 | 0.99736 | 1.0114 | 1.0034 | 0.99724 | 1.0115 | 1.0028 | 0.99879 | 1.0101
WB | M022_Howard - ISIS 66 kV | Contingency Outage | 785_ISIS 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | 6366_Gootchie 66 kV | 7315_Aramara 132 kV | M036_Bundaberg-South Bundaberg 66 kV | M012_Maryborough-Rocky St 66 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7315_Aramara 132 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 30.02% | 32.14% | 17.9% | 30.13% | 31.87% | 17.92% | 30.28% | 32.12% | 17.96% | 30.3% | 32.15% | 17.97% | 31.28% | 33.34% | 18.38%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 181.6317 | 214.6781 | 97.9177 | 182.2662 | 212.8733 | 98.0025 | 183.1845 | 214.5517 | 98.2685 | 183.3166 | 214.7348 | 98.2822 | 189.2426 | 222.7175 | 100.5259
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 20.1224 | 22.904 | 11.3016 | 20.1147 | 22.895 | 11.2964 | 20.1932 | 22.982 | 11.3404 | 20.1917 | 22.9806 | 11.3396 | 20.6867 | 23.5438 | 11.5662
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 19.7363 | 22.6152 | 10.3691 | 19.7371 | 22.6135 | 10.3691 | 19.8211 | 22.7107 | 10.4129 | 19.8212 | 22.711 | 10.4129 | 20.3249 | 23.2904 | 10.6761
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.9808 | 0.98737 | 0.91749 | 0.98121 | 0.98769 | 0.91792 | 0.98156 | 0.98818 | 0.91821 | 0.98164 | 0.98825 | 0.91828 | 0.98249 | 0.98922 | 0.92305
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Min Voltage at Constrained Conductor (pu) | 0.96912 | 0.93327 | 1.0097 | 0.96537 | 0.94081 | 1.0083 | 0.96428 | 0.937 | 1.0095 | 0.96351 | 0.93615 | 1.0093 | 0.95622 | 0.92471 | 1.0065
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 56.46% | 37.74% | 27.14% | 55.19% | 37.36% | 26.97% | 54.92% | 37.23% | 26.97% | 54.01% | 36.62% | 26.59% | 54.94% | 37.22% | 26.98%
WB | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 74.5325 | 66.8038 | 46.1435 | 72.8452 | 66.1204 | 45.8507 | 72.4893 | 65.9024 | 45.8429 | 71.2987 | 64.8184 | 45.2091 | 72.5194 | 65.8713 | 45.8628
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 8.4241 | 7.6438 | 5.2913 | 8.3272 | 7.5783 | 5.2605 | 8.2796 | 7.5427 | 5.2669 | 8.1527 | 7.4227 | 5.1962 | 8.279 | 7.5441 | 5.2634
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 8.2698 | 7.4339 | 4.732 | 8.1682 | 7.3498 | 4.676 | 8.0873 | 7.2788 | 4.6285 | 7.9696 | 7.1687 | 4.5715 | 8.0876 | 7.2783 | 4.6286
WB | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.98169 | 0.97254 | 0.8943 | 0.9809 | 0.96986 | 0.8889 | 0.97678 | 0.96502 | 0.87879 | 0.97754 | 0.96578 | 0.87978 | 0.97687 | 0.96478 | 0.8794
WB | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | M024_Gayndah - Mundubbera 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M024_Gayndah - Mundubbera 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9699 | 0.98502 | 0.99603 | 0.98168 | 0.98712 | 0.99682 | 0.98145 | 0.98623 | 0.99863 | 0.98275 | 0.98695 | 0.99908 | 0.98095 | 0.98692 | 0.9975
WB | M024_Gayndah - Mundubbera 66 kV | Contingency Outage | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M028_Childers - Gayndah 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M012_Maryborough-Rocky St 66 kV | M028_Childers - Gayndah 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M028_Childers - Gayndah 66 kV | M035_Bundaberg-South Kolan No 2 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV
WB | M025_Eidsvold 66 kV | % of Rated A | 14.86% | 10.77% | 5.767% | 14.68% | 10.76% | 5.766% | 14.68% | 10.76% | 5.763% | 13.83% | 10.15% | 5.466% | 14.69% | 10.75% | 5.735%
WB | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1
WB | M025_Eidsvold 66 kV | Loading (A) | 15.9 | 14.8676 | 7.6119 | 15.704 | 14.8432 | 7.6108 | 15.7055 | 14.8553 | 7.6067 | 14.7937 | 14.0027 | 7.2156 | 15.7139 | 14.8392 | 7.5708
WB | M025_Eidsvold 66 kV | Loading (MVA) | 1.742 | 1.6565 | 0.86114 | 1.742 | 1.6576 | 0.86116 | 1.742 | 1.6576 | 0.86123 | 1.6439 | 1.5643 | 0.81689 | 1.742 | 1.657 | 0.86197
WB | M025_Eidsvold 66 kV | Loading (MW) | 1.7278 | 1.6437 | 0.8414 | 1.7277 | 1.6442 | 0.8414 | 1.7277 | 1.6442 | 0.84139 | 1.631 | 1.5522 | 0.79437 | 1.7277 | 1.644 | 0.84127
WB | M025_Eidsvold 66 kV | Power Factor | 0.99017 | 0.99073 | 0.97708 | 0.99015 | 0.99041 | 0.97706 | 0.99015 | 0.9904 | 0.97697 | 0.99058 | 0.99079 | 0.97243 | 0.99015 | 0.99059 | 0.97598
WB | M025_Eidsvold 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | M025_Eidsvold 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M025_Eidsvold 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95838 | 0.97467 | 0.98959 | 0.97037 | 0.97687 | 0.98975 | 0.97028 | 0.97609 | 0.99038 | 0.97207 | 0.97726 | 0.99031 | 0.96977 | 0.9768 | 0.99593
WB | M025_Eidsvold 66 kV | Contingency Outage | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M036_Bundaberg-South Bundaberg 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M012_Maryborough-Rocky St 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M035_Bundaberg-South Kolan No 2 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV
WB | M026_ISIS - Bundaberg 66 kV | % of Rated A | 13.14% | 16.29% | 6.867% | 13.13% | 16.28% | 6.873% | 13.11% | 16.26% | 6.867% | 13.12% | 16.26% | 6.866% | 13.53% | 16.74% | 7.08%
WB | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2
WB | M026_ISIS - Bundaberg 66 kV | Loading (A) | 17.346 | 27.1998 | 10.9191 | 17.3379 | 27.1865 | 10.9281 | 17.3032 | 27.1504 | 10.9189 | 17.3207 | 27.1536 | 10.9177 | 17.864 | 27.9568 | 11.2575
WB | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 2.0116 | 3.1521 | 1.271 | 2.0116 | 3.152 | 1.2709 | 2.0085 | 3.1445 | 1.2695 | 2.0084 | 3.1445 | 1.2695 | 2.0707 | 3.2436 | 1.3074
WB | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 2.0087 | 3.151 | 1.2531 | 2.0087 | 3.1509 | 1.2531 | 2.0056 | 3.1432 | 1.2519 | 2.0056 | 3.1432 | 1.2519 | 2.0684 | 3.2418 | 1.2911
WB | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.99855 | 0.99956 | 0.98597 | 0.99854 | 0.99956 | 0.98605 | 0.99856 | 0.99952 | 0.98613 | 0.99858 | 0.99952 | 0.98612 | 0.9989 | 0.99938 | 0.98755
WB | M026_ISIS - Bundaberg 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M026_ISIS - Bundaberg 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M026_ISIS - Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0143 | 1.0135 | 1.0181 | 1.0148 | 1.014 | 1.0172 | 1.0152 | 1.0129 | 1.017 | 1.0142 | 1.0128 | 1.0171 | 1.0138 | 1.0147 | 1.0158
WB | M026_ISIS - Bundaberg 66 kV | Contingency Outage | 785_ISIS 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7315_Aramara 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M012_Maryborough-Rocky St 66 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7315_Aramara 132 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB | M026b_FORMER_ISIS - Bundaberg 66kV | % of Rated A | 0.2426% | 0.2228% | 0.274% | 0.2436% | 0.2227% | 0.2738% | 0.2436% | 0.2228% | 0.2737% | 0.2436% | 0.2228% | 0.2737% | 0.2434% | 0.2225% | 0.2748%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Limiting Line Name | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (A) | 1.0652 | 1.0693 | 1.0657 | 1.0692 | 1.069 | 1.065 | 1.0695 | 1.0695 | 1.0647 | 1.0694 | 1.0695 | 1.0649 | 1.0687 | 1.0678 | 1.0691
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MVA) | 0.12248 | 0.12343 | 0.12259 | 0.12341 | 0.12336 | 0.12244 | 0.12348 | 0.12348 | 0.12236 | 0.12345 | 0.12348 | 0.1224 | 0.12328 | 0.12308 | 0.12339
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MW) | 1.9218e-06 | 1.9367e-06 | 1.9235e-06 | 1.9364e-06 | 1.9355e-06 | 1.9212e-06 | 1.9375e-06 | 1.9374e-06 | 1.9198e-06 | 1.937e-06 | 1.9375e-06 | 1.9205e-06 | 1.9344e-06 | 1.9312e-06 | 1.936e-06
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Power Factor | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Min Voltage at Constrained Conductor (pu) | 1.0059 | 1.0098 | 1.0063 | 1.0097 | 1.0094 | 1.0057 | 1.0099 | 1.0099 | 1.0053 | 1.0098 | 1.01 | 1.0055 | 1.0091 | 1.0083 | 1.0096
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Contingency Outage | SOBU-BARG-1_SOBU-Bargara-1 66 kV | M026_ISIS - Bundaberg 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | M041_West Bundaberg-Meadowvale 66 kV | M030_Farnsfield - Childers 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | M029_Bundaberg - Farnsfield 66 kV | M022_Howard - ISIS 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | M041_West Bundaberg-Meadowvale 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | M042_Meadowvale-Gooburrum 66 kV | M027_ISIS - Childers 66 kV | M041_West Bundaberg-Meadowvale 66 kV
WB | M027_ISIS - Childers 66 kV | % of Rated A | 57.62% | 60.42% | 43.04% | 57.59% | 60.38% | 43.08% | 57.56% | 60.46% | 43.09% | 57.31% | 60.13% | 42.9% | 58.55% | 61.36% | 43.81%
WB | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1
WB | M027_ISIS - Childers 66 kV | Loading (A) | 148.6487 | 160.1056 | 100.7183 | 148.5697 | 160.0188 | 100.8172 | 148.4986 | 160.2138 | 100.8407 | 147.8569 | 159.3504 | 100.3965 | 151.0478 | 162.6015 | 102.5266
WB | M027_ISIS - Childers 66 kV | Loading (MVA) | 17.0513 | 18.351 | 11.6413 | 17.0506 | 18.35 | 11.6421 | 17.0499 | 18.3521 | 11.6422 | 16.9595 | 18.2525 | 11.5928 | 17.315 | 18.656 | 11.8213
WB | M027_ISIS - Childers 66 kV | Loading (MW) | 16.7858 | 18.0075 | 11.5832 | 16.7857 | 18.0073 | 11.5833 | 16.7856 | 18.0077 | 11.5833 | 16.6972 | 17.9119 | 11.535 | 17.0336 | 18.2946 | 11.755
WB | M027_ISIS - Childers 66 kV | Power Factor | 0.98443 | 0.98128 | 0.995 | 0.98446 | 0.98133 | 0.99494 | 0.9845 | 0.98123 | 0.99493 | 0.98453 | 0.98134 | 0.99501 | 0.98375 | 0.98063 | 0.99438
WB | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | M027_ISIS - Childers 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M027_ISIS - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0018 | 1.0009 | 1.0101 | 1.0023 | 1.0014 | 1.0092 | 1.0028 | 1.0003 | 1.0089 | 1.0018 | 1.0003 | 1.0091 | 1.0011 | 1.0019 | 1.0076
WB | M027_ISIS - Childers 66 kV | Contingency Outage | 785_ISIS 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7315_Aramara 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M012_Maryborough-Rocky St 66 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7315_Aramara 132 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB | M028_GAYN TEE DEGI FDR 66kV | % of Rated A | 25.85% | 23.11% | 14.82% | 26.4% | 23.81% | 15.14% | 27.14% | 24.63% | 15.56% | 26.76% | 24.28% | 15.39% | 27.18% | 24.33% | 15.55%
WB | M028_GAYN TEE DEGI FDR 66kV | Limiting Line Name | TR_LINE 160969_1 | TR_LINE 12103276_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 160969_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 160969_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 12103276_1 | TR_LINE 12103276_2(New M028) | TR_LINE 160969_1 | TR_LINE 103820347_1 | TR_LINE 12103276_2(New M028)
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (A) | 141.6793 | 133.8157 | 77.2244 | 144.6811 | 137.8411 | 78.8862 | 148.7232 | 142.6332 | 81.0581 | 146.6196 | 140.5582 | 80.1894 | 148.952 | 140.8594 | 81.0112
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MVA) | 16.111 | 15.3675 | 9.0438 | 16.4194 | 15.6696 | 9.2317 | 16.8505 | 16.1755 | 9.4843 | 16.6263 | 16.0717 | 9.3836 | 16.8507 | 16.2709 | 9.4707
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MW) | 16.1053 | 15.3672 | 8.7109 | 16.4163 | 15.6695 | 8.9117 | 16.8482 | 16.1753 | 9.1683 | 16.6243 | 16.0715 | 9.0615 | 16.8494 | 16.2709 | 9.1669
WB | M028_GAYN TEE DEGI FDR 66kV | Power Factor | 0.99965 | 0.99998 | 0.96319 | 0.99981 | 0.99999 | 0.96534 | 0.99986 | 0.99999 | 0.96669 | 0.99988 | 0.99999 | 0.96568 | 0.99992 | 1 | 0.96792
WB | M028_GAYN TEE DEGI FDR 66kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M028_GAYN TEE DEGI FDR 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M028_GAYN TEE DEGI FDR 66kV | Min Voltage at Constrained Conductor (pu) | 0.99473 | 0.9982 | 1.0215 | 0.99274 | 0.99442 | 1.0204 | 0.99111 | 0.99203 | 1.02 | 0.99196 | 0.99353 | 1.0203 | 0.9896 | 1.0104 | 1.019
WB | M028_GAYN TEE DEGI FDR 66kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV
WB | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 12.37% | 7.532% | 9.885% | 12.38% | 7.55% | 9.888% | 12.32% | 7.534% | 9.888% | 12.39% | 7.531% | 9.887% | 12.69% | 7.755% | 10.17%
WB | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 23.8657 | 20.6371 | 26.3937 | 23.8945 | 20.6873 | 26.402 | 23.7802 | 20.6441 | 26.4022 | 23.9112 | 20.6349 | 26.3982 | 24.4867 | 21.2496 | 27.1457
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 2.7012 | 2.3395 | 2.9947 | 2.7013 | 2.3396 | 2.9947 | 2.701 | 2.3395 | 2.9947 | 2.7014 | 2.3395 | 2.9947 | 2.7815 | 2.4091 | 3.0839
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 2.3836 | 2.0676 | 2.6395 | 2.3836 | 2.0676 | 2.6395 | 2.3836 | 2.0676 | 2.6395 | 2.3836 | 2.0676 | 2.6395 | 2.4538 | 2.1285 | 2.7173
WB | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.88206 | 0.88345 | 0.88102 | 0.88204 | 0.8834 | 0.88101 | 0.88214 | 0.88344 | 0.88101 | 0.88203 | 0.88345 | 0.88101 | 0.88184 | 0.88319 | 0.88071
WB | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267
WB | M029_Bundaberg - Farnsfield 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M029_Bundaberg - Farnsfield 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99011 | 0.99169 | 0.99253 | 0.98895 | 0.98933 | 0.99223 | 0.99358 | 0.99136 | 0.99222 | 0.98828 | 0.99179 | 0.99237 | 0.99366 | 0.99175 | 0.9938
WB | M029_Bundaberg - Farnsfield 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M049_ISIS - Gayndah 66 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7315_Aramara 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | M030_Farnsfield - Childers 66 kV | % of Rated A | 47.85% | 45.79% | 30.61% | 47.82% | 45.77% | 30.64% | 47.8% | 45.82% | 30.64% | 47.85% | 45.82% | 30.64% | 48.97% | 46.8% | 31.34%
WB | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB | M030_Farnsfield - Childers 66 kV | Loading (A) | 63.1589 | 76.4721 | 48.6687 | 63.1255 | 76.4294 | 48.7121 | 63.0953 | 76.5253 | 48.7225 | 63.1623 | 76.5277 | 48.7148 | 64.6427 | 78.1592 | 49.8344
WB | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 7.2096 | 8.7097 | 5.6101 | 7.2094 | 8.7093 | 5.6099 | 7.2092 | 8.7104 | 5.6099 | 7.2097 | 8.7104 | 5.6099 | 7.3726 | 8.9093 | 5.7296
WB | M030_Farnsfield - Childers 66 kV | Loading (MW) | 7.1947 | 8.6386 | 5.6035 | 7.1946 | 8.6385 | 5.6035 | 7.1946 | 8.6387 | 5.6036 | 7.1947 | 8.6387 | 5.6035 | 7.3524 | 8.8281 | 5.7261
WB | M030_Farnsfield - Childers 66 kV | Power Factor | 0.99774 | 0.99163 | 0.99882 | 0.99777 | 0.99167 | 0.99886 | 0.99779 | 0.99157 | 0.99887 | 0.99774 | 0.99157 | 0.99887 | 0.99706 | 0.99068 | 0.99938
WB | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | M030_Farnsfield - Childers 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M030_Farnsfield - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99636 | 0.99363 | 1.0066 | 0.99686 | 0.99413 | 1.0057 | 0.99731 | 0.99301 | 1.0055 | 0.99632 | 0.99298 | 1.0056 | 0.99546 | 0.99439 | 1.0039
WB | M030_Farnsfield - Childers 66 kV | Contingency Outage | 785_ISIS 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7315_Aramara 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M012_Maryborough-Rocky St 66 kV | 7315_Aramara 132 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7315_Aramara 132 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 65.61% | 56.85% | 33.53% | 65.62% | 57.01% | 33.53% | 65.3% | 56.87% | 33.53% | 65.67% | 56.85% | 33.53% | 65.92% | 57.38% | 33.76%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 86.6102 | 100.6284 | 56.9932 | 86.6218 | 100.8996 | 57.0069 | 86.1943 | 100.6666 | 57.0072 | 86.6847 | 100.6169 | 57.0007 | 87.014 | 101.5571 | 57.3978
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 9.7808 | 11.3631 | 6.4788 | 9.7809 | 11.366 | 6.4784 | 9.7785 | 11.3635 | 6.4784 | 9.7812 | 11.3629 | 6.4786 | 9.8726 | 11.4681 | 6.5336
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 9.7806 | 11.3465 | 6.3471 | 9.7806 | 11.3483 | 6.3472 | 9.778 | 11.3468 | 6.3472 | 9.781 | 11.3465 | 6.3471 | 9.8724 | 11.4492 | 6.4054
WB | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.99998 | 0.99855 | 0.97968 | 0.99998 | 0.99844 | 0.97975 | 0.99994 | 0.99853 | 0.97975 | 0.99998 | 0.99855 | 0.97972 | 0.99998 | 0.99835 | 0.98037
WB | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | M032_Bundaberg-South Kolan No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M032_Bundaberg-South Kolan No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98787 | 0.97306 | 0.99441 | 0.98774 | 0.97061 | 0.99411 | 0.9924 | 0.97271 | 0.9941 | 0.98706 | 0.97316 | 0.99424 | 0.99251 | 0.97292 | 0.99576
WB | M032_Bundaberg-South Kolan No 1 66 kV | Contingency Outage | M035_Bundaberg-South Kolan No 2 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M049_ISIS - Gayndah 66 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7315_Aramara 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 11.57% | 13.14% | 7.741% | 11.58% | 13.17% | 7.743% | 11.53% | 13.14% | 7.743% | 11.59% | 13.14% | 7.742% | 11.66% | 13.3% | 7.816%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 63.4014 | 76.0669 | 40.3294 | 63.479 | 76.2715 | 40.3411 | 63.1575 | 76.0957 | 40.3413 | 63.5305 | 76.0582 | 40.3358 | 63.9156 | 76.9796 | 40.7239
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 7.178 | 8.6117 | 4.5894 | 7.1783 | 8.6143 | 4.5893 | 7.1756 | 8.6121 | 4.5893 | 7.1792 | 8.6116 | 4.5893 | 7.2626 | 8.7159 | 4.6407
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 7.1623 | 8.555 | 4.5733 | 7.1624 | 8.5561 | 4.5733 | 7.161 | 8.5552 | 4.5733 | 7.1629 | 8.555 | 4.5733 | 7.2462 | 8.6555 | 4.6257
WB | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.99709 | 0.99264 | 0.99649 | 0.99706 | 0.99248 | 0.99651 | 0.99725 | 0.99262 | 0.99651 | 0.997 | 0.99265 | 0.9965 | 0.99701 | 0.99231 | 0.99677
WB | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | M035_Bundaberg-South Kolan No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M035_Bundaberg-South Kolan No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98903 | 0.98864 | 0.99442 | 0.98786 | 0.98627 | 0.99412 | 0.99252 | 0.98831 | 0.99411 | 0.98718 | 0.98875 | 0.99426 | 0.99264 | 0.9887 | 0.99577
WB | M035_Bundaberg-South Kolan No 2 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M049_ISIS - Gayndah 66 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7315_Aramara 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 122.4% | 128.6% | 85.93% | 121.2% | 129.3% | 86.13% | 121.6% | 130% | 86.32% | 121.4% | 130% | 86.29% | 124.5% | 133.8% | 87.92%
WB | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 537.3723 | 617.1025 | 334.2694 | 531.8702 | 620.8614 | 335.0531 | 533.638 | 624.2222 | 335.7932 | 532.9101 | 624.0851 | 335.6722 | 546.3625 | 642.3601 | 341.9983
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 61.0272 | 70.7687 | 38.2736 | 61.0959 | 71.0154 | 38.3397 | 61.2319 | 71.2672 | 38.4088 | 61.1804 | 71.2878 | 38.3994 | 62.5332 | 73.0395 | 39.0756
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 60.8251 | 70.7357 | 36.1486 | 60.884 | 70.99 | 36.2304 | 61.0278 | 71.24 | 36.3119 | 60.9664 | 71.2585 | 36.288 | 62.3812 | 73.0306 | 37.0961
WB | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.98807 | 0.99363 | 0.92842 | 0.98804 | 0.99398 | 0.92894 | 0.98824 | 0.99381 | 0.92937 | 0.98795 | 0.99369 | 0.92893 | 0.98975 | 0.99482 | 0.9335
WB | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB | M036_Bundaberg-South Bundaberg 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M036_Bundaberg-South Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95965 | 0.96047 | 0.99213 | 0.97148 | 0.95733 | 0.99141 | 0.97016 | 0.95533 | 0.99093 | 0.97087 | 0.95593 | 0.9911 | 0.96598 | 0.94907 | 0.98905
WB | M036_Bundaberg-South Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB | M037_South - East Bundaberg 66 kV | % of Rated A | 137.3% | 106.4% | 73.73% | 135.6% | 106.7% | 73.76% | 135.7% | 107.1% | 73.78% | 134.9% | 106.6% | 73.52% | 137.7% | 109.2% | 74.5%
WB | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB | M037_South - East Bundaberg 66 kV | Loading (A) | 310.39 | 330.8044 | 190.2221 | 306.4128 | 331.884 | 190.2914 | 306.6416 | 333.0464 | 190.3456 | 304.8655 | 331.4264 | 189.6914 | 311.1728 | 339.5527 | 192.1995
WB | M037_South - East Bundaberg 66 kV | Loading (MVA) | 33.998 | 36.2563 | 21.5843 | 33.9778 | 36.2542 | 21.5766 | 33.9568 | 36.3068 | 21.5722 | 33.7864 | 36.1544 | 21.5023 | 34.3069 | 36.7695 | 21.7402
WB | M037_South - East Bundaberg 66 kV | Loading (MW) | 33.3323 | 35.6622 | 18.9942 | 33.3028 | 35.6775 | 18.9893 | 33.2846 | 35.693 | 18.9844 | 33.0868 | 35.519 | 18.8797 | 33.6854 | 36.1956 | 19.2218
WB | M037_South - East Bundaberg 66 kV | Power Factor | 0.97753 | 0.98076 | 0.87627 | 0.97731 | 0.98126 | 0.87635 | 0.97738 | 0.98016 | 0.8763 | 0.97642 | 0.97945 | 0.87428 | 0.97912 | 0.98148 | 0.88042
WB | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | M037_South - East Bundaberg 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M037_South - East Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9523 | 0.95225 | 0.99178 | 0.96426 | 0.94901 | 0.99107 | 0.96293 | 0.94712 | 0.99058 | 0.96378 | 0.94785 | 0.99082 | 0.95845 | 0.94053 | 0.98857
WB | M037_South - East Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 72.59% | 67.9% | 46.1% | 72.52% | 68.97% | 46.57% | 73.59% | 70.17% | 47.11% | 73.19% | 69.89% | 46.92% | 74.74% | 71.43% | 47.69%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 7876_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1 | TR_LINE 7886_1 | TR_LINE 7886_1 | TR_LINE 200241_1
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 585.0859 | 613.1814 | 343.4377 | 584.4928 | 622.7548 | 346.9482 | 593.1332 | 633.6356 | 350.9376 | 589.9494 | 631.0961 | 349.5315 | 602.4196 | 645.0111 | 355.3147
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 66.3242 | 70.201 | 39.357 | 66.9843 | 71.1044 | 39.7383 | 67.8491 | 72.1711 | 40.1782 | 67.5254 | 71.8995 | 40.0235 | 68.7137 | 73.249 | 40.6389
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 66.3186 | 70.1797 | 38.4989 | 66.9785 | 71.0698 | 38.9065 | 67.8347 | 72.1135 | 39.3936 | 67.5143 | 71.8468 | 39.221 | 68.689 | 73.1907 | 39.9005
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.99992 | 0.9997 | 0.97812 | 0.99991 | 0.99951 | 0.97899 | 0.99979 | 0.9992 | 0.9804 | 0.99984 | 0.99927 | 0.97988 | 0.99964 | 0.9992 | 0.98176
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99108 | 0.99546 | 1.0025 | 0.997 | 0.99251 | 1.0019 | 0.9949 | 0.98976 | 1.0015 | 0.99559 | 0.99007 | 1.0017 | 0.9918 | 0.9867 | 1.0005
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Contingency Outage | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 72.11% | 67.48% | 45.78% | 72.05% | 68.53% | 46.25% | 73.12% | 69.73% | 46.78% | 72.73% | 69.45% | 46.59% | 74.25% | 70.99% | 47.37%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 7295_1 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_1 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_2 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_1 | TR_LINE 7295_2 | TR_LINE 169764_1 | TR_LINE 7295_2 | TR_LINE 7295_2 | TR_LINE 169764_1
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 581.2285 | 609.3062 | 341.0784 | 580.7543 | 618.839 | 344.5658 | 589.3556 | 629.6771 | 348.5295 | 586.1864 | 627.1474 | 347.1324 | 598.4854 | 640.996 | 352.8789
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 65.8569 | 69.3186 | 39.0847 | 66.5459 | 70.1935 | 39.4635 | 67.0134 | 71.2247 | 39.9005 | 67.0844 | 70.961 | 39.7468 | 67.8521 | 72.2793 | 40.3582
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 65.8512 | 69.3177 | 38.2526 | 66.5363 | 70.1891 | 38.6574 | 67.0133 | 71.211 | 39.1409 | 67.0683 | 70.9494 | 38.9696 | 67.8503 | 72.2662 | 39.6441
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.99991 | 0.99999 | 0.97673 | 0.99985 | 0.99994 | 0.97761 | 1 | 0.99981 | 0.97903 | 0.99976 | 0.99984 | 0.9785 | 0.99997 | 0.99982 | 0.98042
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 0.98567 | 0.99473 | 1.0022 | 0.99677 | 0.99175 | 1.0016 | 0.99422 | 0.98897 | 1.0011 | 0.99536 | 0.98929 | 1.0013 | 0.99129 | 0.98588 | 1.0001
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Contingency Outage | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV
WB | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 53.66% | 44.96% | 28.2% | 57.76% | 48.7% | 30.14% | 62.11% | 52.54% | 32.26% | 62.5% | 52.52% | 32.26% | 63.18% | 53.58% | 32.8%
WB | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 121.2725 | 139.8233 | 72.7585 | 130.54 | 151.4628 | 77.7585 | 140.3668 | 163.4036 | 83.2407 | 141.2555 | 163.3367 | 83.2253 | 142.7934 | 166.6329 | 84.6356
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 13.4072 | 15.4802 | 8.2164 | 14.4457 | 16.7001 | 8.7692 | 15.5836 | 18.0203 | 9.3766 | 15.5966 | 18.0222 | 9.377 | 15.8415 | 18.3235 | 9.5185
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 12.1582 | 14.1328 | 7.0845 | 13.1623 | 15.2884 | 7.6519 | 14.251 | 16.5423 | 8.2672 | 14.2511 | 16.5424 | 8.2672 | 14.4959 | 16.829 | 8.4097
WB | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.90684 | 0.91296 | 0.86112 | 0.91116 | 0.91547 | 0.87166 | 0.91448 | 0.91798 | 0.88093 | 0.91373 | 0.91789 | 0.88088 | 0.91506 | 0.91844 | 0.8828
WB | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | M041_West Bundaberg-Meadowvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M041_West Bundaberg-Meadowvale 66 kV | Min Voltage at Constrained Conductor (pu) | 0.96459 | 0.96534 | 0.98761 | 0.9652 | 0.96098 | 0.98595 | 0.96802 | 0.9608 | 0.9845 | 0.96268 | 0.9613 | 0.98473 | 0.96723 | 0.95792 | 0.98285
WB | M041_West Bundaberg-Meadowvale 66 kV | Contingency Outage | M039_Bundaberg-West Bundaberg No 1 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M049_ISIS - Gayndah 66 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 29.01% | 26.4% | 16.46% | 28.99% | 26.52% | 16.49% | 28.9% | 26.52% | 16.51% | 29.07% | 26.52% | 16.51% | 29.6% | 27.23% | 16.92%
WB | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 32.1977 | 38.5473 | 19.5912 | 32.1765 | 38.7181 | 19.6214 | 32.0788 | 38.7258 | 19.651 | 32.2642 | 38.7183 | 19.6463 | 32.8506 | 39.7536 | 20.1369
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 3.5144 | 4.2079 | 2.1986 | 3.5143 | 4.2075 | 2.1983 | 3.5141 | 4.2076 | 2.1983 | 3.5145 | 4.2089 | 2.1983 | 3.5948 | 4.3064 | 2.2485
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 3.3217 | 3.9698 | 2.0794 | 3.3217 | 3.97 | 2.0793 | 3.3216 | 3.97 | 2.0793 | 3.3218 | 3.9703 | 2.0793 | 3.3976 | 4.0613 | 2.1267
WB | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.93965 | 0.93806 | 0.94251 | 0.93966 | 0.93823 | 0.94262 | 0.93971 | 0.93823 | 0.9426 | 0.93961 | 0.93798 | 0.9426 | 0.93951 | 0.93795 | 0.94247
WB | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119
WB | M042_Meadowvale-Gooburrum 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M042_Meadowvale-Gooburrum 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95482 | 0.95361 | 0.9817 | 0.95543 | 0.94921 | 0.98004 | 0.95829 | 0.94903 | 0.97857 | 0.95288 | 0.94953 | 0.97881 | 0.95726 | 0.94583 | 0.97678
WB | M042_Meadowvale-Gooburrum 66 kV | Contingency Outage | M039_Bundaberg-West Bundaberg No 1 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M049_ISIS - Gayndah 66 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | M046_Tarong-Caboonbah 66 kV | % of Rated A | 14.56% | 5.867% | 6.091% | 14.56% | 5.867% | 6.091% | 14.56% | 5.867% | 6.09% | 14.56% | 5.866% | 6.09% | 14.57% | 5.868% | 6.091%
WB | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1
WB | M046_Tarong-Caboonbah 66 kV | Loading (A) | 36.2614 | 22.412 | 22.5356 | 36.2603 | 22.411 | 22.5349 | 36.2589 | 22.4106 | 22.5346 | 36.2525 | 22.407 | 22.5331 | 36.2673 | 22.4172 | 22.5369
WB | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 4.2571 | 2.646 | 2.6804 | 4.2571 | 2.6459 | 2.6804 | 4.2571 | 2.6459 | 2.6804 | 4.257 | 2.6459 | 2.6804 | 4.2572 | 2.6461 | 2.6805
WB | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 3.9473 | 2.5366 | 2.574 | 3.9473 | 2.5366 | 2.574 | 3.9473 | 2.5366 | 2.574 | 3.9473 | 2.5366 | 2.574 | 3.9473 | 2.5366 | 2.574
WB | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.92722 | 0.95866 | 0.96027 | 0.92723 | 0.95867 | 0.96028 | 0.92723 | 0.95867 | 0.96028 | 0.92725 | 0.95869 | 0.96029 | 0.92721 | 0.95863 | 0.96026
WB | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | M046_Tarong-Caboonbah 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M046_Tarong-Caboonbah 66 kV | Min Voltage at Constrained Conductor (pu) | 1.027 | 1.0328 | 1.0405 | 1.027 | 1.0328 | 1.0405 | 1.0271 | 1.0328 | 1.0405 | 1.0272 | 1.033 | 1.0406 | 1.0268 | 1.0326 | 1.0404
WB | M046_Tarong-Caboonbah 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M002_Tarong-Kingaroy West 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M002_Tarong-Kingaroy West 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M002_Tarong-Kingaroy West 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M002_Tarong-Kingaroy West 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV
WB | M049_ISIS - Gayndah 66 kV | % of Rated A | 58.03% | 52.73% | 42.7% | 56.46% | 51.42% | 42.46% | 56.16% | 51.21% | 42.33% | 55.54% | 50.66% | 42.05% | 56.33% | 51.45% | 42.37%
WB | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB | M049_ISIS - Gayndah 66 kV | Loading (A) | 231.558 | 218.8444 | 157.986 | 225.2699 | 213.3965 | 157.0921 | 224.0873 | 212.5241 | 156.6068 | 221.6177 | 210.2505 | 155.602 | 224.7439 | 213.5152 | 156.7682
WB | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 26.7948 | 25.3367 | 18.3977 | 26.3874 | 24.9936 | 18.284 | 26.2453 | 24.8799 | 18.2294 | 25.9674 | 24.623 | 18.1133 | 26.2698 | 24.9131 | 18.232
WB | M049_ISIS - Gayndah 66 kV | Loading (MW) | 26.4209 | 25.0716 | 18.3974 | 26.0768 | 24.7782 | 18.284 | 25.9679 | 24.6878 | 18.2292 | 25.7 | 24.4387 | 18.113 | 25.984 | 24.7104 | 18.2318
WB | M049_ISIS - Gayndah 66 kV | Power Factor | 0.98605 | 0.98954 | 0.99953 | 0.98823 | 0.99138 | 0.9994 | 0.98943 | 0.99228 | 0.99916 | 0.9897 | 0.99251 | 0.99919 | 0.98912 | 0.99186 | 0.99919
WB | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
WB | M049_ISIS - Gayndah 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M049_ISIS - Gayndah 66 kV | Min Voltage at Constrained Conductor (pu) | 0.947 | 0.9526 | 0.98126 | 0.96215 | 0.96674 | 0.9812 | 0.96286 | 0.96692 | 0.98184 | 0.96413 | 0.96805 | 0.98209 | 0.9605 | 0.96306 | 0.98085
WB | M049_ISIS - Gayndah 66 kV | Contingency Outage | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV
WB | M051_Tarong Tie 66 kV | % of Rated A | 39.04% | 31.33% | 14.9% | 39.02% | 31.31% | 14.89% | 39.01% | 31.29% | 14.89% | 38.95% | 31.25% | 14.88% | 39.93% | 32.06% | 15.22%
WB | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1
WB | M051_Tarong Tie 66 kV | Loading (A) | 41.7766 | 43.2313 | 19.6669 | 41.7545 | 43.2011 | 19.6607 | 41.737 | 43.1863 | 19.6575 | 41.6712 | 43.1245 | 19.6464 | 42.7236 | 44.2476 | 20.0949
WB | M051_Tarong Tie 66 kV | Loading (MVA) | 4.3195 | 4.5002 | 2.2097 | 4.3194 | 4.5001 | 2.2096 | 4.3194 | 4.5 | 2.2096 | 4.319 | 4.4997 | 2.2096 | 4.4118 | 4.5989 | 2.2566
WB | M051_Tarong Tie 66 kV | Loading (MW) | 4.227 | 4.402 | 2.1738 | 4.2269 | 4.4019 | 2.1738 | 4.2269 | 4.4019 | 2.1738 | 4.2268 | 4.4018 | 2.1738 | 4.3172 | 4.4968 | 2.2201
WB | M051_Tarong Tie 66 kV | Power Factor | 0.9766 | 0.97627 | 0.98195 | 0.97662 | 0.97629 | 0.98196 | 0.97663 | 0.97629 | 0.98196 | 0.97666 | 0.97633 | 0.98196 | 0.97666 | 0.97596 | 0.98197
WB | M051_Tarong Tie 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | M051_Tarong Tie 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | M051_Tarong Tie 66 kV | Min Voltage at Constrained Conductor (pu) | 0.90242 | 0.90836 | 0.98285 | 0.90288 | 0.90897 | 0.98315 | 0.90324 | 0.90927 | 0.98331 | 0.90462 | 0.91053 | 0.98385 | 0.90111 | 0.90681 | 0.98234
WB | M051_Tarong Tie 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M001_Tarong-Kingaroy East 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 28.2% | 24.65% | 11.74% | 28.18% | 25.02% | 11.88% | 28.54% | 25.36% | 12.02% | 28.84% | 25.63% | 12.16% | 29.97% | 26.69% | 12.59%
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 115.6361 | 156.0068 | 63.2776 | 115.5366 | 158.3577 | 64.0516 | 117.0199 | 160.525 | 64.8118 | 118.2542 | 162.2454 | 65.5285 | 122.8573 | 168.9329 | 67.8503
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 12.635 | 17.0332 | 7.1618 | 12.7803 | 17.2312 | 7.244 | 12.926 | 17.4288 | 7.3262 | 13.0714 | 17.6255 | 7.4083 | 13.5091 | 18.2146 | 7.6543
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 12.5647 | 16.9087 | 7.135 | 12.7085 | 17.1029 | 7.2166 | 12.8525 | 17.297 | 7.2983 | 12.9964 | 17.4909 | 7.38 | 13.4287 | 18.0722 | 7.6248
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.99444 | 0.99269 | 0.99614 | 0.99438 | 0.99256 | 0.99612 | 0.99432 | 0.99244 | 0.99609 | 0.99427 | 0.99236 | 0.99606 | 0.99405 | 0.99218 | 0.99604
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.95552 | 0.95462 | 0.99003 | 0.96735 | 0.95137 | 0.98929 | 0.96597 | 0.94927 | 0.98877 | 0.96663 | 0.9498 | 0.98892 | 0.96155 | 0.94265 | 0.98678
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV