## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extend that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
The Network Modeling Team makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be taken into account when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modeling Team obtain these forecast values as populated by the Strategic Forecasting Team, the accuracy of these values are as per their quality assurance processes.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The studies results contained are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using PowerFactory 2024 SP5. The reported studies were calculated in PowerFactory 2024 SP5
· For the Energex network the model is running from External Grids representing the Powerlink Network at the common coupling points.
· For the Ergon network the model is running using the current years Powerlink Transmission TAPR model connected to the Ergon Subtransmission Model at the points of connection between the two utilities.
· The Mount Isa North West Power System network is running self contained within the Ergon Subtransmission model and is supplied by the large required generators in the system
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model as required by the study (most generation is excluded due to current settings)
· The Forecasts are extracted from SIFT or Tableau depending on where the current data is stored. 10PoE and 50PoE Forecasts from SIFT the Minimum Forecasts and Ergon Energy Daily Load Profiles are from Tableau
· Python automation was used to pull demand forecasts into PowerFactory model
· Load Flow studies were run for each of the following senarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLF_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Export Packaged Master Model
2. Import and Activate Extracted Model
3. Activate Load Characterstic Application Study Case
4. Run appropraite Forecast Load script for the given study
5. Run the DAPR Feeder Association Script to identify elements required for the new Feeder Voltage Attributes
6. Run The Setup Task Automation Script to create the command required for each individual year/Time Combination
7. Run the Task Automation Command with Parallel Computing turned on to calculate multiple studies at once
7. Repeat 4-6 for other characterstic combinations (such as SEQ Night Forecasts after running SEQ Day forecasts) required in the report.
8. Run a Python Interpreter that reads the output files and produces the formatted document
This entire process is completed with the RunExternalPowerFactoryGooey custom tool to run PowerFactory in external mode to minimise failed calculations due to momentary license outages.
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.
NNC | Normal Network Configuration
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor at the constrained conductor. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## Important Info - MINLF_EE_N-1
2. Important Information
2.1 Study Information - MinLF_EE_N-1 - Known Issues and Limitations
· The List of Subtransmission Projects to be stored as Variations has been produced manually from Copperleaf for the next 10 years.
· This report does not offer details of active Generators considered for each project
· Time Periods are based on Day (6am-5pm), Evening (5pm-10pm) and Night. This means that SN sift forecasts run at 7:30pm will be labelled as SE. This is unlikely to change
3. Additional Information
3.1 Information About Variables
The Values for a given timeslot shown are calculated as follows. All of the values will be for the line element in PowerFactory with the Loading Constraint.
This means that the Power Factor and Voltage values are recorded at the line that is considered the most "limited" not the minimum voltage on the feeder or the minimum Power Factor on the feeder
For each Contingency Event the values for each line are recorded with them eventually ending up in the following fields
% of Rated A: The % Utilisation called "loading" in PowerFactory [c:loading]
Limiting Line Name: The name of the line the results come from. It is nominally the most constrainted line. See later information for more details
Loading (A): Absolute Maximum Current for Both Ends in kA
Loading (MVA): Absolute Maximum Apparent Power for Both Ends in MVA
Loading (MW): Absolute Maximum Real Power for Both Ends in MW
Power Factor: Absolute Min PowerFactor for Both Ends
Rating (A): Line Nominal Rating using [e:Inom_a]
Time: The time at which the limiting study was completed
Min Voltage at Constrained Conductor: Min Voltage seen on both sides of line for the constrained line
Min Feeder Voltage: The minimum voltage seen on the ElmFeeder object associated with the line. Includes Open End Branch voltages and Feeder End Terminals
Min Feeder End Terminal Voltage: The Feeder voltage at the end terminals of a feeder. Does not include Open End Branches
Min Feeder Associated Sift-Load or Customer Terminal Voltage: The minimum voltage at terminals connected to a SIFT-load that the ElmFeeder can get to without traversing another feeder or at the Terminal Connected to a Customer site with an ElmOwner association starting with NMI_
Min Feeder Voltage at MV Connected TXs: The Minimum Voltage at any MV Terminals of Transformers within the ElmFeeder object
Once they are calculated for each feeder and Timeslot the Limiting entry is determined. This will be the values for a single line limited in the following order.
At each step all lines that share the "limiting" value will be recorded, provided their float representative is identical.
Minor differences in the float representation will result in the Min or Max value being utilised even if the value when considering real life significant figures are otherwise identical
1. % of Rated A - Max
2. Rating (A) - Min
3. Loading (MVA) - Max
The following limit calculations are applied to ensure only 1 line's values are recorded even if all entries have the same electrical loading characteristics
4. For N-1 results. Contingency Outage: Alphabetical Max
Note that "_NNC" is used with is a "Normal Network Configuration" contingency where nothing is taken out of service. If it is displayed then taking a feeder out of service did not make a recordable difference to the feeder loading.
If multiple feeder outage contingencies have the same affect on the feeder then the higher alphabetical name will be recorded.
5. Limiting Line Name: Alphabetical Min: This is to ensure there is a unique value
6. Current Study Case Time: Alphabetical Min: This is a stopgap to ensure there is a unique value

## MinLF_EE_N-1_2025
Region | PF Feeder Obj Name | Variable | 2026 SD | 2027 SD | 2028 SD | 2029 SD | 2030 SD
CA | 6011_Blackwater - Comet 66 kV | % of Rated A | 33.7% | 34.03% | 34.48% | 35.07% | 35.66%
CA | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1
CA | 6011_Blackwater - Comet 66 kV | Loading (A) | 93.3574 | 94.2682 | 95.5034 | 97.1522 | 98.7916
CA | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 11.4555 | 11.5679 | 11.72 | 11.923 | 12.1246
CA | 6011_Blackwater - Comet 66 kV | Loading (MW) | 0.016268 | 0.8713 | 1.6698 | 2.4977 | 3.1836
CA | 6011_Blackwater - Comet 66 kV | Power Factor | 0.0013613 | 0.075261 | 0.14241 | 0.20942 | 0.26251
CA | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
CA | 6011_Blackwater - Comet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6011_Blackwater - Comet 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0734 | 1.0735 | 1.0735 | 1.0736 | 1.0736
CA | 6011_Blackwater - Comet 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 12.71% | 12.48% | 12.27% | 12% | 11.77%
CA | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 35.3456 | 34.6865 | 34.1027 | 33.3464 | 32.7248
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 4.3173 | 4.2368 | 4.1655 | 4.0732 | 3.9973
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 4.1818 | 4.0982 | 4.024 | 3.9277 | 3.8485
CA | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.96862 | 0.96727 | 0.96601 | 0.96428 | 0.96277
CA | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
CA | 6012_Blackwater - Bedford Weir 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6012_Blackwater - Bedford Weir 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0685 | 1.0685 | 1.0685 | 1.0685 | 1.0685
CA | 6012_Blackwater - Bedford Weir 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV
CA | 6014_Blackwater - South Blackwater 66 kV | % of Rated A | 28.9% | 28.9% | 28.89% | 28.88% | 28.87%
CA | 6014_Blackwater - South Blackwater 66 kV | Limiting Line Name | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (A) | 143.3677 | 143.325 | 143.2846 | 143.2449 | 143.2174
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MVA) | 17.5348 | 17.5296 | 17.5246 | 17.5197 | 17.5155
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MW) | 17.5327 | 17.5274 | 17.5224 | 17.5175 | 17.5133
CA | 6014_Blackwater - South Blackwater 66 kV | Power Factor | 0.99988 | 0.99988 | 0.99988 | 0.99988 | 0.99988
CA | 6014_Blackwater - South Blackwater 66 kV | Rating (A) | 496 | 496 | 496 | 496 | 496
CA | 6014_Blackwater - South Blackwater 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6014_Blackwater - South Blackwater 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0699 | 1.0699 | 1.0699 | 1.0699 | 1.0698
CA | 6014_Blackwater - South Blackwater 66 kV | Contingency Outage | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV | 6013_Blackwater - Leichardt 66 kV
CA | 6056_Comet - Emerald 66 kV | % of Rated A | 32.46% | 32.54% | 32.75% | 33.12% | 33.53%
CA | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1
CA | 6056_Comet - Emerald 66 kV | Loading (A) | 89.9234 | 90.1296 | 90.7259 | 91.7403 | 92.8811
CA | 6056_Comet - Emerald 66 kV | Loading (MVA) | 11.3617 | 11.407 | 11.5003 | 11.6473 | 11.8073
CA | 6056_Comet - Emerald 66 kV | Loading (MW) | 0.96981 | 0.12156 | 0.67563 | 1.499 | 2.1849
CA | 6056_Comet - Emerald 66 kV | Power Factor | 0.085339 | 0.010636 | 0.058728 | 0.12868 | 0.18503
CA | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
CA | 6056_Comet - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6056_Comet - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 1.1053 | 1.1071 | 1.1089 | 1.1106 | 1.112
CA | 6056_Comet - Emerald 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 9.797% | 9.768% | 9.741% | 9.712% | 9.688%
CA | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 27.235 | 27.1556 | 27.0797 | 27.0001 | 26.9327
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 3.3168 | 3.3075 | 3.2985 | 3.2892 | 3.2813
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 3.2125 | 3.2027 | 3.1934 | 3.1837 | 3.1754
CA | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.96854 | 0.96833 | 0.96813 | 0.96792 | 0.96773
CA | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
CA | 6058_Bedford Weir - Bingegang 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6058_Bedford Weir - Bingegang 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0653 | 1.0654 | 1.0655 | 1.0656 | 1.0657
CA | 6058_Bedford Weir - Bingegang 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV
CA | 6059_Leichardt - Cook Colliery 66 kV | % of Rated A | 81.15% | 81.12% | 81.09% | 81.06% | 81.04%
CA | 6059_Leichardt - Cook Colliery 66 kV | Limiting Line Name | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (A) | 116.0442 | 115.9999 | 115.9579 | 115.9166 | 115.8867
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MVA) | 13.9687 | 13.9635 | 13.9584 | 13.9535 | 13.9493
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MW) | 13.9495 | 13.9442 | 13.9391 | 13.9342 | 13.93
CA | 6059_Leichardt - Cook Colliery 66 kV | Power Factor | 0.99845 | 0.99844 | 0.99844 | 0.99844 | 0.99844
CA | 6059_Leichardt - Cook Colliery 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA | 6059_Leichardt - Cook Colliery 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6059_Leichardt - Cook Colliery 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0421 | 1.0421 | 1.0421 | 1.0421 | 1.0421
CA | 6059_Leichardt - Cook Colliery 66 kV | Contingency Outage | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV | 6014_Blackwater - South Blackwater 66 kV
CA | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 25.99% | 25.88% | 25.85% | 25.69% | 25.49%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 63.1674 | 62.8919 | 62.8124 | 62.4233 | 61.9509
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 7.5662 | 7.5336 | 7.5058 | 7.4596 | 7.4214
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 7.532 | 7.499 | 7.4716 | 7.4249 | 7.3857
CA | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.99547 | 0.99541 | 0.99544 | 0.99535 | 0.99518
CA | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA | 6065_Lilyvale - Tieri Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6065_Lilyvale - Tieri Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0478 | 1.0478 | 1.0453 | 1.0453 | 1.0479
CA | 6065_Lilyvale - Tieri Tee 66 kV | Contingency Outage | 6069_Lilyvale - German Creek Mine 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV
CA | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 26.84% | 26.84% | 26.65% | 26.9% | 27.52%
CA | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 91.5178 | 91.5206 | 90.8604 | 91.7444 | 93.8317
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 11.0673 | 11.0682 | 10.8574 | 10.9635 | 11.3491
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 0.86367 | 0.14821 | 0.94959 | 1.7795 | 2.472
CA | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.066161 | 0.0012709 | 0.072719 | 0.1474 | 0.20273
CA | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 341 | 341 | 341 | 341
CA | 6067 Lilyvale - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6067 Lilyvale - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0579 | 1.0579 | 1.0453 | 1.0454 | 1.0581
CA | 6067 Lilyvale - Emerald 66 kV | Contingency Outage | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV
CA | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 4.135% | 4.165% | 4.226% | 4.323% | 4.427%
CA | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38974_1
CA | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 15.2183 | 15.3283 | 15.5526 | 15.9071 | 16.2906
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 1.9004 | 1.9169 | 1.9477 | 1.995 | 2.0455
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 0.017511 | 0.19603 | 0.36895 | 0.55103 | 0.70321
CA | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.0092085 | 0.10226 | 0.18942 | 0.2762 | 0.34377
CA | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 368 | 368 | 368 | 368 | 368
CA | 6079_Barcaldine - Longreach 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6079_Barcaldine - Longreach 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0924 | 1.094 | 1.0955 | 1.0971 | 1.0984
CA | 6079_Barcaldine - Longreach 66 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV
CA | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 3.582% | 3.624% | 3.675% | 3.738% | 3.8%
CA | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 13.8254 | 13.987 | 14.1852 | 14.4277 | 14.6687
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 1.7038 | 1.7261 | 1.7529 | 1.7854 | 1.8173
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 0.28394 | 0.37631 | 0.46968 | 0.56703 | 0.65247
CA | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.16664 | 0.218 | 0.26793 | 0.31759 | 0.35902
CA | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 386 | 386 | 386 | 386 | 386
CA | 6080_Barcaldine - Blackall 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6080_Barcaldine - Blackall 66 kV | Min Voltage at Constrained Conductor (pu) | 1.078 | 1.0795 | 1.081 | 1.0825 | 1.0838
CA | 6080_Barcaldine - Blackall 66 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV
CA | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 1.342% | 1.308% | 1.282% | 1.24% | 1.203%
CA | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 3.2607 | 3.1796 | 3.115 | 3.012 | 2.9232
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 0.38941 | 0.37976 | 0.37114 | 0.35889 | 0.34918
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 0.37097 | 0.3608 | 0.35189 | 0.33892 | 0.32839
CA | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.95263 | 0.95007 | 0.94814 | 0.94436 | 0.94045
CA | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA | 6085_Tieri Tee - Tieri 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6085_Tieri Tee - Tieri 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0446 | 1.0447 | 1.0421 | 1.0422 | 1.0448
CA | 6085_Tieri Tee - Tieri 66 kV | Contingency Outage | 6069_Lilyvale - German Creek Mine 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV
CA | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 24.65% | 24.57% | 24.57% | 24.45% | 24.3%
CA | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 59.9025 | 59.711 | 59.6996 | 59.4177 | 59.0372
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 7.1531 | 7.1307 | 7.112 | 7.0789 | 7.0512
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 7.1341 | 7.1115 | 7.093 | 7.0597 | 7.0314
CA | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.99734 | 0.99731 | 0.99734 | 0.99729 | 0.99719
CA | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA | 6086_Tieri Tee - Middlemount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6086_Tieri Tee - Middlemount 66 kV | Min Voltage at Constrained Conductor (pu) | 1.035 | 1.0351 | 1.0325 | 1.0327 | 1.0354
CA | 6086_Tieri Tee - Middlemount 66 kV | Contingency Outage | 6069_Lilyvale - German Creek Mine 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV
CA | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 17.66% | 17.56% | 17.46% | 17.32% | 17.25%
CA | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 125.051 | 124.327 | 123.6431 | 122.6434 | 122.1261
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 30.3412 | 30.1658 | 30.0001 | 29.7578 | 29.6324
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 13.1905 | 12.6413 | 12.105 | 11.5421 | 11.1145
CA | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.43474 | 0.41906 | 0.4035 | 0.38787 | 0.37508
CA | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 708 | 708 | 708 | 708
CA | 7153_Lilyvale - Clermont 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7153_Lilyvale - Clermont 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0612 | 1.0612 | 1.0613 | 1.0613 | 1.0613
CA | 7153_Lilyvale - Clermont 132 kV | Contingency Outage | 6080_Barcaldine - Blackall 66 kV | 6080_Barcaldine - Blackall 66 kV | 6080_Barcaldine - Blackall 66 kV | 6080_Barcaldine - Blackall 66 kV | 6079_Barcaldine - Longreach 66 kV
CA | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 22.43% | 22.46% | 22.49% | 22.54% | 22.58%
CA | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 80.7442 | 80.8525 | 80.9778 | 81.1282 | 81.2723
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 20.5381 | 20.5733 | 20.6125 | 20.6582 | 20.7011
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 0.5045 | 0.085252 | 0.35519 | 0.78521 | 1.1518
CA | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.023655 | 0.0028405 | 0.015873 | 0.036649 | 0.054275
CA | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 360 | 360 | 360 | 360
CA | 7154_Clermont - Barcaldine 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7154_Clermont - Barcaldine 132 kV | Min Voltage at Constrained Conductor (pu) | 1.1125 | 1.1129 | 1.1133 | 1.1137 | 1.1141
CA | 7154_Clermont - Barcaldine 132 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV
CA | 7286_Blackwater - Memooloo 132 kV | % of Rated A | 15.67% | 15.62% | 15.58% | 15.53% | 15.5%
CA | 7286_Blackwater - Memooloo 132 kV | Limiting Line Name | TR_LINE 62090_1 | TR_LINE 62090_1 | TR_LINE 62090_1 | TR_LINE 62090_1 | TR_LINE 62090_1
CA | 7286_Blackwater - Memooloo 132 kV | Loading (A) | 110.4765 | 110.1435 | 109.8292 | 109.5111 | 109.2432
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MVA) | 26.7738 | 26.6931 | 26.617 | 26.5399 | 26.4749
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MW) | 26.2372 | 26.1523 | 26.0721 | 25.9909 | 25.9225
CA | 7286_Blackwater - Memooloo 132 kV | Power Factor | 0.97996 | 0.97974 | 0.97953 | 0.97932 | 0.97913
CA | 7286_Blackwater - Memooloo 132 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
CA | 7286_Blackwater - Memooloo 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7286_Blackwater - Memooloo 132 kV | Min Voltage at Constrained Conductor (pu) | 1.06 | 1.06 | 1.06 | 1.06 | 1.06
CA | 7286_Blackwater - Memooloo 132 kV | Contingency Outage | _NNC | _NNC | 6059_Leichardt - Cook Colliery 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 10.22% | 10.17% | 10.12% | 10.08% | 10.04%
CA | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1
CA | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 72.0457 | 71.7018 | 71.3772 | 71.0485 | 70.7718
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 17.4015 | 17.3192 | 17.2416 | 17.1629 | 17.0967
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 17.2976 | 17.2142 | 17.1354 | 17.0556 | 16.9885
CA | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.99403 | 0.99393 | 0.99384 | 0.99375 | 0.99367
CA | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
CA | 7450_Memooloo - Rolleston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7450_Memooloo - Rolleston 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0537 | 1.0538 | 1.0538 | 1.0539 | 1.0539
CA | 7450_Memooloo - Rolleston 132 kV | Contingency Outage | 6059_Leichardt - Cook Colliery 66 kV | _NNC | 6059_Leichardt - Cook Colliery 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 9.312% | 9.327% | 9.339% | 9.369% | 9.393%
CA | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 37.3428 | 37.4 | 37.4493 | 37.5688 | 37.6651
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 4.474 | 4.4816 | 4.4881 | 4.503 | 4.5148
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 4.4224 | 4.4307 | 4.4382 | 4.4544 | 4.4677
CA | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.98629 | 0.98648 | 0.9867 | 0.98704 | 0.98738
CA | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA | 6001_Glenmore - Parkhurst 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6001_Glenmore - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0481 | 1.0482 | 1.0484 | 1.0485 | 1.0486
CA | 6001_Glenmore - Parkhurst 66 kV | Contingency Outage | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV
CA | 6003_Glenmore - Berserker 66 kV | % of Rated A | 29.69% | 30.95% | 32.3% | 33.76% | 35.03%
CA | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1
CA | 6003_Glenmore - Berserker 66 kV | Loading (A) | 119.05 | 124.1174 | 129.5233 | 135.3767 | 140.4737
CA | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 14.303 | 14.9144 | 15.5664 | 16.2719 | 16.8858
CA | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 7.1496 | 8.4462 | 9.6857 | 10.919 | 11.9313
CA | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.49983 | 0.56628 | 0.62219 | 0.67102 | 0.70658
CA | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA | 6003_Glenmore - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6003_Glenmore - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0509 | 1.0511 | 1.0512 | 1.0514 | 1.0514
CA | 6003_Glenmore - Berserker 66 kV | Contingency Outage | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV
CA | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 15.98% | 15.96% | 15.91% | 15.85% | 15.82%
CA | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 58.6427 | 58.5665 | 58.3847 | 58.1708 | 58.0705
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 7.0471 | 7.0393 | 7.0187 | 6.9942 | 6.9828
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 1.5136 | 1.4543 | 1.3374 | 1.1897 | 1.1063
CA | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.21476 | 0.20657 | 0.19052 | 0.17007 | 0.1584
CA | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 367 | 367 | 367 | 367
CA | 6004_Glenmore - Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6004_Glenmore - Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0512 | 1.0514 | 1.0516 | 1.0518 | 1.0519
CA | 6004_Glenmore - Rockhampton South 66 kV | Contingency Outage | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 21.31% | 21.24% | 21.21% | 21.2% | 21.2%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 85.0127 | 84.7556 | 84.6097 | 84.5743 | 84.5882
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 10.1992 | 10.1698 | 10.1538 | 10.1507 | 10.1531
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 0.65303 | 0.239 | 0.16684 | 0.56799 | 0.85956
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.063785 | 0.023247 | 0.01617 | 0.055695 | 0.084399
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0495 | 1.0496 | 1.0498 | 1.0499 | 1.05
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 14.3% | 15.29% | 16.15% | 16.89% | 17.39%
CA | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1
CA | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 57.3566 | 61.3021 | 64.7764 | 67.7418 | 69.7365
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 6.905 | 7.3824 | 7.803 | 8.1624 | 8.4041
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 6.9035 | 7.3805 | 7.8009 | 8.1599 | 8.4014
CA | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.99978 | 0.99975 | 0.99972 | 0.9997 | 0.99968
CA | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA | 6006_Glenmore - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6006_Glenmore - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0531 | 1.0534 | 1.0537 | 1.054 | 1.0542
CA | 6006_Glenmore - Frenchville 66 kV | Contingency Outage | 6050_Parkhurst - Frenchville 66 kV | 6050_Parkhurst - Frenchville 66 kV | 6050_Parkhurst - Frenchville 66 kV | 6050_Parkhurst - Frenchville 66 kV | 6050_Parkhurst - Frenchville 66 kV
CA | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 23.07% | 23.61% | 24.17% | 24.8% | 25.37%
CA | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 30.4534 | 31.1656 | 31.9092 | 32.7362 | 33.4947
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 3.6555 | 3.7415 | 3.831 | 3.9305 | 4.0218
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 1.2085 | 1.4336 | 1.6447 | 1.8589 | 2.0416
CA | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.33056 | 0.38313 | 0.42928 | 0.4729 | 0.5076
CA | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6007_Biloela - Coominglah Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6007_Biloela - Coominglah Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.0502 | 1.0502 | 1.0503 | 1.0504
CA | 6007_Biloela - Coominglah Tee 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV
CA | 6008_Biloela - Wowan 66 kV | % of Rated A | 93.32% | 92.3% | 91.32% | 90.25% | 89.25%
CA | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1
CA | 6008_Biloela - Wowan 66 kV | Loading (A) | 123.1822 | 121.8382 | 120.5395 | 119.1278 | 117.8126
CA | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 13.8394 | 13.7011 | 13.5661 | 13.419 | 13.2817
CA | 6008_Biloela - Wowan 66 kV | Loading (MW) | 13.8174 | 13.68 | 13.5459 | 13.3998 | 13.2634
CA | 6008_Biloela - Wowan 66 kV | Power Factor | 0.99841 | 0.99846 | 0.99852 | 0.99857 | 0.99862
CA | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6008_Biloela - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6008_Biloela - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 0.97243 | 0.97346 | 0.97438 | 0.97538 | 0.9763
CA | 6008_Biloela - Wowan 66 kV | Contingency Outage | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV
CA | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 30.68% | 31.09% | 31.41% | 31.55% | 31.57%
CA | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1
CA | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 75.1559 | 76.1735 | 76.9641 | 77.2874 | 77.3533
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 8.9641 | 9.0849 | 9.1785 | 9.2164 | 9.2236
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 7.809 | 7.8899 | 7.9445 | 7.9385 | 7.9075
CA | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.87113 | 0.86846 | 0.86555 | 0.86135 | 0.85732
CA | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 245 | 245 | 245 | 245
CA | 6019_Gladstone South - Friend St 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6019_Gladstone South - Friend St 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0434 | 1.0433 | 1.0432 | 1.0431 | 1.0431
CA | 6019_Gladstone South - Friend St 66 kV | Contingency Outage | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV
CA | 6020_Gladstone South - BORE 66 kV | % of Rated A | 24.06% | 25.51% | 26.8% | 27.97% | 28.85%
CA | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1
CA | 6020_Gladstone South - BORE 66 kV | Loading (A) | 50.7589 | 53.8271 | 56.5411 | 59.0112 | 60.8794
CA | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 6.0614 | 6.4281 | 6.7524 | 7.0474 | 7.2706
CA | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 6.0604 | 6.4275 | 6.752 | 7.0473 | 7.2705
CA | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.99983 | 0.9999 | 0.99994 | 0.99997 | 0.99999
CA | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
CA | 6020_Gladstone South - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6020_Gladstone South - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0445 | 1.0446 | 1.0446 | 1.0446 | 1.0446
CA | 6020_Gladstone South - BORE 66 kV | Contingency Outage | 6024_Awoonga - Calliope 66kV | 6024_Awoonga - Calliope 66kV | 6024_Awoonga - Calliope 66kV | 6024_Awoonga - Calliope 66kV | 6024_Awoonga - Calliope 66kV
CA | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 7.783% | 8.221% | 8.612% | 8.974% | 9.255%
CA | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1
CA | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 48.4887 | 51.2164 | 53.654 | 55.9087 | 57.6569
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 5.7994 | 6.1257 | 6.4173 | 6.6869 | 6.8959
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 5.4041 | 5.7483 | 6.0545 | 6.3367 | 6.5548
CA | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.93145 | 0.93797 | 0.94302 | 0.94716 | 0.95006
CA | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 623 | 623 | 623 | 623
CA | 6022_Gladstone South - Calliope 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6022_Gladstone South - Calliope 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0463 | 1.0463 | 1.0463 | 1.0463 | 1.0462
CA | 6022_Gladstone South - Calliope 66 kV | Contingency Outage | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV
CA | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 13.93% | 14.79% | 15.59% | 16.38% | 17.02%
CA | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 61.1596 | 64.9453 | 68.4593 | 71.9051 | 74.7063
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 7.2942 | 7.7454 | 8.1642 | 8.5747 | 8.9084
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 7.0978 | 7.5826 | 8.0277 | 8.4596 | 8.8081
CA | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.97304 | 0.97896 | 0.98327 | 0.98656 | 0.98873
CA | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 439 | 439 | 439 | 439 | 439
CA | 6023_Friend St-Clinton Industrial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6023_Friend St-Clinton Industrial 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0433 | 1.0433 | 1.0432 | 1.0432 | 1.0431
CA | 6023_Friend St-Clinton Industrial 66 kV | Contingency Outage | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV
CA | 6024_Awoonga - Calliope 66kV | % of Rated A | 21.27% | 19.83% | 18.57% | 17.43% | 16.57%
CA | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1
CA | 6024_Awoonga - Calliope 66kV | Loading (A) | 35.951 | 33.506 | 31.3765 | 29.4587 | 28.0049
CA | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 4.3033 | 4.0133 | 3.7604 | 3.5324 | 3.3594
CA | 6024_Awoonga - Calliope 66kV | Loading (MW) | 3.7283 | 3.3903 | 3.0882 | 2.8082 | 2.5894
CA | 6024_Awoonga - Calliope 66kV | Power Factor | 0.86638 | 0.84476 | 0.82124 | 0.79498 | 0.7708
CA | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA | 6024_Awoonga - Calliope 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6024_Awoonga - Calliope 66kV | Min Voltage at Constrained Conductor (pu) | 1.0466 | 1.0475 | 1.0484 | 1.0489 | 1.0494
CA | 6024_Awoonga - Calliope 66kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 7.563% | 8.008% | 8.425% | 8.812% | 9.12%
CA | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 9.9827 | 10.571 | 11.1209 | 11.6317 | 12.039
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 1.2032 | 1.2748 | 1.3418 | 1.4041 | 1.4537
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 1.1693 | 1.2433 | 1.3124 | 1.3764 | 1.4274
CA | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.97185 | 0.97533 | 0.97808 | 0.98028 | 0.98184
CA | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6029_Littlemore - Miriam Vale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6029_Littlemore - Miriam Vale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0543 | 1.0549 | 1.0554 | 1.0559 | 1.0563
CA | 6029_Littlemore - Miriam Vale 66 kV | Contingency Outage | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV
CA | 6030_Littlemore - Monto 66 kV | % of Rated A | 15.71% | 16% | 16.29% | 16.58% | 16.82%
CA | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 22120_1 | TR_LINE 22120_1 | TR_LINE 22120_1 | TR_LINE 22120_1 | TR_LINE 22120_1
CA | 6030_Littlemore - Monto 66 kV | Loading (A) | 20.7312 | 21.1228 | 21.5063 | 21.884 | 22.2016
CA | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 2.5793 | 2.6337 | 2.6868 | 2.7394 | 2.7839
CA | 6030_Littlemore - Monto 66 kV | Loading (MW) | 1.2635 | 1.3576 | 1.4466 | 1.5313 | 1.6007
CA | 6030_Littlemore - Monto 66 kV | Power Factor | 0.48974 | 0.51533 | 0.53829 | 0.55887 | 0.57487
CA | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6030_Littlemore - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6030_Littlemore - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0884 | 1.0907 | 1.0929 | 1.095 | 1.0969
CA | 6030_Littlemore - Monto 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 19.27% | 19.84% | 20.43% | 21.08% | 21.68%
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 25.4353 | 26.1844 | 26.9649 | 27.8299 | 28.6177
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 3.112 | 3.2075 | 3.3065 | 3.4161 | 3.5159
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 1.1724 | 1.3898 | 1.5936 | 1.8007 | 1.9769
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.37669 | 0.43327 | 0.48194 | 0.52708 | 0.56222
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0703 | 1.0716 | 1.0727 | 1.0738 | 1.0747
CA | 6030_Littlemore - Monto 66 kV ¦ 6045_Coominglah Tee - Monto 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV
CA | 6031_Calliope - Littlemore 66 kV | % of Rated A | 22.77% | 23.33% | 23.93% | 24.59% | 25.19%
CA | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA | 6031_Calliope - Littlemore 66 kV | Loading (A) | 30.0551 | 30.8022 | 31.5841 | 32.4538 | 33.2515
CA | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 3.5968 | 3.6869 | 3.7811 | 3.8857 | 3.9817
CA | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 1.2591 | 1.4879 | 1.7027 | 1.9208 | 2.1069
CA | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.34974 | 0.40324 | 0.44998 | 0.49397 | 0.52878
CA | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6031_Calliope - Littlemore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6031_Calliope - Littlemore 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0469 | 1.0471 | 1.0472 | 1.0474 | 1.0475
CA | 6031_Calliope - Littlemore 66 kV | Contingency Outage | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 15.11% | 13.92% | 12.91% | 12.03% | 11.38%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 31.8843 | 29.3694 | 27.2407 | 25.3778 | 24.0151
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 3.8167 | 3.5173 | 3.2636 | 3.0415 | 2.8789
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 3.167 | 2.7984 | 2.4726 | 2.1724 | 1.9403
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.82979 | 0.79563 | 0.75762 | 0.71427 | 0.67396
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0471 | 1.0476 | 1.048 | 1.0484 | 1.0487
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 27.98% | 29.71% | 31.25% | 32.66% | 33.74%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 46.173 | 49.0196 | 51.5644 | 53.8928 | 55.6692
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 5.52 | 5.8615 | 6.1668 | 6.4461 | 6.6592
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 5.5185 | 5.8597 | 6.1647 | 6.4437 | 6.6566
CA | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.99972 | 0.99969 | 0.99966 | 0.99963 | 0.9996
CA | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 165 | 165 | 165 | 165
CA | 6034_Boyne Residential Tee - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6034_Boyne Residential Tee - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0457 | 1.0459 | 1.0461 | 1.0462 | 1.0463
CA | 6034_Boyne Residential Tee - BORE 66 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV
CA | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 1.813% | 1.813% | 1.813% | 1.813% | 1.813%
CA | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 4.6052 | 4.605 | 4.6048 | 4.6045 | 4.6043
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 0.54945 | 0.5494 | 0.54935 | 0.54929 | 0.54925
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 0.00026984 | 0.00026981 | 0.00026978 | 0.00026976 | 0.00026974
CA | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527 | 0.00048527
CA | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 254 | 254 | 254 | 254 | 254
CA | 6039_Clinton Industrial - Beecher 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6039_Clinton Industrial - Beecher 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0437 | 1.0437 | 1.0436 | 1.0436 | 1.0435
CA | 6039_Clinton Industrial - Beecher 66 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV
CA | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 2.775% | 2.775% | 2.775% | 2.775% | 2.775%
CA | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 3.6633 | 3.6631 | 3.6629 | 3.6627 | 3.6626
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 0.43719 | 0.43715 | 0.4371 | 0.43706 | 0.43703
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 0.00017571 | 0.00017569 | 0.00017568 | 0.00017566 | 0.00017565
CA | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831 | 0.00026831
CA | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6041_Yarwun - Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6041_Yarwun - Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.044 | 1.0439 | 1.0439 | 1.0438 | 1.0438
CA | 6041_Yarwun - Boat Creek 66 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 12.22% | 12.22% | 12.22% | 12.21% | 12.21%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 16.1352 | 16.1295 | 16.1243 | 16.1189 | 16.1152
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 1.929 | 1.9291 | 1.9291 | 1.9291 | 1.9291
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 1.9149 | 1.9149 | 1.9149 | 1.9149 | 1.9149
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.99269 | 0.99267 | 0.99265 | 0.99263 | 0.99262
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0458 | 1.0462 | 1.0466 | 1.0469 | 1.0472
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Contingency Outage | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 4.04% | 4.056% | 4.204% | 4.49% | 4.829%
CA | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 5.3325 | 5.3538 | 5.5499 | 5.9267 | 6.3739
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 0.64457 | 0.64763 | 0.67176 | 0.71783 | 0.77244
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 0.054014 | 0.072035 | 0.18959 | 0.31496 | 0.42455
CA | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.083798 | 0.11122 | 0.28223 | 0.43876 | 0.54961
CA | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6045_Coominglah Tee - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0574 | 1.0582 | 1.0588 | 1.0595 | 1.0601
CA | 6045_Coominglah Tee - Monto 66 kV | Contingency Outage | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV
CA | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 87.66% | 87.33% | 87.02% | 86.72% | 86.45%
CA | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 115.7063 | 115.2744 | 114.8708 | 114.464 | 114.1132
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 12.2146 | 12.2145 | 12.2144 | 12.2143 | 12.2142
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 12.2146 | 12.2145 | 12.2144 | 12.2143 | 12.2142
CA | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6046_Mt Morgan - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6046_Mt Morgan - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 0.9234 | 0.92685 | 0.9301 | 0.9334 | 0.93626
CA | 6046_Mt Morgan - Wowan 66 kV | Contingency Outage | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV
CA | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 0.4826% | 0.5397% | 0.5956% | 0.6533% | 0.7062%
CA | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 0.74313 | 0.83121 | 0.91716 | 1.0061 | 1.0876
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 0.088929 | 0.099551 | 0.10992 | 0.12067 | 0.13054
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 0.088924 | 0.099547 | 0.10992 | 0.12067 | 0.13053
CA | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.99994 | 0.99996 | 0.99997 | 0.99998 | 0.99999
CA | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 154 | 154 | 154 | 154
CA | 6047_Coominglah Sub Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6047_Coominglah Sub Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0468 | 1.0477 | 1.0484 | 1.0492 | 1.0499
CA | 6047_Coominglah Sub Tee 66 kV | Contingency Outage | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV
CA | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 14.69% | 15.3% | 16.17% | 16.9% | 17.4%
CA | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 58.9218 | 61.356 | 64.8255 | 67.7857 | 69.7753
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 7.0596 | 7.3824 | 7.803 | 8.1624 | 8.4041
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 7.0378 | 7.3805 | 7.8009 | 8.1599 | 8.4014
CA | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.99689 | 0.99975 | 0.99972 | 0.9997 | 0.99968
CA | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA | 6050_Parkhurst - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6050_Parkhurst - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0481 | 1.0525 | 1.0529 | 1.0533 | 1.0536
CA | 6050_Parkhurst - Frenchville 66 kV | Contingency Outage | 6075_Keppel - Farnborough 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV
CA | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 54.77% | 60.34% | 65.7% | 71.1% | 75.67%
CA | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 116.1174 | 127.9217 | 139.2758 | 150.7307 | 160.4265
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 14.3825 | 15.8865 | 17.3391 | 18.8101 | 20.059
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 14.0905 | 15.6333 | 17.1177 | 18.6166 | 19.8863
CA | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.97968 | 0.98406 | 0.98723 | 0.98971 | 0.99139
CA | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA | 6051_Parkhurst - Keppel 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6051_Parkhurst - Keppel 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0813 | 1.0838 | 1.0862 | 1.0885 | 1.0905
CA | 6051_Parkhurst - Keppel 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 6052_Pandoin - Kunwarara 66 kV | % of Rated A | 18.96% | 18.96% | 18.96% | 18.95% | 18.95%
CA | 6052_Pandoin - Kunwarara 66 kV | Limiting Line Name | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (A) | 65.7795 | 65.7772 | 65.7747 | 65.7729 | 65.7723
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MVA) | 7.5907 | 7.5907 | 7.5907 | 7.5907 | 7.5907
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MW) | 7.5837 | 7.5837 | 7.5836 | 7.5836 | 7.5836
CA | 6052_Pandoin - Kunwarara 66 kV | Power Factor | 0.99822 | 0.99822 | 0.99822 | 0.99822 | 0.99822
CA | 6052_Pandoin - Kunwarara 66 kV | Rating (A) | 347 | 347 | 347 | 347 | 347
CA | 6052_Pandoin - Kunwarara 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6052_Pandoin - Kunwarara 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0026 | 1.0026 | 1.0027 | 1.0027 | 1.0027
CA | 6052_Pandoin - Kunwarara 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 21.1% | 22.33% | 23.52% | 24.7% | 25.66%
CA | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 110.3575 | 116.7757 | 122.9921 | 129.1768 | 134.214
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 13.219 | 13.9977 | 14.7519 | 15.5009 | 16.1116
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 10.6408 | 11.5748 | 12.4657 | 13.3577 | 14.059
CA | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.80402 | 0.82637 | 0.84483 | 0.86173 | 0.8726
CA | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 523 | 523 | 523 | 523
CA | 6053_Parkhurst - Pandoin 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6053_Parkhurst - Pandoin 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0465 | 1.0467 | 1.0468 | 1.0468 | 1.0468
CA | 6053_Parkhurst - Pandoin 66 kV | Contingency Outage | 6087_Glenmore - QMAG Tee 66 kV | 6087_Glenmore - QMAG Tee 66 kV | 6087_Glenmore - QMAG Tee 66 kV | 6087_Glenmore - QMAG Tee 66 kV | 6087_Glenmore - QMAG Tee 66 kV
CA | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 45.11% | 45.11% | 45.11% | 45.11% | 45.11%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 76.2428 | 76.2364 | 76.232 | 76.2292 | 76.2277
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 9.0595 | 9.0595 | 9.0595 | 9.0595 | 9.0595
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 9.0595 | 9.0594 | 9.0594 | 9.0594 | 9.0594
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.99982 | 0.99982 | 0.99982 | 0.99982 | 0.99982
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0286 | 1.0287 | 1.0287 | 1.0288 | 1.0288
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV
CA | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 29.33% | 32.21% | 34.99% | 37.79% | 40.17%
CA | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | 6074_Lakes Creek | 6074_Lakes Creek | 6074_Lakes Creek | 6074_Lakes Creek | 6074_Lakes Creek
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 117.0393 | 128.5265 | 139.5997 | 150.79 | 160.2731
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 14.2037 | 15.6066 | 16.9601 | 18.3284 | 19.4879
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 13.7861 | 15.263 | 16.6775 | 18.0992 | 19.2985
CA | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.9706 | 0.97798 | 0.98334 | 0.9875 | 0.99028
CA | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
CA | 6074_Lakes Creek - Tanby 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6074_Lakes Creek - Tanby 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0616 | 1.0622 | 1.0627 | 1.0632 | 1.0636
CA | 6074_Lakes Creek - Tanby 66 kV | Contingency Outage | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV
CA | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.3268% | 0.3277% | 0.3285% | 0.3292% | 0.3298%
CA | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.2355 | 1.2386 | 1.2415 | 1.2444 | 1.2468
CA | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.15311 | 0.15389 | 0.15462 | 0.15534 | 0.15594
CA | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.8152e-06 | 3.8347e-06 | 3.853e-06 | 3.871e-06 | 3.8858e-06
CA | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.19e-06 | 2.1906e-06 | 2.1905e-06 | 2.1921e-06 | 2.1939e-06
CA | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
CA | 6075_Keppel - Farnborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6075_Keppel - Farnborough 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0841 | 1.0869 | 1.0894 | 1.092 | 1.0941
CA | 6075_Keppel - Farnborough 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 54.63% | 60.21% | 65.58% | 71% | 75.58%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 115.8124 | 127.6508 | 139.0328 | 150.5122 | 160.2264
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 14.3534 | 15.8609 | 17.3165 | 18.79 | 20.0409
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 14.0914 | 15.6343 | 17.1189 | 18.618 | 19.8879
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.98174 | 0.98571 | 0.98859 | 0.99084 | 0.99237
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0841 | 1.0869 | 1.0894 | 1.092 | 1.0941
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA | 6087_Glenmore - QMAG Tee 66 kV | % of Rated A | 18.03% | 18.04% | 18.06% | 18.09% | 18.12%
CA | 6087_Glenmore - QMAG Tee 66 kV | Limiting Line Name | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (A) | 72.2971 | 72.359 | 72.4131 | 72.5485 | 72.6596
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MVA) | 8.6608 | 8.6696 | 8.6773 | 8.6946 | 8.7085
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MW) | 8.6204 | 8.6297 | 8.638 | 8.6561 | 8.6709
CA | 6087_Glenmore - QMAG Tee 66 kV | Power Factor | 0.99517 | 0.99523 | 0.9953 | 0.99541 | 0.99552
CA | 6087_Glenmore - QMAG Tee 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA | 6087_Glenmore - QMAG Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6087_Glenmore - QMAG Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0473 | 1.0474 | 1.0476 | 1.0477 | 1.0478
CA | 6087_Glenmore - QMAG Tee 66 kV | Contingency Outage | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV
CA | 6088_QMAG Tee - Parkhurst 66 kV | % of Rated A | 34.95% | 36.11% | 37.39% | 38.65% | 39.68%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Limiting Line Name | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (A) | 121.2676 | 125.3095 | 129.7522 | 134.1286 | 137.6898
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MVA) | 14.5598 | 15.1576 | 15.7026 | 16.2395 | 16.676
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MW) | 14.5566 | 14.9814 | 15.5378 | 16.0855 | 16.5308
CA | 6088_QMAG Tee - Parkhurst 66 kV | Power Factor | 0.99978 | 0.98838 | 0.98951 | 0.99052 | 0.99129
CA | 6088_QMAG Tee - Parkhurst 66 kV | Rating (A) | 347 | 347 | 347 | 347 | 347
CA | 6088_QMAG Tee - Parkhurst 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6088_QMAG Tee - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0493 | 1.0571 | 1.0575 | 1.058 | 1.0583
CA | 6088_QMAG Tee - Parkhurst 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA | 6089_QMAG Tee - QMAG 66 kV | % of Rated A | 38.55% | 38.55% | 38.54% | 38.54% | 38.54%
CA | 6089_QMAG Tee - QMAG 66 kV | Limiting Line Name | TR_LINE 22236_1 | TR_LINE 22236_1 | TR_LINE 22236_1 | TR_LINE 22236_1 | TR_LINE 22236_1
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (A) | 154.5999 | 154.5752 | 154.5535 | 154.5359 | 154.5269
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MVA) | 18.501 | 18.501 | 18.501 | 18.501 | 18.501
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MW) | 18.501 | 18.501 | 18.501 | 18.501 | 18.501
CA | 6089_QMAG Tee - QMAG 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA | 6089_QMAG Tee - QMAG 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA | 6089_QMAG Tee - QMAG 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6089_QMAG Tee - QMAG 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0468 | 1.047 | 1.0471 | 1.0472 | 1.0473
CA | 6089_QMAG Tee - QMAG 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV
CA | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 13.9% | 13.43% | 13% | 12.53% | 12.15%
CA | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 18.3495 | 17.724 | 17.1582 | 16.5352 | 16.0363
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 2.2062 | 2.1312 | 2.0634 | 1.9886 | 1.9287
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 2.1095 | 2.0304 | 1.9586 | 1.8792 | 1.8153
CA | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.95618 | 0.95271 | 0.94923 | 0.94498 | 0.94121
CA | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6090_Egan's Hill - Raglan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6090_Egan's Hill - Raglan 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0515 | 1.0516 | 1.0517 | 1.0518 | 1.0519
CA | 6090_Egan's Hill - Raglan 66 kV | Contingency Outage | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 73.43% | 73.2% | 73.19% | 73.19% | 73.19%
CA | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 22265_1 | TR_LINE 22265_1 | TR_LINE 22265_1 | TR_LINE 22265_1 | TR_LINE 22265_1
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 105.0089 | 104.6715 | 104.6636 | 104.6573 | 104.6572
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 12.6271 | 12.5608 | 12.5608 | 12.5607 | 12.5607
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 12.617 | 12.5507 | 12.5506 | 12.5506 | 12.5506
CA | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.9992 | 0.99919 | 0.99919 | 0.99919 | 0.99919
CA | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA | 6091_Egan's Hill - Gavial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6091_Egan's Hill - Gavial 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0516 | 1.0495 | 1.0495 | 1.0496 | 1.0496
CA | 6091_Egan's Hill - Gavial 66 kV | Contingency Outage | 6008_Biloela - Wowan 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV
CA | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 79.52% | 79.27% | 79.26% | 79.26% | 79.26%
CA | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 104.9695 | 104.6322 | 104.6242 | 104.6179 | 104.6178
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 12.5035 | 12.438 | 12.4379 | 12.4379 | 12.4379
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 12.4931 | 12.4275 | 12.4275 | 12.4275 | 12.4275
CA | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.99905 | 0.99904 | 0.99904 | 0.99904 | 0.99904
CA | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA | 6093_Gavial - Mt Morgan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6093_Gavial - Mt Morgan 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0274 | 1.0253 | 1.0254 | 1.0255 | 1.0255
CA | 6093_Gavial - Mt Morgan 66 kV | Contingency Outage | 6008_Biloela - Wowan 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV
CA | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 24.61% | 25.87% | 27.11% | 28.34% | 29.4%
CA | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 41.5906 | 43.7262 | 45.8163 | 47.8906 | 49.6782
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 5.0099 | 5.2683 | 5.5212 | 5.7723 | 5.9885
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 5.0089 | 5.2672 | 5.5199 | 5.7708 | 5.9868
CA | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.99981 | 0.99979 | 0.99977 | 0.99975 | 0.99973
CA | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA | 6094_Malchi Tee - Malchi 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6094_Malchi Tee - Malchi 66 kV | Min Voltage at Constrained Conductor (pu) | 1.051 | 1.051 | 1.0511 | 1.0512 | 1.0512
CA | 6094_Malchi Tee - Malchi 66 kV | Contingency Outage | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 23.82% | 23.9% | 23.99% | 24.08% | 24.19%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 59.0651 | 59.2814 | 59.4917 | 59.7183 | 60.0014
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 7.1051 | 7.1324 | 7.159 | 7.1874 | 7.2221
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 1.3468 | 1.4613 | 1.573 | 1.6867 | 1.8175
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.18877 | 0.20413 | 0.21899 | 0.23398 | 0.25098
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0523 | 1.0525 | 1.0527 | 1.0528 | 1.0529
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Contingency Outage | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA | 6096_Egan's Hill - Lakes Creek 66 kV | % of Rated A | 30.08% | 31.48% | 33% | 34.64% | 36.08%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Limiting Line Name | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (A) | 96.5656 | 101.0592 | 105.917 | 111.1821 | 115.8277
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MVA) | 11.7418 | 12.2965 | 12.8957 | 13.5448 | 14.117
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MW) | 5.2583 | 6.4283 | 7.5419 | 8.6402 | 9.5455
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Power Factor | 0.4473 | 0.52229 | 0.58442 | 0.63754 | 0.67587
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Rating (A) | 321 | 321 | 321 | 321 | 321
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0636 | 1.0642 | 1.0647 | 1.0652 | 1.0656
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 18.32% | 18.26% | 18.2% | 18.14% | 18.07%
CA | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1
CA | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 45.4267 | 45.2921 | 45.1413 | 44.9774 | 44.8136
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 5.4684 | 5.4533 | 5.4363 | 5.4175 | 5.3983
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 0.25319 | 0.25541 | 0.26534 | 0.27832 | 0.27156
CA | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.045235 | 0.045773 | 0.047751 | 0.050319 | 0.049254
CA | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
CA | 6097_Egan's Hill - Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6097_Egan's Hill - Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 1.053 | 1.0533 | 1.0535 | 1.0537 | 1.0538
CA | 6097_Egan's Hill - Canning 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA | 6100_Boat Creek - ICI 66 kV | % of Rated A | 7.812% | 7.858% | 7.859% | 7.859% | 7.86%
CA | 6100_Boat Creek - ICI 66 kV | Limiting Line Name | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1
CA | 6100_Boat Creek - ICI 66 kV | Loading (A) | 57.8113 | 58.1502 | 58.1543 | 58.1585 | 58.162
CA | 6100_Boat Creek - ICI 66 kV | Loading (MVA) | 6.716 | 6.7158 | 6.7158 | 6.7158 | 6.7158
CA | 6100_Boat Creek - ICI 66 kV | Loading (MW) | 6.7137 | 6.7135 | 6.7135 | 6.7135 | 6.7135
CA | 6100_Boat Creek - ICI 66 kV | Power Factor | 0.99964 | 0.99965 | 0.99965 | 0.99965 | 0.99965
CA | 6100_Boat Creek - ICI 66 kV | Rating (A) | 740 | 740 | 740 | 740 | 740
CA | 6100_Boat Creek - ICI 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6100_Boat Creek - ICI 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0162 | 1.0102 | 1.0102 | 1.0101 | 1.01
CA | 6100_Boat Creek - ICI 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 1.542% | 1.551% | 1.551% | 1.551% | 1.551%
CA | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 4.3173 | 4.3425 | 4.3428 | 4.3431 | 4.3434
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 0.50153 | 0.50149 | 0.50149 | 0.50149 | 0.50149
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 0.50019 | 0.50019 | 0.50019 | 0.50019 | 0.50019
CA | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.99734 | 0.9974 | 0.99741 | 0.99741 | 0.99741
CA | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 280 | 280 | 280 | 280 | 280
CA | 6102_Boat Creek - Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6102_Boat Creek - Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0161 | 1.0101 | 1.01 | 1.01 | 1.0099
CA | 6102_Boat Creek - Yarwun 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 85.5% | 85.78% | 85.78% | 85.79% | 85.79%
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 239.4117 | 240.1718 | 240.1888 | 240.2065 | 240.221
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.905 | 27.9063 | 27.9063 | 27.9064 | 27.9064
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 27.9048 | 27.9061 | 27.9062 | 27.9062 | 27.9062
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 280 | 280 | 280 | 280
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0126 | 1.0094 | 1.0093 | 1.0092 | 1.0092
CA | 6102_Boat Creek - Yarwun 66 kV ¦ 6103_Fisherman Landing-Boat Creek 66 kV | Contingency Outage | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV | 6103_Fisherman Landing-Boat Creek 66 kV
CA | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 83.97% | 84.47% | 84.47% | 84.48% | 84.49%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 235.1116 | 236.5101 | 236.5268 | 236.5441 | 236.5584
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.2031 | 27.2032 | 27.2032 | 27.2032 | 27.2032
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 27.2031 | 27.2032 | 27.2032 | 27.2032 | 27.2032
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 280 | 280 | 280 | 280
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 1.012 | 1.006 | 1.006 | 1.0059 | 1.0058
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 30.99% | 29.18% | 27.52% | 25.89% | 24.6%
CA | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1
CA | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 112.4756 | 105.9087 | 99.9121 | 93.992 | 89.3
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 13.3694 | 12.5871 | 11.8728 | 11.1678 | 10.6092
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 11.3689 | 10.5032 | 9.701 | 8.8903 | 8.2339
CA | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.85028 | 0.83442 | 0.81707 | 0.79607 | 0.77611
CA | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 363 | 363 | 363 | 363
CA | 6109_Gladstone North - Clinton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6109_Gladstone North - Clinton 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0398 | 1.0397 | 1.0395 | 1.0394 | 1.0393
CA | 6109_Gladstone North - Clinton 66 kV | Contingency Outage | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV
CA | 6110_Port Curtis 66 kV | % of Rated A | 39.03% | 39.03% | 39.03% | 39.04% | 39.04%
CA | 6110_Port Curtis 66 kV | Limiting Line Name | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1
CA | 6110_Port Curtis 66 kV | Loading (A) | 141.6641 | 141.6799 | 141.6954 | 141.7107 | 141.7231
CA | 6110_Port Curtis 66 kV | Loading (MVA) | 16.8404 | 16.8405 | 16.8405 | 16.8405 | 16.8405
CA | 6110_Port Curtis 66 kV | Loading (MW) | 16.8343 | 16.8343 | 16.8343 | 16.8343 | 16.8343
CA | 6110_Port Curtis 66 kV | Power Factor | 0.99963 | 0.99963 | 0.99963 | 0.99963 | 0.99963
CA | 6110_Port Curtis 66 kV | Rating (A) | 363 | 363 | 363 | 363 | 363
CA | 6110_Port Curtis 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6110_Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0389 | 1.0388 | 1.0387 | 1.0386 | 1.0385
CA | 6110_Port Curtis 66 kV | Contingency Outage | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV
CA | 6111_Gladstone North - Port Curtis 66 kV | % of Rated A | 39.05% | 39.06% | 39.06% | 39.07% | 39.07%
CA | 6111_Gladstone North - Port Curtis 66 kV | Limiting Line Name | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (A) | 141.7582 | 141.7784 | 141.798 | 141.8176 | 141.8335
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MVA) | 16.8404 | 16.8404 | 16.8404 | 16.8405 | 16.8405
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MW) | 16.8342 | 16.8343 | 16.8343 | 16.8343 | 16.8343
CA | 6111_Gladstone North - Port Curtis 66 kV | Power Factor | 0.99963 | 0.99963 | 0.99963 | 0.99963 | 0.99963
CA | 6111_Gladstone North - Port Curtis 66 kV | Rating (A) | 363 | 363 | 363 | 363 | 363
CA | 6111_Gladstone North - Port Curtis 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6111_Gladstone North - Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0382 | 1.0381 | 1.0379 | 1.0378 | 1.0377
CA | 6111_Gladstone North - Port Curtis 66 kV | Contingency Outage | 6110_Port Curtis 66 kV | 6110_Port Curtis 66 kV | 6110_Port Curtis 66 kV | 6110_Port Curtis 66 kV | 6110_Port Curtis 66 kV
CA | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 17.45% | 19.4% | 21.29% | 23.25% | 24.93%
CA | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1
CA | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 65.979 | 73.3271 | 80.4885 | 87.8709 | 94.2391
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 8.3177 | 9.2723 | 10.2072 | 11.1748 | 12.012
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 7.535 | 8.5826 | 9.5911 | 10.6223 | 11.5068
CA | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.90579 | 0.92551 | 0.93956 | 0.9505 | 0.9579
CA | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
CA | 6298_Tanby - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6298_Tanby - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 1.1028 | 1.1061 | 1.1093 | 1.1124 | 1.1149
CA | 6298_Tanby - Yeppoon 66 kV | Contingency Outage | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV
CA | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 20.37% | 21.8% | 23.21% | 24.66% | 25.87%
CA | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | TR_LINE 20950_1 | TR_LINE 20950_1 | TR_LINE 20950_1 | TR_LINE 20950_1 | TR_LINE 20950_1
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 81.6962 | 87.4064 | 93.0756 | 98.8764 | 103.7468
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 9.8634 | 10.5571 | 11.246 | 11.9508 | 12.5424
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 7.9664 | 8.8737 | 9.7444 | 10.6123 | 11.3279
CA | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.80752 | 0.84042 | 0.86639 | 0.88793 | 0.90313
CA | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA | 6310_Lakes Creek - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6310_Lakes Creek - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0561 | 1.0565 | 1.0568 | 1.0572 | 1.0574
CA | 6310_Lakes Creek - Berserker 66 kV | Contingency Outage | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV | 6075_Keppel - Farnborough 66 kV
CA | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 27.68% | 32.22% | 32.2% | 32.19% | 32.18%
CA | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 246.065 | 286.4027 | 286.285 | 286.1793 | 286.093
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 59.0578 | 68.6407 | 68.6076 | 68.5772 | 68.5523
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 58.6222 | 67.6683 | 67.6354 | 67.6052 | 67.5806
CA | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.99263 | 0.98583 | 0.98583 | 0.98583 | 0.98582
CA | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA | 7290_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7290_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0497 | 1.0482 | 1.0481 | 1.048 | 1.0479
CA | 7290_Boat Creek - Yarwun 132 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 27.68% | 32.21% | 32.2% | 32.19% | 32.18%
CA | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 246.047 | 286.3724 | 286.2547 | 286.149 | 286.0627
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 59.0551 | 68.6359 | 68.6028 | 68.5724 | 68.5475
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 58.6212 | 67.6669 | 67.6341 | 67.6039 | 67.5792
CA | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.99265 | 0.98588 | 0.98588 | 0.98588 | 0.98587
CA | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA | 7291_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7291_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0497 | 1.0482 | 1.0481 | 1.0481 | 1.048
CA | 7291_Boat Creek - Yarwun 132 kV | Contingency Outage | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV
CA | 6026_Moura - Theodore 66 kV | % of Rated A | 5.188% | 5.082% | 4.987% | 4.881% | 4.793%
CA | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1
CA | 6026_Moura - Theodore 66 kV | Loading (A) | 37.8192 | 37.0499 | 36.3522 | 35.5846 | 34.9404
CA | 6026_Moura - Theodore 66 kV | Loading (MVA) | 4.4484 | 4.3589 | 4.2775 | 4.1879 | 4.1127
CA | 6026_Moura - Theodore 66 kV | Loading (MW) | 4.3851 | 4.2929 | 4.209 | 4.1166 | 4.0388
CA | 6026_Moura - Theodore 66 kV | Power Factor | 0.98578 | 0.98487 | 0.98399 | 0.98296 | 0.98204
CA | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
CA | 6026_Moura - Theodore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6026_Moura - Theodore 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0289 | 1.0292 | 1.0293 | 1.0295 | 1.0297
CA | 6026_Moura - Theodore 66 kV | Contingency Outage | 6028_Moura-Ammonium Nitrate Plant 66 kV | 6028_Moura-Ammonium Nitrate Plant 66 kV | 6028_Moura-Ammonium Nitrate Plant 66 kV | 6028_Moura-Ammonium Nitrate Plant 66 kV | 6028_Moura-Ammonium Nitrate Plant 66 kV
FN | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 13.39% | 13.15% | 12.93% | 12.55% | 12.24%
FN | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 55.9798 | 54.9709 | 54.0309 | 52.455 | 51.1727
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 13.4367 | 13.1945 | 12.969 | 12.5908 | 12.283
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 13.43 | 13.187 | 12.9605 | 12.5807 | 12.2716
FN | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.9995 | 0.99943 | 0.99935 | 0.9992 | 0.99907
FN | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 418 | 418 | 418 | 418
FN | 7206 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7206 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 1.0494 | 1.0494 | 1.0494 | 1.0495 | 1.0495
FN | 7206 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City
FN | 7227 Woree-Cairns Terminal-Cairns City | % of Rated A | 13.39% | 13.15% | 12.93% | 12.55% | 12.24%
FN | 7227 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (A) | 55.9788 | 54.9696 | 54.0294 | 52.4533 | 51.1708
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 13.4366 | 13.1945 | 12.9689 | 12.5907 | 12.283
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MW) | 13.4299 | 13.1869 | 12.9605 | 12.5807 | 12.2716
FN | 7227 Woree-Cairns Terminal-Cairns City | Power Factor | 0.9995 | 0.99943 | 0.99935 | 0.99921 | 0.99907
FN | 7227 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 418 | 418 | 418 | 418
FN | 7227 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7227 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 1.0498 | 1.0499 | 1.0499 | 1.0499 | 1.0499
FN | 7227 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City
FN | 7332_Cairns North 132 kV | % of Rated A | 15.03% | 15.12% | 15.3% | 15.57% | 15.85%
FN | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN | 7332_Cairns North 132 kV | Loading (A) | 71.1094 | 71.5093 | 72.3694 | 73.6547 | 74.9724
FN | 7332_Cairns North 132 kV | Loading (MVA) | 17.0707 | 17.1667 | 17.3732 | 17.6817 | 17.998
FN | 7332_Cairns North 132 kV | Loading (MW) | 0.38963 | 1.9086 | 3.3844 | 4.8374 | 5.9925
FN | 7332_Cairns North 132 kV | Power Factor | 0.022816 | 0.11117 | 0.1948 | 0.27357 | 0.33294
FN | 7332_Cairns North 132 kV | Rating (A) | 473 | 473 | 473 | 473 | 473
FN | 7332_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7332_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
FN | 7332_Cairns North 132 kV | Contingency Outage | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV
FN | 7333_Cairns North 132 kV | % of Rated A | 15.12% | 15.2% | 15.38% | 15.65% | 15.93%
FN | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN | 7333_Cairns North 132 kV | Loading (A) | 71.5145 | 71.9097 | 72.7597 | 74.0303 | 75.3332
FN | 7333_Cairns North 132 kV | Loading (MVA) | 17.1679 | 17.2628 | 17.4669 | 17.7719 | 18.0847
FN | 7333_Cairns North 132 kV | Loading (MW) | 0.38823 | 1.9072 | 3.383 | 4.836 | 5.9911
FN | 7333_Cairns North 132 kV | Power Factor | 0.022604 | 0.11047 | 0.19367 | 0.2721 | 0.33127
FN | 7333_Cairns North 132 kV | Rating (A) | 473 | 473 | 473 | 473 | 473
FN | 7333_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7333_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
FN | 7333_Cairns North 132 kV | Contingency Outage | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV
FN | 3CRO_Croydon 66 kV | % of Rated A | 3.962% | 3.73% | 3.729% | 3.729% | 3.728%
FN | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN | 3CRO_Croydon 66 kV | Loading (A) | 18.1069 | 17.0465 | 17.0431 | 17.04 | 17.0377
FN | 3CRO_Croydon 66 kV | Loading (MVA) | 2.1781 | 2.059 | 2.0588 | 2.0585 | 2.0584
FN | 3CRO_Croydon 66 kV | Loading (MW) | 0.95994 | 0.12494 | 0.11229 | 0.098108 | 0.085598
FN | 3CRO_Croydon 66 kV | Power Factor | 0.44073 | 0.060677 | 0.054543 | 0.047659 | 0.041585
FN | 3CRO_Croydon 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN | 3CRO_Croydon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3CRO_Croydon 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0523 | 1.0566 | 1.0567 | 1.0568 | 1.0568
FN | 3CRO_Croydon 66 kV | Contingency Outage | Kidston Solar Farm (Genex) | 3NOR_Normanton 66 kV | 3NOR_Normanton 66 kV | 3NOR_Normanton 66 kV | 3NOR_Normanton 66 kV
FN | 3NOR_Normanton 66 kV | % of Rated A | 4.436% | 4.588% | 4.606% | 4.637% | 4.671%
FN | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN | 3NOR_Normanton 66 kV | Loading (A) | 20.2739 | 20.9653 | 21.0514 | 21.1904 | 21.3458
FN | 3NOR_Normanton 66 kV | Loading (MVA) | 2.4107 | 2.4944 | 2.5051 | 2.5222 | 2.5411
FN | 3NOR_Normanton 66 kV | Loading (MW) | 0.81916 | 0.71338 | 0.61178 | 0.49757 | 0.39915
FN | 3NOR_Normanton 66 kV | Power Factor | 0.33589 | 0.28195 | 0.24025 | 0.19337 | 0.15317
FN | 3NOR_Normanton 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN | 3NOR_Normanton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3NOR_Normanton 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0401 | 1.0408 | 1.041 | 1.0412 | 1.0414
FN | 3NOR_Normanton 66 kV | Contingency Outage | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | 2MOU_Mourilyan 22 kV | 2MOU_Mourilyan 22 kV | 2MOU_Mourilyan 22 kV
FN | 4KID_Ross - Kidston 132 kV | % of Rated A | 19.24% | 19.52% | 19.52% | 19.52% | 19.52%
FN | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN | 4KID_Ross - Kidston 132 kV | Loading (A) | 68.3018 | 69.2882 | 69.2873 | 69.2881 | 69.288
FN | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 16.3951 | 16.6319 | 16.6317 | 16.6319 | 16.6319
FN | 4KID_Ross - Kidston 132 kV | Loading (MW) | 0.22816 | 2.6266 | 2.6252 | 2.6265 | 2.6263
FN | 4KID_Ross - Kidston 132 kV | Power Factor | 0.013916 | 0.14026 | 0.14018 | 0.14025 | 0.14024
FN | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 355 | 355 | 355 | 355
FN | 4KID_Ross - Kidston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 4KID_Ross - Kidston 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0499 | 1.0499 | 1.0499 | 1.0499 | 1.0499
FN | 4KID_Ross - Kidston 132 kV | Contingency Outage | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV
FN | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 10.2% | 10.87% | 10.88% | 10.89% | 10.9%
FN | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 30.3864 | 32.3817 | 32.4177 | 32.457 | 32.4895
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 7.507 | 8.03 | 8.0394 | 8.0498 | 8.0584
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 0.18379 | 0.14726 | 0.1077 | 0.067388 | 0.033884
FN | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.021721 | 0.015276 | 0.010328 | 0.0052974 | 0.001126
FN | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 298 | 298 | 298 | 298
FN | 7216_4GEO (Georgetown) 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7216_4GEO (Georgetown) 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0806 | 1.0846 | 1.0847 | 1.0848 | 1.0848
FN | 7216_4GEO (Georgetown) 132 kV | Contingency Outage | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV
FN | 3AT1_Atherton No 1 66 kV | % of Rated A | 7.793% | 8.133% | 8.773% | 9.667% | 10.57%
FN | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1
FN | 3AT1_Atherton No 1 66 kV | Loading (A) | 42.704 | 44.571 | 48.0749 | 52.9737 | 57.9188
FN | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 5.3003 | 5.5372 | 5.9774 | 6.5919 | 7.2119
FN | 3AT1_Atherton No 1 66 kV | Loading (MW) | 0.41777 | 1.6268 | 2.7785 | 3.9414 | 4.9237
FN | 3AT1_Atherton No 1 66 kV | Power Factor | 0.078688 | 0.29365 | 0.46469 | 0.59775 | 0.68255
FN | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN | 3AT1_Atherton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3AT1_Atherton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0857 | 1.0868 | 1.0876 | 1.0885 | 1.0892
FN | 3AT1_Atherton No 1 66 kV | Contingency Outage | 3MO2_Mossman No 2 66 kV | 3MO2_Mossman No 2 66 kV | 3MO2_Mossman No 2 66 kV | 3MO2_Mossman No 2 66 kV | 3MO2_Mossman No 2 66 kV
FN | 3AT2_Atherton No 2 66 kV | % of Rated A | 5.782% | 6.239% | 7.064% | 8.161% | 9.226%
FN | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1
FN | 3AT2_Atherton No 2 66 kV | Loading (A) | 31.6831 | 34.1918 | 38.7086 | 44.7246 | 50.561
FN | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 3.9223 | 4.2369 | 4.8005 | 5.5512 | 6.2796
FN | 3AT2_Atherton No 2 66 kV | Loading (MW) | 0.44457 | 1.6536 | 2.8053 | 3.9682 | 4.9505
FN | 3AT2_Atherton No 2 66 kV | Power Factor | 0.11324 | 0.39017 | 0.58426 | 0.7147 | 0.78819
FN | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN | 3AT2_Atherton No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3AT2_Atherton No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.083 | 1.084 | 1.0849 | 1.0858 | 1.0864
FN | 3AT2_Atherton No 2 66 kV | Contingency Outage | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV
FN | 3CHI_Chillagoe 66 kV | % of Rated A | 2.576% | 2.576% | 2.575% | 2.576% | 2.576%
FN | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1
FN | 3CHI_Chillagoe 66 kV | Loading (A) | 14.1176 | 14.1151 | 14.1132 | 14.1142 | 14.1156
FN | 3CHI_Chillagoe 66 kV | Loading (MVA) | 1.7621 | 1.7639 | 1.7656 | 1.7677 | 1.7695
FN | 3CHI_Chillagoe 66 kV | Loading (MW) | 0.2142 | 0.19226 | 0.17108 | 0.14992 | 0.13192
FN | 3CHI_Chillagoe 66 kV | Power Factor | 0.12156 | 0.10899 | 0.096897 | 0.084812 | 0.074553
FN | 3CHI_Chillagoe 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN | 3CHI_Chillagoe 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3CHI_Chillagoe 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0918 | 1.0932 | 1.0944 | 1.0956 | 1.0966
FN | 3CHI_Chillagoe 66 kV | Contingency Outage | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 2MOS_Mossman 22 kV | 2MOS_Mossman 22 kV
FN | 3COO_Cooktown 66 kV | % of Rated A | 1.249% | 1.119% | 1.056% | 1.075% | 1.162%
FN | 3COO_Cooktown 66 kV | Limiting Line Name | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1
FN | 3COO_Cooktown 66 kV | Loading (A) | 4.9831 | 4.4665 | 4.2148 | 4.29 | 4.6362
FN | 3COO_Cooktown 66 kV | Loading (MVA) | 0.60885 | 0.54664 | 0.51661 | 0.52682 | 0.57021
FN | 3COO_Cooktown 66 kV | Loading (MW) | 0.33232 | 0.19017 | 0.047946 | 0.10445 | 0.23906
FN | 3COO_Cooktown 66 kV | Power Factor | 0.54582 | 0.34789 | 0.092807 | 0.19798 | 0.41889
FN | 3COO_Cooktown 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
FN | 3COO_Cooktown 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3COO_Cooktown 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0688 | 1.0706 | 1.0722 | 1.0742 | 1.0759
FN | 3COO_Cooktown 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV
FN | 3DIM_Dimbulah 66 kV | % of Rated A | 18.45% | 18.43% | 18.41% | 18.39% | 18.38%
FN | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1
FN | 3DIM_Dimbulah 66 kV | Loading (A) | 40.2124 | 40.1704 | 40.1338 | 40.0996 | 40.0733
FN | 3DIM_Dimbulah 66 kV | Loading (MVA) | 4.9105 | 4.9105 | 4.9106 | 4.9106 | 4.9106
FN | 3DIM_Dimbulah 66 kV | Loading (MW) | 4.9105 | 4.9105 | 4.9106 | 4.9106 | 4.9106
FN | 3DIM_Dimbulah 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
FN | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 218 | 218 | 218 | 218
FN | 3DIM_Dimbulah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3DIM_Dimbulah 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0681 | 1.0692 | 1.0702 | 1.0711 | 1.0718
FN | 3DIM_Dimbulah 66 kV | Contingency Outage | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN | 3EVE_Evelyn 66 kV | % of Rated A | 6.536% | 6.807% | 7.131% | 7.51% | 7.873%
FN | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN | 3EVE_Evelyn 66 kV | Loading (A) | 11.0463 | 11.5033 | 12.0516 | 12.6915 | 13.3053
FN | 3EVE_Evelyn 66 kV | Loading (MVA) | 1.3795 | 1.4389 | 1.5096 | 1.5922 | 1.6711
FN | 3EVE_Evelyn 66 kV | Loading (MW) | 0.42308 | 0.58016 | 0.7328 | 0.886 | 1.0183
FN | 3EVE_Evelyn 66 kV | Power Factor | 0.30669 | 0.4032 | 0.48541 | 0.55648 | 0.60933
FN | 3EVE_Evelyn 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN | 3EVE_Evelyn 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3EVE_Evelyn 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0924 | 1.0942 | 1.0958 | 1.0974 | 1.0987
FN | 3EVE_Evelyn 66 kV | Contingency Outage | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV
FN | 3HLA_Helenvale 66 kV | % of Rated A | 3.131% | 3.056% | 3.022% | 3.034% | 3.082%
FN | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1
FN | 3HLA_Helenvale 66 kV | Loading (A) | 11.8358 | 11.5535 | 11.4247 | 11.467 | 11.6511
FN | 3HLA_Helenvale 66 kV | Loading (MVA) | 1.4413 | 1.4088 | 1.3947 | 1.4019 | 1.4262
FN | 3HLA_Helenvale 66 kV | Loading (MW) | 0.40614 | 0.23893 | 0.070941 | 0.10717 | 0.26476
FN | 3HLA_Helenvale 66 kV | Power Factor | 0.28178 | 0.1696 | 0.050866 | 0.076208 | 0.1854
FN | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
FN | 3HLA_Helenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3HLA_Helenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0653 | 1.0667 | 1.0679 | 1.0695 | 1.0708
FN | 3HLA_Helenvale 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV
FN | 3MO1_Mossman No 1 66 kV | % of Rated A | 57.8% | 60.46% | 63.17% | 66.01% | 68.47%
FN | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN | 3MO1_Mossman No 1 66 kV | Loading (A) | 76.3008 | 79.8133 | 83.3834 | 87.136 | 90.3741
FN | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 9.5788 | 10.0343 | 10.4968 | 10.9835 | 11.4032
FN | 3MO1_Mossman No 1 66 kV | Loading (MW) | 5.1026 | 5.9353 | 6.7133 | 7.4794 | 8.1091
FN | 3MO1_Mossman No 1 66 kV | Power Factor | 0.53239 | 0.59119 | 0.63928 | 0.68072 | 0.71089
FN | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN | 3MO1_Mossman No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3MO1_Mossman No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0982 | 1.0997 | 1.1011 | 1.1025 | 1.1036
FN | 3MO1_Mossman No 1 66 kV | Contingency Outage | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV
FN | 3MO2_Mossman No 2 66 kV | % of Rated A | 48.74% | 50.82% | 52.95% | 55.21% | 57.18%
FN | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1)
FN | 3MO2_Mossman No 2 66 kV | Loading (A) | 82.3695 | 85.8874 | 89.4887 | 93.3121 | 96.6331
FN | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 10.2119 | 10.6577 | 11.1131 | 11.5973 | 12.0175
FN | 3MO2_Mossman No 2 66 kV | Loading (MW) | 5.1008 | 5.9795 | 6.7979 | 7.606 | 8.2693
FN | 3MO2_Mossman No 2 66 kV | Power Factor | 0.4994 | 0.56095 | 0.6116 | 0.65575 | 0.68802
FN | 3MO2_Mossman No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN | 3MO2_Mossman No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3MO2_Mossman No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0845 | 1.0855 | 1.0863 | 1.0872 | 1.0878
FN | 3MO2_Mossman No 2 66 kV | Contingency Outage | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV
FN | 3MTG_Mt Garnet 66 kV | % of Rated A | 7.343% | 7.197% | 7.165% | 7.246% | 7.403%
FN | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1
FN | 3MTG_Mt Garnet 66 kV | Loading (A) | 12.4104 | 12.1624 | 12.1088 | 12.2457 | 12.5114
FN | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 1.5494 | 1.5211 | 1.5167 | 1.5363 | 1.5717
FN | 3MTG_Mt Garnet 66 kV | Loading (MW) | 0.36361 | 0.16776 | 0.023671 | 0.21737 | 0.38413
FN | 3MTG_Mt Garnet 66 kV | Power Factor | 0.23468 | 0.11029 | 0.01457 | 0.14043 | 0.24333
FN | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN | 3MTG_Mt Garnet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3MTG_Mt Garnet 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0921 | 1.094 | 1.0957 | 1.0975 | 1.0989
FN | 3MTG_Mt Garnet 66 kV | Contingency Outage | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV | 3EVE_Evelyn 66 kV
FN | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 6.323% | 6.437% | 6.578% | 6.744% | 6.906%
FN | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 10.6854 | 10.8788 | 11.1164 | 11.3976 | 11.6714
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 1.3344 | 1.3608 | 1.3925 | 1.4298 | 1.4659
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 0.23968 | 0.34348 | 0.44303 | 0.54103 | 0.62475
FN | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.17961 | 0.25241 | 0.31815 | 0.37838 | 0.42618
FN | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN | 3RA1_Ravenshoe No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3RA1_Ravenshoe No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0924 | 1.0942 | 1.0958 | 1.0974 | 1.0987
FN | 3RA1_Ravenshoe No 1 66 kV | Contingency Outage | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV | 3MTG_Mt Garnet 66 kV
FN | 7200_Craiglie No 2 132 kV | % of Rated A | 15.57% | 15.58% | 15.62% | 15.71% | 15.82%
FN | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN | 7200_Craiglie No 2 132 kV | Loading (A) | 70.3701 | 70.4369 | 70.5958 | 70.9942 | 71.4869
FN | 7200_Craiglie No 2 132 kV | Loading (MVA) | 17.7935 | 17.827 | 17.8816 | 17.9977 | 18.1344
FN | 7200_Craiglie No 2 132 kV | Loading (MW) | 0.79643 | 0.014007 | 0.73069 | 1.7557 | 2.6224
FN | 7200_Craiglie No 2 132 kV | Power Factor | 0.044676 | 0.00026012 | 0.040334 | 0.097021 | 0.14407
FN | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
FN | 7200_Craiglie No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7200_Craiglie No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.106 | 1.107 | 1.1079 | 1.1088 | 1.1095
FN | 7200_Craiglie No 2 132 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV
FN | 7201_Craiglie No 1 132 kV | % of Rated A | 13.66% | 13.68% | 13.72% | 13.81% | 13.93%
FN | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
FN | 7201_Craiglie No 1 132 kV | Loading (A) | 61.7639 | 61.8348 | 62.0059 | 62.4373 | 62.9745
FN | 7201_Craiglie No 1 132 kV | Loading (MVA) | 15.6161 | 15.6486 | 15.7047 | 15.8272 | 15.9737
FN | 7201_Craiglie No 1 132 kV | Loading (MW) | 0.76505 | 0.017889 | 0.75322 | 1.778 | 2.6443
FN | 7201_Craiglie No 1 132 kV | Power Factor | 0.048991 | 0.0011335 | 0.047952 | 0.11233 | 0.16553
FN | 7201_Craiglie No 1 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
FN | 7201_Craiglie No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7201_Craiglie No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.1059 | 1.1069 | 1.1078 | 1.1087 | 1.1094
FN | 7201_Craiglie No 1 132 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
FN | 7285_4LAK (Lakeland) 132kV | % of Rated A | 8.094% | 8.107% | 8.118% | 8.125% | 8.132%
FN | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN | 7285_4LAK (Lakeland) 132kV | Loading (A) | 41.1159 | 41.1839 | 41.2376 | 41.2741 | 41.313
FN | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 10.5638 | 10.595 | 10.621 | 10.6445 | 10.6658
FN | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 0.37908 | 0.43586 | 0.49424 | 0.27721 | 0.087238
FN | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.035885 | 0.041138 | 0.046534 | 0.026042 | 0.008089
FN | 7285_4LAK (Lakeland) 132kV | Rating (A) | 508 | 508 | 508 | 508 | 508
FN | 7285_4LAK (Lakeland) 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7285_4LAK (Lakeland) 132kV | Min Voltage at Constrained Conductor (pu) | 1.1238 | 1.1252 | 1.1265 | 1.128 | 1.1292
FN | 7285_4LAK (Lakeland) 132kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV
FN | MOSS_7496 | % of Rated A | 2.312% | 2.55% | 2.836% | 3.171% | 3.555%
FN | MOSS_7496 | Limiting Line Name | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a
FN | MOSS_7496 | Loading (A) | 8.7642 | 9.6656 | 10.7486 | 12.0186 | 13.4721
FN | MOSS_7496 | Loading (MVA) | 2.2356 | 2.4682 | 2.7474 | 3.0753 | 3.469
FN | MOSS_7496 | Loading (MW) | 0.87759 | 1.3614 | 1.8181 | 2.2836 | 2.8304
FN | MOSS_7496 | Power Factor | 0.39252 | 0.55151 | 0.66168 | 0.74248 | 0.81586
FN | MOSS_7496 | Rating (A) | 379 | 379 | 379 | 379 | 379
FN | MOSS_7496 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | MOSS_7496 | Min Voltage at Constrained Conductor (pu) | 1.1157 | 1.1169 | 1.118 | 1.1192 | 1.1263
FN | MOSS_7496 | Contingency Outage | 2MOS_Mossman 22 kV | 2MOS_Mossman 22 kV | 2MOS_Mossman 22 kV | 2MOS_Mossman 22 kV | 7200_Craiglie No 2 132 kV
MK | 231_Carmila 33 kV | % of Rated A | 5.683% | 5.672% | 5.664% | 0% | 0%
MK | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1 | 0 | 0
MK | 231_Carmila 33 kV | Loading (A) | 10.9688 | 10.9473 | 10.9321 | 0 | 0
MK | 231_Carmila 33 kV | Loading (MVA) | 0.65792 | 0.65798 | 0.65802 | 0 | 0
MK | 231_Carmila 33 kV | Loading (MW) | 0.54406 | 0.54408 | 0.54409 | 0 | 0
MK | 231_Carmila 33 kV | Power Factor | 0.8269 | 0.82686 | 0.82682 | 0 | 0
MK | 231_Carmila 33 kV | Rating (A) | 193 | 193 | 193 | 0 | 0
MK | 231_Carmila 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 0:00 | 0:00
MK | 231_Carmila 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0494 | 1.0516 | 1.0531 | 0 | 0
MK | 231_Carmila 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3046_Rosella 33 kV | 3046_Rosella 33 kV | 0 | 0
MK | 3045_Sarina No 1 33 kV | % of Rated A | 27.49% | 27.78% | 28.08% | 28.39% | 28.66%
MK | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1
MK | 3045_Sarina No 1 33 kV | Loading (A) | 82.1908 | 83.0712 | 83.97 | 84.88 | 85.6952
MK | 3045_Sarina No 1 33 kV | Loading (MVA) | 5.1292 | 5.188 | 5.2478 | 5.3071 | 5.3609
MK | 3045_Sarina No 1 33 kV | Loading (MW) | 1.7154 | 1.8676 | 2.0146 | 2.1579 | 2.2795
MK | 3045_Sarina No 1 33 kV | Power Factor | 0.3343 | 0.35984 | 0.38375 | 0.40648 | 0.42509
MK | 3045_Sarina No 1 33 kV | Rating (A) | 299 | 299 | 299 | 299 | 299
MK | 3045_Sarina No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 3045_Sarina No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0917 | 1.0925 | 1.0932 | 1.0937 | 1.0943
MK | 3045_Sarina No 1 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 3046_Rosella 33 kV | % of Rated A | 48.73% | 48.75% | 48.77% | 48.94% | 49.11%
MK | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1
MK | 3046_Rosella 33 kV | Loading (A) | 199.3046 | 199.4054 | 199.4627 | 200.151 | 200.8443
MK | 3046_Rosella 33 kV | Loading (MVA) | 12.0146 | 12.0212 | 12.0248 | 12.0676 | 12.1097
MK | 3046_Rosella 33 kV | Loading (MW) | 1.2433 | 0.66524 | 0.17629 | 0.33503 | 0.72177
MK | 3046_Rosella 33 kV | Power Factor | 0.10348 | 0.055306 | 0.01458 | 0.027665 | 0.059505
MK | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409
MK | 3046_Rosella 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 3046_Rosella 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0547 | 1.0547 | 1.0547 | 1.0548 | 1.0549
MK | 3046_Rosella 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 3047_Sarina No 2 33 kV | % of Rated A | 15.88% | 17.93% | 19.88% | 0.1277% | 0.1277%
MK | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11141_1 | TR_LINE 11141_1
MK | 3047_Sarina No 2 33 kV | Loading (A) | 60.346 | 68.1243 | 75.5274 | 0.91439 | 0.91441
MK | 3047_Sarina No 2 33 kV | Loading (MVA) | 3.6306 | 4.1029 | 4.5533 | 0.055131 | 0.055134
MK | 3047_Sarina No 2 33 kV | Loading (MW) | 3.6271 | 4.0992 | 4.5492 | 2.7265e-06 | 2.7267e-06
MK | 3047_Sarina No 2 33 kV | Power Factor | 0.99904 | 0.99907 | 0.99908 | 4.9424e-05 | 4.9426e-05
MK | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 380 | 380 | 716 | 716
MK | 3047_Sarina No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 3047_Sarina No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0523 | 1.0534 | 1.0544 | 1.0548 | 1.0549
MK | 3047_Sarina No 2 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 3053_Mt Bassett 33 kV | % of Rated A | 13.86% | 16.75% | 19.64% | 22.71% | 25.28%
MK | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK | 3053_Mt Bassett 33 kV | Loading (A) | 32.565 | 39.3606 | 46.1442 | 53.3712 | 59.4102
MK | 3053_Mt Bassett 33 kV | Loading (MVA) | 1.9652 | 2.3775 | 2.7896 | 3.2295 | 3.5975
MK | 3053_Mt Bassett 33 kV | Loading (MW) | 1.9652 | 2.3775 | 2.7895 | 3.2292 | 3.5971
MK | 3053_Mt Bassett 33 kV | Power Factor | 0.99997 | 0.99996 | 0.99994 | 0.99992 | 0.9999
MK | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 235 | 235 | 235 | 235
MK | 3053_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 3053_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0546 | 1.0553 | 1.0559 | 1.0567 | 1.0572
MK | 3053_Mt Bassett 33 kV | Contingency Outage | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV
MK | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.348% | 2.353% | 2.358% | 2.362% | 2.365%
MK | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1
MK | 340_MK3-1 Farleigh 33 kV | Loading (A) | 4.0392 | 4.0477 | 4.0553 | 4.0627 | 4.0685
MK | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.25039 | 0.25144 | 0.2524 | 0.25332 | 0.25404
MK | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0046005 | 0.0046199 | 0.0046375 | 0.0046544 | 0.0046677
MK | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018374 | 0.018374 | 0.018374 | 0.018374
MK | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 172 | 172 | 172 | 172
MK | 340_MK3-1 Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 340_MK3-1 Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0845 | 1.0868 | 1.0889 | 1.0909 | 1.0924
MK | 340_MK3-1 Farleigh 33 kV | Contingency Outage | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV
MK | 341_Tennyson St No 2 33 kV | % of Rated A | 17.17% | 17.48% | 17.98% | 18.73% | 19.53%
MK | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1
MK | 341_Tennyson St No 2 33 kV | Loading (A) | 60.1087 | 61.1774 | 62.9439 | 65.5493 | 68.3597
MK | 341_Tennyson St No 2 33 kV | Loading (MVA) | 3.6152 | 3.6807 | 3.7879 | 3.9459 | 4.1159
MK | 341_Tennyson St No 2 33 kV | Loading (MW) | 0.59393 | 0.996 | 1.4037 | 1.8405 | 2.2222
MK | 341_Tennyson St No 2 33 kV | Power Factor | 0.16295 | 0.26928 | 0.36926 | 0.46517 | 0.53865
MK | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350
MK | 341_Tennyson St No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 341_Tennyson St No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0522 | 1.0526 | 1.0529 | 1.0532 | 1.0534
MK | 341_Tennyson St No 2 33 kV | Contingency Outage | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV
MK | 342_South Mackay 33 kV | % of Rated A | 40.43% | 40.39% | 40.11% | 40.15% | 40.19%
MK | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12106200_1 | TR_LINE 12106200_1 | TR_LINE 12106200_1 | TR_LINE 12106200_1 | TR_LINE 12106200_1
MK | 342_South Mackay 33 kV | Loading (A) | 189.2262 | 189.0062 | 187.7336 | 187.8951 | 188.0932
MK | 342_South Mackay 33 kV | Loading (MVA) | 11.4027 | 11.3938 | 11.3218 | 11.3351 | 11.3495
MK | 342_South Mackay 33 kV | Loading (MW) | 0.79374 | 0.2149 | 0.12661 | 0.20959 | 0.44248
MK | 342_South Mackay 33 kV | Power Factor | 0.069511 | 0.018763 | 0.011085 | 0.018395 | 0.038895
MK | 342_South Mackay 33 kV | Rating (A) | 468 | 468 | 468 | 468 | 468
MK | 342_South Mackay 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 342_South Mackay 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0541 | 1.0545 | 1.0549 | 1.0553 | 1.0555
MK | 342_South Mackay 33 kV | Contingency Outage | 3046_Rosella 33 kV | 3046_Rosella 33 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV
MK | 343_Pleystowe 33 kV | % of Rated A | 35.27% | 37.74% | 40.05% | 42.22% | 43.97%
MK | 343_Pleystowe 33 kV | Limiting Line Name | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 11839_1
MK | 343_Pleystowe 33 kV | Loading (A) | 77.5858 | 83.0323 | 88.1168 | 92.8803 | 96.7317
MK | 343_Pleystowe 33 kV | Loading (MVA) | 4.6683 | 4.9977 | 5.3051 | 5.5935 | 5.8307
MK | 343_Pleystowe 33 kV | Loading (MW) | 4.6626 | 4.9935 | 5.3021 | 5.5915 | 5.8302
MK | 343_Pleystowe 33 kV | Power Factor | 0.99878 | 0.99917 | 0.99945 | 0.99964 | 0.99992
MK | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220
MK | 343_Pleystowe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 343_Pleystowe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0526 | 1.0529 | 1.0532 | 1.0535 | 1.0541
MK | 343_Pleystowe 33 kV | Contingency Outage | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV
MK | 344_West Mackay 2 33 kV | % of Rated A | 1.244% | 0.1527% | 0.9646% | 2.028% | 2.88%
MK | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK | 344_West Mackay 2 33 kV | Loading (A) | 7.7768 | 0.95432 | 6.0286 | 12.6734 | 18.0006
MK | 344_West Mackay 2 33 kV | Loading (MVA) | 0.46795 | 0.057443 | 0.36297 | 0.76327 | 1.0843
MK | 344_West Mackay 2 33 kV | Loading (MW) | 0.46594 | 0.0369 | 0.36122 | 0.7631 | 1.0843
MK | 344_West Mackay 2 33 kV | Power Factor | 0.99571 | 0.64238 | 0.99275 | 0.99861 | 0.99943
MK | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625
MK | 344_West Mackay 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 344_West Mackay 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0531 | 1.0534 | 1.0537 | 1.0539
MK | 344_West Mackay 2 33 kV | Contingency Outage | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV | 364_West Mackay No 1 33 kV
MK | 346_Ritchies Rd 33 kV | % of Rated A | 51.85% | 52.72% | 53.59% | 54.48% | 55.26%
MK | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11706_1 | TR_LINE 11706_1 | TR_LINE 11706_1 | TR_LINE 11706_1 | TR_LINE 11706_1
MK | 346_Ritchies Rd 33 kV | Loading (A) | 87.6295 | 89.096 | 90.5724 | 92.0761 | 93.39
MK | 346_Ritchies Rd 33 kV | Loading (MVA) | 5.4848 | 5.5854 | 5.6861 | 5.7888 | 5.878
MK | 346_Ritchies Rd 33 kV | Loading (MW) | 2.4136 | 2.612 | 2.8031 | 2.9895 | 3.1472
MK | 346_Ritchies Rd 33 kV | Power Factor | 0.43903 | 0.46669 | 0.49209 | 0.51563 | 0.53468
MK | 346_Ritchies Rd 33 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
MK | 346_Ritchies Rd 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 346_Ritchies Rd 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0928 | 1.0944 | 1.0959 | 1.0973 | 1.0985
MK | 346_Ritchies Rd 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK | 347_Mt Bassett 33 kV | % of Rated A | 12.8% | 15.46% | 18.12% | 20.96% | 23.33%
MK | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK | 347_Mt Bassett 33 kV | Loading (A) | 32.6465 | 39.4209 | 46.1992 | 53.4458 | 59.503
MK | 347_Mt Bassett 33 kV | Loading (MVA) | 1.9654 | 2.3742 | 2.7843 | 3.2224 | 3.5888
MK | 347_Mt Bassett 33 kV | Loading (MW) | 1.9594 | 2.3699 | 2.7842 | 3.2222 | 3.5884
MK | 347_Mt Bassett 33 kV | Power Factor | 0.99686 | 0.99813 | 0.99996 | 0.99993 | 0.9999
MK | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255
MK | 347_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 347_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0533 | 1.0537 | 1.0544 | 1.0548 | 1.0552
MK | 347_Mt Bassett 33 kV | Contingency Outage | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV
MK | 348_Farleigh 33 kV | % of Rated A | 14.88% | 16% | 17.08% | 18.08% | 18.9%
MK | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1
MK | 348_Farleigh 33 kV | Loading (A) | 28.8712 | 31.0424 | 33.1279 | 35.0813 | 36.6655
MK | 348_Farleigh 33 kV | Loading (MVA) | 1.7383 | 1.8709 | 1.9983 | 2.1179 | 2.215
MK | 348_Farleigh 33 kV | Loading (MW) | 1.723 | 1.8575 | 1.9866 | 2.1076 | 2.2057
MK | 348_Farleigh 33 kV | Power Factor | 0.99118 | 0.99283 | 0.99411 | 0.99509 | 0.99577
MK | 348_Farleigh 33 kV | Rating (A) | 194 | 194 | 194 | 194 | 194
MK | 348_Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 348_Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0533 | 1.0544 | 1.0553 | 1.0562 | 1.0568
MK | 348_Farleigh 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 20.11% | 21.17% | 22.17% | 23.13% | 23.94%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 44.2321 | 46.5848 | 48.7781 | 50.8849 | 52.6696
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 5.3682 | 5.6537 | 5.9195 | 6.1749 | 6.391
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 5.2842 | 5.5766 | 5.8482 | 6.1087 | 6.3288
MK | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.98434 | 0.98634 | 0.98793 | 0.98926 | 0.99026
MK | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 220 | 220 | 220 | 220 | 220
MK | 349_Pioneer Valley - Pinnacle 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 349_Pioneer Valley - Pinnacle 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0617 | 1.0617 | 1.0616 | 1.0615 | 1.0615
MK | 349_Pioneer Valley - Pinnacle 66 kV | Contingency Outage | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV
MK | 351_Alligator Creek 33 kV | % of Rated A | 84.65% | 84.72% | 84.82% | 85% | 85.16%
MK | 351_Alligator Creek 33 kV | Limiting Line Name | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK | 351_Alligator Creek 33 kV | Loading (A) | 198.0883 | 198.2355 | 198.4835 | 198.8977 | 199.264
MK | 351_Alligator Creek 33 kV | Loading (MVA) | 12.4758 | 12.5056 | 12.5372 | 12.5821 | 12.6187
MK | 351_Alligator Creek 33 kV | Loading (MW) | 0.9261 | 0.51957 | 0.1901 | 0.14539 | 0.37788
MK | 351_Alligator Creek 33 kV | Power Factor | 0.07423 | 0.041515 | 0.015105 | 0.011483 | 0.029874
MK | 351_Alligator Creek 33 kV | Rating (A) | 234 | 234 | 234 | 234 | 234
MK | 351_Alligator Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 351_Alligator Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.1019 | 1.1037 | 1.1051 | 1.1067 | 1.1079
MK | 351_Alligator Creek 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 6.632% | 6.538% | 6.443% | 6.345% | 6.258%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 6.1017 | 6.0148 | 5.9272 | 5.8378 | 5.7574
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 0.7474 | 0.73704 | 0.72653 | 0.71582 | 0.70613
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 0.39677 | 0.37606 | 0.35444 | 0.33138 | 0.30969
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.53087 | 0.51023 | 0.48785 | 0.46295 | 0.43857
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 92 | 92 | 92 | 92
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0715 | 1.0719 | 1.0723 | 1.0726 | 1.0729
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Contingency Outage | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV
MK | 364_West Mackay No 1 33 kV | % of Rated A | 2.665% | 0.2064% | 2.069% | 4.369% | 6.207%
MK | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11500_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK | 364_West Mackay No 1 33 kV | Loading (A) | 7.7289 | 0.59854 | 5.9996 | 12.6706 | 18.0005
MK | 364_West Mackay No 1 33 kV | Loading (MVA) | 0.46505 | 0.036027 | 0.36122 | 0.76311 | 1.0843
MK | 364_West Mackay No 1 33 kV | Loading (MW) | 0.46505 | 0.03602 | 0.36122 | 0.7631 | 1.0843
MK | 364_West Mackay No 1 33 kV | Power Factor | 1 | 0.99978 | 1 | 0.99999 | 0.99998
MK | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 290 | 290 | 290 | 290
MK | 364_West Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 364_West Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0531 | 1.0534 | 1.0537 | 1.0539
MK | 364_West Mackay No 1 33 kV | Contingency Outage | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV | 344_West Mackay 2 33 kV
MK | 365_Tennyson St No 1 33 kV | % of Rated A | 2.128% | 2.175% | 2.251% | 2.365% | 2.535%
MK | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_LINE 11727_1 | TR_LINE 11727_1 | TR_LINE 11727_1 | TR_LINE 11727_1 | TR_LINE 11727_1
MK | 365_Tennyson St No 1 33 kV | Loading (A) | 14.1486 | 14.4668 | 14.9681 | 15.7241 | 16.857
MK | 365_Tennyson St No 1 33 kV | Loading (MVA) | 0.85095 | 0.87039 | 0.90078 | 0.94636 | 1.0147
MK | 365_Tennyson St No 1 33 kV | Loading (MW) | 0.2509 | 0.15949 | 0.066568 | 0.17157 | 0.27633
MK | 365_Tennyson St No 1 33 kV | Power Factor | 0.29484 | 0.18324 | 0.073901 | 0.18129 | 0.2723
MK | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665
MK | 365_Tennyson St No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 365_Tennyson St No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0522 | 1.0526 | 1.0529 | 1.053 | 1.0532
MK | 365_Tennyson St No 1 33 kV | Contingency Outage | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV
MK | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.06535% | 0.06535% | 0.06535% | 0.06535% | 0.06534%
MK | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16469 | 0.16469 | 0.16468 | 0.16468 | 0.16466
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.020004 | 0.020004 | 0.020002 | 0.02 | 0.019997
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.1437e-08 | 8.1389e-08 | 8.1478e-08 | 8.148e-08 | 8.1484e-08
MK | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.071e-06 | 4.0686e-06 | 4.0735e-06 | 4.074e-06 | 4.0749e-06
MK | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 252 | 252 | 252 | 252
MK | 367_Pioneer Valley - Greenmount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 367_Pioneer Valley - Greenmount 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0625 | 1.0625 | 1.0625 | 1.0624 | 1.0623
MK | 367_Pioneer Valley - Greenmount 66 kV | Contingency Outage | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV
MK | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 7.439% | 7.917% | 8.39% | 8.845% | 9.227%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 14.5052 | 15.4375 | 16.3602 | 17.2483 | 17.9919
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 1.7559 | 1.8689 | 1.9806 | 2.0881 | 2.1781
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 1.7532 | 1.8667 | 1.9788 | 2.0868 | 2.1771
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.99795 | 0.9983 | 0.99858 | 0.99881 | 0.99898
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.059 | 1.059 | 1.059 | 1.059 | 1.059
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK | 422_North Mackay No 1 33 kV | % of Rated A | 64.16% | 68.46% | 72.65% | 76.78% | 80.1%
MK | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1
MK | 422_North Mackay No 1 33 kV | Loading (A) | 400.9864 | 427.8967 | 454.0833 | 479.8898 | 500.6429
MK | 422_North Mackay No 1 33 kV | Loading (MVA) | 24.1776 | 25.789 | 27.3515 | 28.8876 | 30.1181
MK | 422_North Mackay No 1 33 kV | Loading (MW) | 22.9524 | 24.7109 | 26.401 | 28.05 | 29.3634
MK | 422_North Mackay No 1 33 kV | Power Factor | 0.94932 | 0.9582 | 0.96525 | 0.971 | 0.97494
MK | 422_North Mackay No 1 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625
MK | 422_North Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 422_North Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0546 | 1.0541 | 1.0535 | 1.0528 | 1.0521
MK | 422_North Mackay No 1 33 kV | Contingency Outage | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV
MK | 423_North Mackay No 2 33 kV | % of Rated A | 33.42% | 34.94% | 36.41% | 37.83% | 38.99%
MK | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1
MK | 423_North Mackay No 2 33 kV | Loading (A) | 254.3208 | 265.9044 | 277.0729 | 287.8727 | 296.7422
MK | 423_North Mackay No 2 33 kV | Loading (MVA) | 15.2789 | 15.9741 | 16.6431 | 17.2901 | 17.8203
MK | 423_North Mackay No 2 33 kV | Loading (MW) | 12.6259 | 13.5324 | 14.3857 | 15.1951 | 15.8492
MK | 423_North Mackay No 2 33 kV | Power Factor | 0.82613 | 0.8469 | 0.86412 | 0.87858 | 0.88913
MK | 423_North Mackay No 2 33 kV | Rating (A) | 761 | 761 | 761 | 761 | 761
MK | 423_North Mackay No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 423_North Mackay No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0511 | 1.051 | 1.0509 | 1.0508 | 1.0507
MK | 423_North Mackay No 2 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK | PV 6/4_Glenella No 2 66 kV | % of Rated A | 26.92% | 28.89% | 30.79% | 32.65% | 34.14%
MK | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1
MK | PV 6/4_Glenella No 2 66 kV | Loading (A) | 217.7847 | 233.745 | 249.0961 | 264.1698 | 276.1998
MK | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 26.4413 | 28.3759 | 30.2341 | 32.0586 | 33.5124
MK | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 25.4192 | 27.5374 | 29.5499 | 31.5071 | 33.0547
MK | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.96134 | 0.97045 | 0.97737 | 0.9828 | 0.98634
MK | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 809 | 809 | 809 | 809
MK | PV 6/4_Glenella No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | PV 6/4_Glenella No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.062 | 1.0619 | 1.0617 | 1.0616 | 1.0614
MK | PV 6/4_Glenella No 2 66 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV
MK | PV 6/5_Glenella No 1 66 kV | % of Rated A | 26.9% | 28.88% | 30.79% | 32.67% | 34.16%
MK | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1
MK | PV 6/5_Glenella No 1 66 kV | Loading (A) | 217.583 | 233.6589 | 249.1096 | 264.2725 | 276.3672
MK | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 26.8202 | 28.8087 | 30.7172 | 32.5896 | 34.0807
MK | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 25.654 | 27.8081 | 29.8574 | 31.853 | 33.433
MK | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.95652 | 0.96527 | 0.97201 | 0.9774 | 0.98099
MK | PV 6/5_Glenella No 1 66 kV | Rating (A) | 809 | 809 | 809 | 809 | 809
MK | PV 6/5_Glenella No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | PV 6/5_Glenella No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0782 | 1.0785 | 1.0786 | 1.0787 | 1.0787
MK | PV 6/5_Glenella No 1 66 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV
MK | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 2.216% | 2.211% | 2.207% | 2.192% | 2.174%
MK | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1
MK | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 8.553 | 8.535 | 8.5199 | 8.4593 | 8.3925
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 1.0247 | 1.0226 | 1.0209 | 1.0137 | 1.0057
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 1.024 | 1.0219 | 1.0202 | 1.013 | 1.005
MK | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.99935 | 0.99934 | 0.99934 | 0.99932 | 0.99931
MK | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 386 | 386 | 386 | 386
MK | 6328_Broadlea - Moorvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 6328_Broadlea - Moorvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0479 | 1.0479 | 1.048 | 1.048 | 1.0481
MK | 6328_Broadlea - Moorvale 66 kV | Contingency Outage | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV
MK | 6329_Broadlea - Coppabella 66 kV | % of Rated A | 24.95% | 24.95% | 24.95% | 24.94% | 24.94%
MK | 6329_Broadlea - Coppabella 66 kV | Limiting Line Name | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1
MK | 6329_Broadlea - Coppabella 66 kV | Loading (A) | 96.3023 | 96.2969 | 96.2916 | 96.2861 | 96.2806
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MVA) | 11.5022 | 11.5022 | 11.5022 | 11.5021 | 11.5021
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MW) | 11.5011 | 11.5011 | 11.5011 | 11.5011 | 11.501
MK | 6329_Broadlea - Coppabella 66 kV | Power Factor | 0.99983 | 0.99983 | 0.99983 | 0.99983 | 0.99983
MK | 6329_Broadlea - Coppabella 66 kV | Rating (A) | 386 | 386 | 386 | 386 | 386
MK | 6329_Broadlea - Coppabella 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 6329_Broadlea - Coppabella 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0308 | 1.0309 | 1.031 | 1.031 | 1.0311
MK | 6329_Broadlea - Coppabella 66 kV | Contingency Outage | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV | 6330 Broadlea - Millennium 66 kV
MK | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 40.96% | 40.96% | 40.96% | 40.95% | 40.94%
MK | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 288.802 | 288.777 | 288.7536 | 288.7065 | 288.656
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 68.5772 | 68.575 | 68.5732 | 68.5659 | 68.5578
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 68.5213 | 68.5192 | 68.5174 | 68.5101 | 68.5021
MK | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.99919 | 0.99919 | 0.99919 | 0.99919 | 0.99919
MK | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
MK | 7366_Moranbah - Broadlea 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 7366_Moranbah - Broadlea 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0386 | 1.0386 | 1.0387 | 1.0387 | 1.0388
MK | 7366_Moranbah - Broadlea 132 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK | 232_Newlands-Glenden 66 kV | % of Rated A | 2.395% | 2.379% | 2.366% | 2.342% | 2.324%
MK | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1
MK | 232_Newlands-Glenden 66 kV | Loading (A) | 2.7786 | 2.7598 | 2.7444 | 2.717 | 2.6953
MK | 232_Newlands-Glenden 66 kV | Loading (MVA) | 0.33437 | 0.33212 | 0.33029 | 0.327 | 0.32441
MK | 232_Newlands-Glenden 66 kV | Loading (MW) | 0.15878 | 0.15389 | 0.1498 | 0.14228 | 0.1361
MK | 232_Newlands-Glenden 66 kV | Power Factor | 0.47487 | 0.46335 | 0.45355 | 0.4351 | 0.41954
MK | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
MK | 232_Newlands-Glenden 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 232_Newlands-Glenden 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0527 | 1.0528 | 1.0528 | 1.0529
MK | 232_Newlands-Glenden 66 kV | Contingency Outage | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 42.75% | 42.73% | 42.72% | 42.71% | 42.7%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 80.3646 | 80.338 | 80.315 | 80.2903 | 80.271
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 9.5756 | 9.573 | 9.5707 | 9.5682 | 9.5664
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 9.512 | 9.5094 | 9.5071 | 9.5045 | 9.5027
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.99336 | 0.99335 | 0.99335 | 0.99334 | 0.99334
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 188 | 188 | 188 | 188
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0422 | 1.0423 | 1.0423 | 1.0424 | 1.0424
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Contingency Outage | 232_Newlands-Glenden 66 kV | 232_Newlands-Glenden 66 kV | 232_Newlands-Glenden 66 kV | 232_Newlands-Glenden 66 kV | 232_Newlands-Glenden 66 kV
NQ | 6321_Lucinda 66 kV | % of Rated A | 4.242% | 4.519% | 4.793% | 5.062% | 5.323%
NQ | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1
NQ | 6321_Lucinda 66 kV | Loading (A) | 8.4421 | 8.9929 | 9.5387 | 10.0735 | 10.592
NQ | 6321_Lucinda 66 kV | Loading (MVA) | 0.99921 | 1.0711 | 1.1361 | 1.1999 | 1.2556
NQ | 6321_Lucinda 66 kV | Loading (MW) | 0.94821 | 1.0227 | 1.0911 | 1.1577 | 1.2163
NQ | 6321_Lucinda 66 kV | Power Factor | 0.94896 | 0.95486 | 0.96035 | 0.96478 | 0.96871
NQ | 6321_Lucinda 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ | 6321_Lucinda 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6321_Lucinda 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0354 | 1.0419 | 1.0419 | 1.042 | 1.0369
NQ | 6321_Lucinda 66 kV | Contingency Outage | IN-GR_Ingham-Black River/Greenvale 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 1.515% | 1.657% | 1.82% | 1.987% | 2.158%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 31685_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 2.955 | 2.2205 | 2.4391 | 2.6631 | 2.8911
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 0.35436 | 0.2655 | 0.29164 | 0.31844 | 0.34454
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 0.18554 | 0.21784 | 0.24914 | 0.28014 | 0.31008
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.52358 | 0.82045 | 0.85425 | 0.87971 | 0.89998
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 195 | 134 | 134 | 134 | 134
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.049 | 1.0459 | 1.046 | 1.046 | 1.0425
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Contingency Outage | BC-IN-1_Black River - Ingham No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 32.53% | 32.23% | 32.23% | 32.22% | 32.23%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 64.7434 | 64.1289 | 64.1295 | 64.1273 | 64.1285
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 7.7422 | 7.7415 | 7.7415 | 7.7415 | 7.7415
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 7.742 | 7.7412 | 7.7412 | 7.7412 | 7.7412
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0461 | 1.056 | 1.056 | 1.056 | 1.056
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Contingency Outage | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV
NQ | 118_Cannonvale No 2 66 kV | % of Rated A | 53.61% | 54.25% | 55.02% | 55.95% | 56.84%
NQ | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1
NQ | 118_Cannonvale No 2 66 kV | Loading (A) | 103.4667 | 104.6976 | 106.1804 | 107.9779 | 109.7053
NQ | 118_Cannonvale No 2 66 kV | Loading (MVA) | 12.4433 | 12.6008 | 12.7882 | 13.0138 | 13.2296
NQ | 118_Cannonvale No 2 66 kV | Loading (MW) | 2.0303 | 2.7457 | 3.4546 | 4.1875 | 4.8099
NQ | 118_Cannonvale No 2 66 kV | Power Factor | 0.16307 | 0.21781 | 0.27005 | 0.32169 | 0.36349
NQ | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
NQ | 118_Cannonvale No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 118_Cannonvale No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.052 | 1.0528 | 1.0535 | 1.0543 | 1.0549
NQ | 118_Cannonvale No 2 66 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV
NQ | 119_Cannonvale No 1 66 kV | % of Rated A | 57.5% | 57.78% | 58.3% | 59.09% | 59.94%
NQ | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQ | 119_Cannonvale No 1 66 kV | Loading (A) | 106.3794 | 106.8867 | 107.8525 | 109.3083 | 110.8832
NQ | 119_Cannonvale No 1 66 kV | Loading (MVA) | 12.7659 | 12.8401 | 12.9688 | 13.1568 | 13.3572
NQ | 119_Cannonvale No 1 66 kV | Loading (MW) | 0.062444 | 0.9846 | 1.8912 | 2.8206 | 3.6022
NQ | 119_Cannonvale No 1 66 kV | Power Factor | 0.0040772 | 0.075871 | 0.14503 | 0.2136 | 0.26893
NQ | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 185 | 185 | 185 | 185
NQ | 119_Cannonvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 119_Cannonvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0497 | 1.0508 | 1.0517 | 1.0527 | 1.0534
NQ | 119_Cannonvale No 1 66 kV | Contingency Outage | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV
NQ | 120_Prosperpine - Calen 66 kV | % of Rated A | 16.38% | 17.4% | 18.48% | 19.55% | 22.22%
NQ | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1
NQ | 120_Prosperpine - Calen 66 kV | Loading (A) | 21.6192 | 22.9719 | 24.3978 | 25.8001 | 29.3311
NQ | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 2.5771 | 2.7404 | 2.9125 | 3.0819 | 3.514
NQ | 120_Prosperpine - Calen 66 kV | Loading (MW) | 2.3295 | 2.5096 | 2.6974 | 2.8805 | 3.3401
NQ | 120_Prosperpine - Calen 66 kV | Power Factor | 0.90389 | 0.91577 | 0.92613 | 0.93461 | 0.95051
NQ | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ | 120_Prosperpine - Calen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 120_Prosperpine - Calen 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0428 | 1.0435 | 1.0443 | 1.0449 | 1.048
NQ | 120_Prosperpine - Calen 66 kV | Contingency Outage | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | 125_Hayman Island 22 kV | % of Rated A | 6.368% | 6.359% | 6.351% | 6.343% | 6.396%
NQ | 125_Hayman Island 22 kV | Limiting Line Name | HV_CABLE 41068222_1 | HV_CABLE 41068222_1 | HV_CABLE 41068222_1 | HV_CABLE 41068222_1 | HV_CABLE 41068222_1
NQ | 125_Hayman Island 22 kV | Loading (A) | 17.5133 | 17.4886 | 17.4651 | 17.4419 | 17.5899
NQ | 125_Hayman Island 22 kV | Loading (MVA) | 0.6877 | 0.6877 | 0.6877 | 0.6877 | 0.69603
NQ | 125_Hayman Island 22 kV | Loading (MW) | 0.68651 | 0.6865 | 0.68649 | 0.68648 | 0.69482
NQ | 125_Hayman Island 22 kV | Power Factor | 0.99827 | 0.99825 | 0.99824 | 0.99823 | 0.99825
NQ | 125_Hayman Island 22 kV | Rating (A) | 275 | 275 | 275 | 275 | 275
NQ | 125_Hayman Island 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 125_Hayman Island 22 kV | Min Voltage at Constrained Conductor (pu) | 1.0304 | 1.0319 | 1.0332 | 1.0346 | 1.0384
NQ | 125_Hayman Island 22 kV | Contingency Outage | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | 426_Mt Rooper 66 kV | % of Rated A | 10.38% | 10.33% | 10.28% | 10.25% | 10.78%
NQ | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1
NQ | 426_Mt Rooper 66 kV | Loading (A) | 25.8522 | 25.7169 | 25.6079 | 25.5113 | 26.8329
NQ | 426_Mt Rooper 66 kV | Loading (MVA) | 3.1254 | 3.1134 | 3.1044 | 3.0968 | 3.2692
NQ | 426_Mt Rooper 66 kV | Loading (MW) | 3.0583 | 3.0456 | 3.0359 | 3.0277 | 3.2037
NQ | 426_Mt Rooper 66 kV | Power Factor | 0.97853 | 0.97821 | 0.97794 | 0.97769 | 0.97996
NQ | 426_Mt Rooper 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
NQ | 426_Mt Rooper 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 426_Mt Rooper 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0576 | 1.059 | 1.0605 | 1.0619 | 1.0658
NQ | 426_Mt Rooper 66 kV | Contingency Outage | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | CANN_JUPO (Ex119&118) | % of Rated A | 7.776% | 7.327% | 6.931% | 6.564% | 6.458%
NQ | CANN_JUPO (Ex119&118) | Limiting Line Name | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1
NQ | CANN_JUPO (Ex119&118) | Loading (A) | 21.772 | 20.5162 | 19.4076 | 18.3803 | 18.0829
NQ | CANN_JUPO (Ex119&118) | Loading (MVA) | 2.6324 | 2.5248 | 2.393 | 2.2706 | 2.2032
NQ | CANN_JUPO (Ex119&118) | Loading (MW) | 2.0004 | 1.7974 | 1.6019 | 1.4075 | 1.3746
NQ | CANN_JUPO (Ex119&118) | Power Factor | 0.75992 | 0.71188 | 0.66944 | 0.6199 | 0.62392
NQ | CANN_JUPO (Ex119&118) | Rating (A) | 280 | 280 | 280 | 280 | 280
NQ | CANN_JUPO (Ex119&118) | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CANN_JUPO (Ex119&118) | Min Voltage at Constrained Conductor (pu) | 1.0577 | 1.0765 | 1.0786 | 1.0806 | 1.0658
NQ | CANN_JUPO (Ex119&118) | Contingency Outage | PR-BN-1_Proserpine - Bowen No 1 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | 118_Cannonvale No 2 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 32.57% | 33.71% | 34.9% | 36.16% | 37.28%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 63.5021 | 65.7388 | 68.0501 | 70.5182 | 72.7018
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 7.6347 | 7.9059 | 8.1859 | 8.485 | 8.7495
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 4.5615 | 5.0149 | 5.4595 | 5.9133 | 6.3004
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.59744 | 0.63429 | 0.66689 | 0.69687 | 0.72004
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0517 | 1.052 | 1.0523 | 1.0526 | 1.0528
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Contingency Outage | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 10.32% | 10.53% | 11.19% | 12.23% | 13.11%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175208_1 | TR_LINE 175208_1 | TR_LINE 175208_1
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 19.9127 | 20.3233 | 21.5901 | 23.5954 | 25.3108
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 2.3849 | 2.4356 | 2.5741 | 2.8139 | 3.0191
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 1.8953 | 1.9705 | 2.343 | 2.6187 | 2.8504
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.79472 | 0.80906 | 0.90439 | 0.92411 | 0.93703
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0477 | 1.0483 | 1.043 | 1.0432 | 1.0435
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 64.83% | 64.79% | 64.75% | 64.71% | 68.12%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 129.0181 | 128.9297 | 128.8478 | 128.7668 | 135.5558
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 15.2331 | 15.233 | 15.2328 | 15.2326 | 16.0496
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 15.2331 | 15.2329 | 15.2327 | 15.2325 | 16.0495
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0238 | 1.0245 | 1.0252 | 1.0258 | 1.0262
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Contingency Outage | 120_Prosperpine - Calen 66 kV | 120_Prosperpine - Calen 66 kV | 120_Prosperpine - Calen 66 kV | 120_Prosperpine - Calen 66 kV | WO-CT-1_Woodstock-CHTO No 1 66 kV
NQ | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 9.126% | 9.833% | 10.5% | 11.13% | 11.86%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 16.1522 | 17.4051 | 18.5788 | 19.7036 | 20.9959
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 1.9255 | 2.0764 | 2.2179 | 2.3537 | 2.5154
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 1.9252 | 2.076 | 2.2175 | 2.3532 | 2.5148
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.99985 | 0.99983 | 0.99981 | 0.99978 | 0.99976
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0428 | 1.0436 | 1.0443 | 1.045 | 1.048
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Contingency Outage | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 18.23% | 19.65% | 20.97% | 22.24% | 23.75%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 32.2742 | 34.7751 | 37.1177 | 39.3623 | 42.0428
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 3.8474 | 4.1486 | 4.4311 | 4.7022 | 5.0371
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 3.8469 | 4.1479 | 4.4302 | 4.7012 | 5.0359
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.99985 | 0.99983 | 0.99981 | 0.99978 | 0.99976
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0428 | 1.0436 | 1.0443 | 1.045 | 1.048
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Contingency Outage | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 15.35% | 15.32% | 15.3% | 15.26% | 15.24%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 131.2718 | 131.0093 | 130.792 | 130.4952 | 130.3019
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 52.6811 | 52.5771 | 52.3325 | 52.2152 | 54.0918
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 43.0229 | 42.8868 | 42.7502 | 42.5974 | 42.929
NQ | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.81667 | 0.81569 | 0.8169 | 0.8158 | 0.79363
NQ | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 855 | 855 | 855 | 855
NQ | 7018_Mica Creek C - Chumvale 220 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 7018_Mica Creek C - Chumvale 220 kV | Min Voltage at Constrained Conductor (pu) | 1.0532 | 1.0532 | 1.05 | 1.0501 | 1.0894
NQ | 7018_Mica Creek C - Chumvale 220 kV | Contingency Outage | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | CH-CC-1_Chumvale-Cloncurry 66 kV
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 0.9665% | 0.9263% | 1.305% | 1.993% | 2.644%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 1.5754 | 1.5099 | 2.1275 | 3.2479 | 4.3095
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 0.19708 | 0.1889 | 0.24646 | 0.37628 | 0.4993
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 0.079279 | 0.055452 | 0.19192 | 0.34321 | 0.47506
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.40227 | 0.29355 | 0.77869 | 0.91209 | 0.95143
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 163 | 163 | 163 | 163
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0943 | 1.0944 | 1.0134 | 1.0135 | 1.0135
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 17.25% | 17.26% | 17.33% | 17.56% | 17.85%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 14.3148 | 14.3276 | 14.3865 | 14.5773 | 14.8168
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 1.7831 | 1.7851 | 1.7889 | 1.8131 | 1.8433
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.091672 | 0.043183 | 0.17935 | 0.32984 | 0.46063
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.051413 | 0.024121 | 0.10019 | 0.18185 | 0.24983
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 83 | 83 | 83 | 83
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0896 | 1.0899 | 1.0877 | 1.088 | 1.0883
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Contingency Outage | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV | 7018_Mica Creek C - Chumvale 220 kV
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 3.283% | 3.814% | 4.372% | 4.96% | 5.47%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 12.605 | 14.6441 | 16.7868 | 19.0462 | 21.0044
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 3.0344 | 3.5254 | 4.0368 | 4.5802 | 5.0512
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 2.2632 | 2.8926 | 3.4819 | 4.1039 | 4.6275
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.74581 | 0.82047 | 0.8625 | 0.89597 | 0.91607
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 384 | 384 | 384 | 384
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0529 | 1.0529 | 1.0518 | 1.0518 | 1.0518
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Contingency Outage | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | MICB-DURO 2_Mica Creek B-DURO 2 132 kV
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 4.346% | 5.102% | 5.861% | 6.69% | 7.406%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 12.1249 | 14.2349 | 16.3517 | 18.6661 | 20.6623
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 2.9187 | 3.4266 | 3.9318 | 4.4884 | 4.9685
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 2.2632 | 2.8926 | 3.4822 | 4.1042 | 4.6278
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.77538 | 0.8441 | 0.88558 | 0.91433 | 0.93134
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 279 | 279 | 279 | 279
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0529 | 1.0529 | 1.0517 | 1.0517 | 1.0518
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Contingency Outage | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV
NQ | MICC-MICB No 1 132 kV | % of Rated A | 75.54% | 75.5% | 75.4% | 75.35% | 75.31%
NQ | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ | MICC-MICB No 1 132 kV | Loading (A) | 394.326 | 394.0978 | 393.6041 | 393.3462 | 393.1208
NQ | MICC-MICB No 1 132 kV | Loading (MVA) | 95.0109 | 94.9577 | 94.7445 | 94.6845 | 94.632
NQ | MICC-MICB No 1 132 kV | Loading (MW) | 52.1711 | 52.0349 | 51.8966 | 51.7437 | 51.6105
NQ | MICC-MICB No 1 132 kV | Power Factor | 0.54905 | 0.54792 | 0.5477 | 0.54643 | 0.54532
NQ | MICC-MICB No 1 132 kV | Rating (A) | 522 | 522 | 522 | 522 | 522
NQ | MICC-MICB No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICC-MICB No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0537 | 1.0537 | 1.0527 | 1.0527 | 1.0527
NQ | MICC-MICB No 1 132 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV
NQ | MICC-MICB No 2 132 kV | % of Rated A | 75.53% | 75.48% | 75.39% | 75.34% | 75.3%
NQ | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ | MICC-MICB No 2 132 kV | Loading (A) | 394.2553 | 394.0269 | 393.533 | 393.2749 | 393.0493
NQ | MICC-MICB No 2 132 kV | Loading (MVA) | 94.992 | 94.9388 | 94.7255 | 94.6654 | 94.6129
NQ | MICC-MICB No 2 132 kV | Loading (MW) | 52.1703 | 52.0341 | 51.8958 | 51.7429 | 51.6097
NQ | MICC-MICB No 2 132 kV | Power Factor | 0.54915 | 0.54803 | 0.5478 | 0.54654 | 0.54543
NQ | MICC-MICB No 2 132 kV | Rating (A) | 522 | 522 | 522 | 522 | 522
NQ | MICC-MICB No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICC-MICB No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0537 | 1.0537 | 1.0527 | 1.0527 | 1.0527
NQ | MICC-MICB No 2 132 kV | Contingency Outage | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV
NQ | 6127_Bohle-Black River 1 66 kV | % of Rated A | 24.03% | 25.72% | 27.22% | 28.66% | 29.8%
NQ | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ | 6127_Bohle-Black River 1 66 kV | Loading (A) | 175.1583 | 187.4838 | 198.469 | 208.9135 | 217.2425
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 21.2784 | 22.7702 | 24.1091 | 25.378 | 26.3939
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 21.2695 | 22.7556 | 24.0882 | 25.3498 | 26.359
NQ | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.99958 | 0.99936 | 0.99913 | 0.99889 | 0.99868
NQ | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
NQ | 6127_Bohle-Black River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6127_Bohle-Black River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0627 | 1.0624 | 1.0626 | 1.0626 | 1.0628
NQ | 6127_Bohle-Black River 1 66 kV | Contingency Outage | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV
NQ | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 24.03% | 25.72% | 27.22% | 28.66% | 29.8%
NQ | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 175.1532 | 187.4777 | 198.462 | 208.9055 | 217.2336
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 21.2788 | 22.7707 | 24.1097 | 25.3786 | 26.3945
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 21.2699 | 22.7561 | 24.0887 | 25.3504 | 26.3597
NQ | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.99958 | 0.99935 | 0.99913 | 0.99888 | 0.99867
NQ | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
NQ | 6266_Bohle-Black River No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6266_Bohle-Black River No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0627 | 1.0624 | 1.0627 | 1.0627 | 1.0628
NQ | 6266_Bohle-Black River No 2 66 kV | Contingency Outage | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV
NQ | 6299_Townsville Port 66 kV | % of Rated A | 7.002% | 2.793% | 3.408% | 3.798% | 4.927%
NQ | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96490_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96490_1
NQ | 6299_Townsville Port 66 kV | Loading (A) | 76.4578 | 30.4953 | 37.2116 | 41.4692 | 53.8066
NQ | 6299_Townsville Port 66 kV | Loading (MVA) | 9.224 | 3.675 | 4.484 | 4.9973 | 6.4469
NQ | 6299_Townsville Port 66 kV | Loading (MW) | 3.515 | 3.6735 | 4.4802 | 4.9945 | 6.2493
NQ | 6299_Townsville Port 66 kV | Power Factor | 0.38107 | 0.99959 | 0.99914 | 0.99944 | 0.96935
NQ | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
NQ | 6299_Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6299_Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0553 | 1.0542 | 1.0541 | 1.0541 | 1.0481
NQ | 6299_Townsville Port 66 kV | Contingency Outage | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV
NQ | 6312_Merinda - Home Hill 66 kV | % of Rated A | 5.762% | 5.743% | 5.726% | 5.708% | 5.899%
NQ | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 32515_1
NQ | 6312_Merinda - Home Hill 66 kV | Loading (A) | 14.8653 | 14.8172 | 14.7726 | 14.7254 | 15.2189
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 1.792 | 1.7849 | 1.7807 | 1.7762 | 1.8279
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 1.1522 | 1.1436 | 1.1344 | 1.1248 | 1.2343
NQ | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.64297 | 0.6407 | 0.63706 | 0.63324 | 0.67527
NQ | 6312_Merinda - Home Hill 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ | 6312_Merinda - Home Hill 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6312_Merinda - Home Hill 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0545 | 1.0537 | 1.0545 | 1.0552 | 1.0507
NQ | 6312_Merinda - Home Hill 66 kV | Contingency Outage | 7182 Ross - Milchester | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 23.37% | 23.13% | 24.68% | 25.64% | 26.92%
NQ | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 31738_1 | TR_LINE 31738_1
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 75.9461 | 75.1769 | 80.203 | 83.3441 | 87.4814
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 9.109 | 9.0174 | 9.6202 | 9.9879 | 10.4831
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 8.6228 | 9.0169 | 9.6178 | 9.9307 | 10.4395
NQ | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.94661 | 0.99995 | 0.99975 | 0.99427 | 0.99584
NQ | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 325 | 325 | 325 | 325
NQ | 6325_Oonoonba-Stuart 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6325_Oonoonba-Stuart 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0492 | 1.049 | 1.0489 | 1.0483 | 1.0482
NQ | 6325_Oonoonba-Stuart 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ | 6382 JACR-HUGH 66kV | % of Rated A | 79.37% | 78.56% | 78.86% | 79.17% | 79.43%
NQ | 6382 JACR-HUGH 66kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ | 6382 JACR-HUGH 66kV | Loading (A) | 112.7093 | 111.5521 | 111.975 | 112.4243 | 112.7858
NQ | 6382 JACR-HUGH 66kV | Loading (MVA) | 19.3593 | 18.9638 | 19.1079 | 19.2616 | 19.3856
NQ | 6382 JACR-HUGH 66kV | Loading (MW) | 0.397 | 0.38884 | 0.39184 | 0.39499 | 0.39748
NQ | 6382 JACR-HUGH 66kV | Power Factor | 0.0076707 | 0.007668 | 0.0076707 | 0.0076707 | 0.0076676
NQ | 6382 JACR-HUGH 66kV | Rating (A) | 142 | 142 | 142 | 142 | 142
NQ | 6382 JACR-HUGH 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6382 JACR-HUGH 66kV | Min Voltage at Constrained Conductor (pu) | 1.5025 | 1.4871 | 1.4928 | 1.4987 | 1.5036
NQ | 6382 JACR-HUGH 66kV | Contingency Outage | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV
NQ | 6383 CARI-CPRE 66kV | % of Rated A | 47% | 46.18% | 46.35% | 46.53% | 46.68%
NQ | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ | 6383 CARI-CPRE 66kV | Loading (A) | 146.6554 | 144.0774 | 144.6083 | 145.1733 | 145.6264
NQ | 6383 CARI-CPRE 66kV | Loading (MVA) | 21.396 | 20.6253 | 20.7479 | 20.8784 | 20.982
NQ | 6383 CARI-CPRE 66kV | Loading (MW) | 0.85926 | 0.97793 | 1.1458 | 1.3223 | 1.4675
NQ | 6383 CARI-CPRE 66kV | Power Factor | 0.040102 | 0.047355 | 0.055165 | 0.063273 | 0.069885
NQ | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 312 | 312 | 312 | 312
NQ | 6383 CARI-CPRE 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6383 CARI-CPRE 66kV | Min Voltage at Constrained Conductor (pu) | 1.2762 | 1.2523 | 1.2551 | 1.258 | 1.2604
NQ | 6383 CARI-CPRE 66kV | Contingency Outage | 7182 Ross - Milchester | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV
NQ | 7182 Ross - Milchester | % of Rated A | 47.54% | 48.25% | 48.08% | 47.89% | 47.76%
NQ | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 178521_1 | TR_LINE 178521_1 | TR_LINE 178521_1 | TR_LINE 178521_1 | TR_LINE 178521_1
NQ | 7182 Ross - Milchester | Loading (A) | 158.3136 | 160.683 | 160.1085 | 159.4639 | 159.0405
NQ | 7182 Ross - Milchester | Loading (MVA) | 38.3143 | 38.7345 | 38.5939 | 38.4376 | 38.401
NQ | 7182 Ross - Milchester | Loading (MW) | 12.052 | 21.9225 | 21.4135 | 20.8701 | 20.6266
NQ | 7182 Ross - Milchester | Power Factor | 0.31455 | 0.56597 | 0.55484 | 0.54296 | 0.53714
NQ | 7182 Ross - Milchester | Rating (A) | 333 | 333 | 333 | 333 | 333
NQ | 7182 Ross - Milchester | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 7182 Ross - Milchester | Min Voltage at Constrained Conductor (pu) | 1.0585 | 1.0544 | 1.0543 | 1.0543 | 1.0561
NQ | 7182 Ross - Milchester | Contingency Outage | CHTO_Clare South - Charters Towers 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | 7460 CPRE-JACR 132kV | % of Rated A | 41.92% | 41.19% | 41.34% | 41.5% | 41.63%
NQ | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ | 7460 CPRE-JACR 132kV | Loading (A) | 72.5251 | 71.2516 | 71.5157 | 71.7966 | 72.0219
NQ | 7460 CPRE-JACR 132kV | Loading (MVA) | 21.776 | 20.9924 | 21.118 | 21.2517 | 21.3579
NQ | 7460 CPRE-JACR 132kV | Loading (MW) | 0.94339 | 1.059 | 1.2272 | 1.4042 | 1.5498
NQ | 7460 CPRE-JACR 132kV | Power Factor | 0.042901 | 0.050023 | 0.05769 | 0.06565 | 0.072139
NQ | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 173 | 173 | 173 | 173
NQ | 7460 CPRE-JACR 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 7460 CPRE-JACR 132kV | Min Voltage at Constrained Conductor (pu) | 1.3133 | 1.2886 | 1.2916 | 1.2947 | 1.2971
NQ | 7460 CPRE-JACR 132kV | Contingency Outage | 7182 Ross - Milchester | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 21.28% | 20.33% | 20.71% | 19.28% | 19.61%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 70.8504 | 67.6831 | 68.9718 | 64.1989 | 65.3001
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 8.5645 | 8.1774 | 8.3335 | 7.7569 | 7.8902
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 7.6453 | 8.1751 | 8.333 | 7.7558 | 7.8901
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.89268 | 0.99972 | 0.99994 | 0.99985 | 0.99999
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 333 | 333 | 333 | 333
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0574 | 1.0568 | 1.0569 | 1.0569 | 1.0569
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 15.94% | 16.9% | 17.68% | 17.33% | 17.92%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 73.3109 | 77.7535 | 81.332 | 79.7294 | 82.4546
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 8.8768 | 9.3635 | 9.7946 | 9.6023 | 9.9306
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 1.4458 | 8.5823 | 9.0951 | 8.8682 | 9.2613
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.16273 | 0.91642 | 0.92842 | 0.9234 | 0.93244
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 460 | 460 | 460 | 460
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0592 | 1.0535 | 1.0535 | 1.0535 | 1.0535
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Contingency Outage | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 13.79% | 13.85% | 14.03% | 14.5% | 14.9%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 35.7156 | 35.8617 | 36.3334 | 37.5461 | 38.5972
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 4.2934 | 4.309 | 4.3816 | 4.5316 | 4.6613
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 3.9583 | 3.9779 | 3.3415 | 3.5197 | 3.6703
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.92165 | 0.92285 | 0.76231 | 0.77638 | 0.78708
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 259 | 259 | 259 | 259
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0516 | 1.0511 | 1.0549 | 1.0558 | 1.0564
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 15.61% | 16.01% | 16.38% | 16.8% | 17.2%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 32456_1 | TR_LINE 32456_1 | TR_LINE 32456_1 | TR_LINE 32456_1 | TR_LINE 32456_1
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 31.0597 | 31.8548 | 32.5935 | 33.4263 | 34.2189
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 3.7282 | 3.8211 | 3.9117 | 4.0138 | 4.1105
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 2.8987 | 3.032 | 3.1545 | 3.2896 | 3.4118
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.77747 | 0.79344 | 0.80637 | 0.81951 | 0.82996
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.05 | 1.0493 | 1.0499 | 1.0504 | 1.0508
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Contingency Outage | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 23.84% | 23.85% | 23.87% | 24.15% | 24.75%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 214252_1 | TR_LINE 214252_1
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 16.4475 | 16.4538 | 16.4676 | 45.6477 | 46.7839
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 2.0538 | 2.0554 | 2.0587 | 5.5614 | 5.701
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 0.036271 | 0.021786 | 0.0072925 | 4.6959 | 4.8648
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.017649 | 0.010588 | 0.0035294 | 0.8431 | 0.85203
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 69 | 69 | 69 | 189 | 189
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0923 | 1.0927 | 1.0936 | 1.0658 | 1.066
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Contingency Outage | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 48.75% | 51.96% | 54.91% | 55.85% | 58.55%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 217.9208 | 232.2825 | 245.4522 | 249.6535 | 261.7347
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 26.3153 | 28.1137 | 29.7086 | 30.2131 | 31.6759
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 26.168 | 28.0004 | 29.6239 | 30.1455 | 31.6269
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.99413 | 0.9957 | 0.99688 | 0.9975 | 0.99819
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0563 | 1.0588 | 1.0588 | 1.0587 | 1.0587
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 112% | 146.4% | 145.5% | 144.7% | 143.9%
NQ | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 288.957 | 377.6114 | 375.2895 | 373.1975 | 371.2509
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 34.4912 | 44.9366 | 44.6679 | 44.4267 | 44.2006
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 28.4904 | 43.0781 | 42.6825 | 42.304 | 41.966
NQ | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.82593 | 0.95858 | 0.95549 | 0.95216 | 0.94938
NQ | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ | CHTO_Clare South - Charters Towers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CHTO_Clare South - Charters Towers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0442 | 1.0409 | 1.0411 | 1.0413 | 1.0414
NQ | CHTO_Clare South - Charters Towers 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 13.33% | 14.07% | 14.74% | 15.39% | 15.9%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 41.5995 | 43.8971 | 45.9781 | 48.0276 | 49.6198
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 4.9425 | 5.209 | 5.4559 | 5.6992 | 5.888
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 4.4123 | 4.7194 | 4.9974 | 5.2687 | 5.4793
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.8927 | 0.90597 | 0.91593 | 0.92442 | 0.93054
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 312 | 312 | 312 | 312
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0393 | 1.038 | 1.038 | 1.038 | 1.038
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 23.12% | 24.46% | 25.67% | 26.87% | 27.79%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 39.0667 | 41.3389 | 43.3894 | 45.4049 | 46.9698
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 4.6791 | 4.9466 | 5.1933 | 5.436 | 5.6243
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 4.374 | 4.6706 | 4.9396 | 5.2021 | 5.4058
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.93471 | 0.94413 | 0.95106 | 0.95689 | 0.96105
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0477 | 1.0468 | 1.047 | 1.0473 | 1.0475
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 144.8% | 143.3% | 143.8% | 144.4% | 144.9%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 207.0367 | 204.8938 | 205.6686 | 206.5008 | 207.1767
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 28.6753 | 28.0418 | 28.2077 | 28.3867 | 28.5312
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 6.2223 | 5.86 | 5.6629 | 5.4566 | 5.2858
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.21691 | 0.20889 | 0.20068 | 0.19214 | 0.18518
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2115 | 1.1971 | 1.1997 | 1.2024 | 1.2046
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Contingency Outage | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV
NQ | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 3.81% | 3.974% | 4.117% | 4.264% | 4.549%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 7.4299 | 7.7484 | 8.0273 | 8.3148 | 8.8703
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 0.87972 | 0.91741 | 0.95043 | 0.98446 | 1.0535
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 0.70463 | 0.75145 | 0.79167 | 0.83247 | 0.91163
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.80098 | 0.8191 | 0.83296 | 0.84561 | 0.86532
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0358 | 1.0357 | 1.0357 | 1.0357 | 1.0389
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Contingency Outage | CHTO_Clare South - Charters Towers 66 kV | CHTO_Clare South - Charters Towers 66 kV | CHTO_Clare South - Charters Towers 66 kV | CHTO_Clare South - Charters Towers 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 90.92% | 89.85% | 90.19% | 90.56% | 90.86%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 167.2972 | 165.3276 | 165.9524 | 166.6241 | 167.1742
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 21.0727 | 20.5288 | 20.6286 | 20.7361 | 20.823
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 5.078 | 4.7063 | 4.4815 | 4.2473 | 4.054
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.23943 | 0.22771 | 0.2157 | 0.20327 | 0.19313
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 184 | 184 | 184 | 184
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.1014 | 1.0857 | 1.0868 | 1.0881 | 1.089
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Contingency Outage | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 97.52% | 92.69% | 93.01% | 93.36% | 93.64%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 271.0966 | 257.6799 | 258.574 | 259.5482 | 260.3184
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 36.5376 | 32.9827 | 33.2586 | 33.5525 | 33.7852
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 11.3328 | 10.7849 | 10.5391 | 10.2912 | 10.0847
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.31003 | 0.32685 | 0.31675 | 0.30659 | 0.29836
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.1788 | 1.1196 | 1.125 | 1.1307 | 1.1352
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 20.13% | 16.04% | 16.33% | 16.67% | 16.94%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 90.9854 | 72.5144 | 73.8268 | 75.3286 | 76.558
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 10.9879 | 8.786 | 8.9457 | 9.1273 | 9.2766
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 6.2286 | 2.1317 | 2.7226 | 3.2829 | 3.6846
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.56683 | 0.24253 | 0.30425 | 0.35958 | 0.39709
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0564 | 1.0599 | 1.06 | 1.0599 | 1.06
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 13.24% | 14.27% | 14.16% | 13.14% | 13.45%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 172527_2 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 172527_2
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 72.9503 | 78.6411 | 77.9962 | 72.3943 | 74.0853
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 8.786 | 9.4813 | 9.4037 | 8.7279 | 8.8938
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 8.6632 | 9.4785 | 9.4025 | 8.7262 | 7.8163
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.98603 | 0.99971 | 0.99987 | 0.9998 | 0.87885
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0535 | 1.0546 | 1.0547 | 1.0546 | 1.0501
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 25.53% | 26.92% | 28.24% | 29.41% | 31.1%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 64.0777 | 67.5801 | 70.8769 | 73.8307 | 78.0621
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 7.7221 | 8.1586 | 8.5566 | 8.9122 | 9.3653
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 7.3115 | 7.7759 | 8.1998 | 8.5768 | 9.0646
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.94683 | 0.95309 | 0.9583 | 0.96237 | 0.96789
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 251 | 251 | 251 | 251
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0542 | 1.0561 | 1.0561 | 1.0559 | 1.0495
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Contingency Outage | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV
NQ | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 19.85% | 21.02% | 22.08% | 23.15% | 23.99%
NQ | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 41.6787 | 44.1332 | 46.3636 | 48.6102 | 50.3812
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 5.0231 | 5.315 | 5.5861 | 5.8594 | 6.0748
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 4.298 | 4.6344 | 4.9392 | 5.2428 | 5.4825
NQ | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.85557 | 0.87188 | 0.88411 | 0.89468 | 0.90241
NQ | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 210 | 210 | 210 | 210
NQ | EAAY_Clare South - East Ayr 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | EAAY_Clare South - East Ayr 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0543 | 1.0535 | 1.054 | 1.0544 | 1.0548
NQ | EAAY_Clare South - East Ayr 66 kV | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 39.36% | 42.17% | 44.56% | 45.32% | 47.51%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 128084_1
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 216.8934 | 232.3444 | 245.5324 | 249.7117 | 261.8021
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 26.2603 | 28.0488 | 29.6429 | 30.1488 | 31.6103
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 26.1336 | 27.9583 | 29.5769 | 30.0969 | 31.5735
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.99517 | 0.99677 | 0.99777 | 0.99828 | 0.99884
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0591 | 1.056 | 1.056 | 1.0561 | 1.0561
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 14.87% | 13.36% | 12.77% | 12.43% | 13.95%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 77120_1 | TR_LINE 77120_1 | TR_LINE 77120_1 | TR_LINE 77120_1
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 51.3107 | 46.0926 | 44.0724 | 42.8918 | 48.1286
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 6.2067 | 5.5557 | 5.3126 | 5.1787 | 5.8113
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 5.5171 | 5.5524 | 5.3042 | 5.1784 | 5.8111
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.88878 | 0.9994 | 0.99842 | 0.99994 | 0.99997
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 345 | 345 | 345 | 345
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0581 | 1.0544 | 1.0545 | 1.0562 | 1.0562
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 13.12% | 17.83% | 19.44% | 18.75% | 17.83%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 22.1777 | 30.1374 | 32.8487 | 31.6929 | 30.1252
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 2.6798 | 3.6327 | 3.9596 | 3.8205 | 3.6069
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 2.5449 | 3.5427 | 3.8799 | 3.7366 | 3.5189
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.94966 | 0.97523 | 0.97987 | 0.97804 | 0.9756
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.057 | 1.0544 | 1.0544 | 1.0545 | 1.0474
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Contingency Outage | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV | TP-NS-1_Townsville Port-NESM No 1 66 kV
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 32.68% | 35.07% | 36.9% | 37.2% | 38.56%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 84.306 | 90.4914 | 95.1921 | 95.9847 | 99.4807
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 10.1576 | 10.9237 | 11.492 | 11.5883 | 12.011
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 9.749 | 10.4797 | 11.0365 | 11.1271 | 11.5376
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.95974 | 0.95935 | 0.96036 | 0.9602 | 0.96059
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0539 | 1.0558 | 1.0558 | 1.0559 | 1.0559
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Contingency Outage | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV
NQ | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 9.221% | 9.683% | 10.11% | 10.54% | 11.63%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 17.4279 | 18.3009 | 19.1114 | 19.9186 | 21.9819
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 2.093 | 2.1966 | 2.2952 | 2.3935 | 2.6413
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 1.7559 | 1.8801 | 1.9947 | 2.1075 | 2.3882
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.83893 | 0.85593 | 0.8691 | 0.88051 | 0.90418
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 189 | 189 | 189 | 189
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0506 | 1.0499 | 1.0506 | 1.0512 | 1.0511
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Contingency Outage | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV | ST-GI-1_Stuart-Giru 66 kV
NQ | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 15.18% | 14.72% | 15.24% | 15.34% | 15.89%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 52.3824 | 50.7916 | 52.59 | 52.9153 | 54.8257
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 6.3136 | 6.1142 | 6.3314 | 6.3684 | 6.5989
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 5.5993 | 6.1127 | 6.3267 | 6.2779 | 6.5272
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.88675 | 0.99976 | 0.99925 | 0.98572 | 0.98908
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 345 | 345 | 345 | 345
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0544 | 1.053 | 1.0531 | 1.0528 | 1.0528
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 16.07% | 15.89% | 15.93% | 15.97% | 16.01%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 45.802 | 45.2819 | 45.3928 | 45.5196 | 45.6262
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 7.882 | 7.7126 | 7.7609 | 7.814 | 7.8575
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 1.3195 | 1.217 | 1.1221 | 1.0223 | 0.93918
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.1674 | 0.15779 | 0.14458 | 0.13083 | 0.11953
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 285 | 285 | 285 | 285
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.5054 | 1.49 | 1.4956 | 1.5016 | 1.5065
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Contingency Outage | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 14.62% | 14.48% | 14.55% | 14.62% | 14.68%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 38.3154 | 37.9507 | 38.1217 | 38.3067 | 38.459
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 6.5812 | 6.4516 | 6.5053 | 6.5631 | 6.6103
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 0.26727 | 0.33414 | 0.39695 | 0.46466 | 0.52183
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.040586 | 0.051767 | 0.060994 | 0.070773 | 0.078916
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 262 | 262 | 262 | 262
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.5025 | 1.4871 | 1.4928 | 1.4987 | 1.5036
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Contingency Outage | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 24.18% | 25.5% | 26.66% | 27.7% | 28.5%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 78407_1 | TR_LINE 78407_1 | TR_LINE 78407_1 | TR_LINE 78407_1 | TR_LINE 78407_1
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 31.9136 | 33.6645 | 35.1946 | 36.5705 | 37.6192
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 3.9345 | 4.1458 | 4.3387 | 4.5128 | 4.6455
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 3.921 | 4.1341 | 4.3284 | 4.5036 | 4.6371
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.99655 | 0.99717 | 0.9976 | 0.99794 | 0.99818
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0785 | 1.0773 | 1.0784 | 1.0795 | 1.0802
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Contingency Outage | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 11.67% | 11.68% | 11.7% | 11.75% | 12.12%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 19.7227 | 19.7383 | 19.7666 | 19.8509 | 20.4815
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 2.3754 | 2.3758 | 2.3806 | 2.3949 | 2.4723
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 0.77149 | 0.8179 | 0.85713 | 2.3946 | 2.4721
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.32476 | 0.34424 | 0.36002 | 0.99987 | 0.99989
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0536 | 1.0529 | 1.0535 | 1.0553 | 1.0559
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Contingency Outage | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 5.911% | 6.139% | 6.343% | 6.535% | 7.052%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 11.7639 | 12.2174 | 12.6233 | 13.0045 | 14.0329
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 1.407 | 1.4618 | 1.5112 | 1.5576 | 1.6862
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 1.3963 | 1.4517 | 1.5015 | 1.5484 | 1.6779
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.99237 | 0.99305 | 0.99359 | 0.99405 | 0.99508
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0463 | 1.0467 | 1.0472 | 1.0478 | 1.0511
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Contingency Outage | CHTO_Clare South - Charters Towers 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 14.79% | 14.62% | 14.49% | 14.37% | 14.3%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 38.1588 | 37.7297 | 37.372 | 37.0665 | 36.9067
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 4.592 | 4.5448 | 4.5015 | 4.4649 | 4.4455
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 1.2646 | 1.0303 | 0.80646 | 0.54501 | 0.33834
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.2754 | 0.22669 | 0.17915 | 0.12206 | 0.076098
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0527 | 1.0537 | 1.0537 | 1.0537 | 1.0537
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Contingency Outage | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 14.99% | 14.83% | 14.69% | 14.57% | 14.51%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 38.6741 | 38.2516 | 37.8985 | 37.6023 | 37.4415
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 4.6544 | 4.6081 | 4.5653 | 4.5298 | 4.5103
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 1.2657 | 1.0314 | 0.80759 | 0.54588 | 0.33932
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.27195 | 0.22382 | 0.1769 | 0.12051 | 0.075222
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0528 | 1.0538 | 1.0538 | 1.0538 | 1.0538
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Contingency Outage | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV
NQ | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 21.47% | 22.7% | 23.84% | 25.01% | 25.94%
NQ | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 45.081 | 47.6749 | 50.0609 | 52.5227 | 54.4822
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 5.3559 | 5.657 | 5.9401 | 6.2323 | 6.4647
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 4.6791 | 5.0302 | 5.3519 | 5.6798 | 5.9408
NQ | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.87362 | 0.88919 | 0.90096 | 0.91134 | 0.91894
NQ | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 210 | 210 | 210 | 210
NQ | MOPA_Clare South - Mona Park 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MOPA_Clare South - Mona Park 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0393 | 1.038 | 1.038 | 1.038 | 1.038
NQ | MOPA_Clare South - Mona Park 66 kV | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 18.04% | 19.01% | 19.89% | 20.75% | 21.41%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 35.8959 | 37.8314 | 39.5787 | 41.294 | 42.6134
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 4.3024 | 4.5302 | 4.7408 | 4.9477 | 5.1068
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 3.7281 | 3.9938 | 4.2332 | 4.4657 | 4.6458
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.86651 | 0.8816 | 0.89294 | 0.90259 | 0.90972
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0485 | 1.0475 | 1.0478 | 1.0481 | 1.0483
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 108.6% | 107.4% | 107.7% | 108% | 108.2%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 168.3847 | 166.5425 | 166.943 | 167.3818 | 167.7359
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 21.328 | 20.8351 | 20.9028 | 20.9769 | 21.035
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 3.5701 | 3.2407 | 2.997 | 2.7425 | 2.5323
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.1673 | 0.15545 | 0.14329 | 0.13065 | 0.12029
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 155 | 155 | 155 | 155
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.1079 | 1.0943 | 1.0952 | 1.0962 | 1.0969
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 35.9% | 36.38% | 36.36% | 36.34% | 36.62%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 67.4853 | 68.402 | 68.3519 | 68.3195 | 68.8516
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 8.3299 | 8.3347 | 8.3343 | 8.3353 | 8.6713
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 8.3246 | 8.3293 | 8.3289 | 8.3295 | 8.6658
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.99762 | 0.99772 | 0.99773 | 0.99762 | 0.99762
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 188 | 188 | 188 | 188
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0566 | 1.0423 | 1.043 | 1.0437 | 1.0781
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Contingency Outage | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 18.85% | 22.28% | 23.21% | 22.24% | 24.05%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 32958_1
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 48.6355 | 57.483 | 59.8792 | 57.3789 | 62.0504
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 5.8548 | 6.9215 | 7.21 | 6.9089 | 7.4518
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 5.6986 | 6.9121 | 7.2041 | 6.9014 | 6.2256
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.97333 | 0.99864 | 0.99919 | 0.99892 | 0.83545
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 1.053 | 1.0533 | 1.0533 | 1.0533 | 1.0505
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 7.464% | 7.384% | 7.406% | 7.43% | 7.45%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 26.4959 | 26.2121 | 26.2917 | 26.3772 | 26.4471
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 4.6718 | 4.5751 | 4.6075 | 4.6423 | 4.6705
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 0.70892 | 0.67025 | 0.63398 | 0.59328 | 0.55916
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.15175 | 0.1465 | 0.1376 | 0.1278 | 0.11972
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 355 | 355 | 355 | 355
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.5424 | 1.5268 | 1.533 | 1.5396 | 1.5448
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Contingency Outage | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV
NQ | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 9.874% | 10.46% | 10.99% | 11.52% | 11.95%
NQ | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 195947_1 | TR_LINE 195947_1 | TR_LINE 195947_1 | TR_LINE 195947_1 | TR_LINE 195947_1
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 13.0332 | 13.8041 | 14.5076 | 15.2066 | 15.7738
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 1.5681 | 1.6597 | 1.7444 | 1.8287 | 1.897
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 1.4976 | 1.5941 | 1.6829 | 1.7708 | 1.8419
NQ | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.95422 | 0.9597 | 0.96388 | 0.96745 | 0.97001
NQ | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ | ST-GI-1_Stuart-Giru 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-GI-1_Stuart-Giru 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0525 | 1.0518 | 1.0518 | 1.052 | 1.052
NQ | ST-GI-1_Stuart-Giru 66 kV | Contingency Outage | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 11.73% | 12.38% | 12.97% | 13.5% | 13.89%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 64.6315 | 68.2162 | 71.469 | 74.3754 | 76.5525
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 7.7574 | 8.1792 | 8.569 | 8.9178 | 9.1791
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 7.3126 | 7.7771 | 8.2011 | 8.5783 | 8.8593
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.93893 | 0.94689 | 0.95292 | 0.95761 | 0.96077
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0499 | 1.0489 | 1.0488 | 1.0489 | 1.0488
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Contingency Outage | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 9.621% | 11.93% | 12.38% | 12.18% | 12.54%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 65.3275 | 81.038 | 84.0583 | 82.6734 | 85.1677
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 7.8376 | 9.7143 | 10.076 | 9.9101 | 10.2087
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 7.5126 | 8.8991 | 9.3243 | 9.1315 | 9.4841
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.95852 | 0.91607 | 0.92539 | 0.92142 | 0.92901
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 679 | 679 | 679 | 679
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0495 | 1.0486 | 1.0486 | 1.0486 | 1.0486
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 15.62% | 20.47% | 20.96% | 20.79% | 21.06%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 39.1979 | 51.385 | 52.603 | 52.1831 | 52.865
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 4.7369 | 6.1875 | 6.3336 | 6.2834 | 6.3651
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 1.8829 | 2.4086 | 2.6054 | 2.5249 | 2.6169
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.39749 | 0.38926 | 0.41135 | 0.40185 | 0.41112
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 251 | 251 | 251 | 251
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0571 | 1.0534 | 1.0533 | 1.0533 | 1.0533
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 15.52% | 16.98% | 17.4% | 17.67% | 16.41%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 142.9593 | 156.3511 | 160.2117 | 162.7808 | 151.1222
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 17.1685 | 18.7482 | 19.2111 | 19.52 | 18.1228
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 2.5135 | 7.6433 | 8.7662 | 9.367 | 5.0407
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.14638 | 0.40768 | 0.45631 | 0.47987 | 0.27813
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 921 | 921 | 921 | 921
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0505 | 1.0489 | 1.0489 | 1.0489 | 1.049
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Contingency Outage | 7182 Ross - Milchester | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | 7182 Ross - Milchester
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 8.987% | 8.13% | 8.874% | 9.32% | 8.035%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 82.774 | 74.8757 | 81.73 | 85.8366 | 74.005
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 9.9878 | 8.9951 | 9.8184 | 10.3122 | 8.8846
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 5.3384 | 6.3059 | 7.4544 | 8.0681 | 8.7372
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.53448 | 0.70103 | 0.75921 | 0.78237 | 0.9834
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 921 | 921 | 921 | 921
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0555 | 1.0509 | 1.0509 | 1.0509 | 1.0502
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Contingency Outage | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 128.3% | 134.3% | 134% | 133.6% | 133.4%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 169.3989 | 177.3276 | 176.9351 | 176.3459 | 176.1031
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 20.8242 | 21.4199 | 21.4038 | 21.3665 | 21.3624
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 9.3099 | 12.873 | 12.5833 | 12.2616 | 12.0224
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.43587 | 0.58959 | 0.57641 | 0.56231 | 0.55115
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0741 | 1.0567 | 1.0582 | 1.0599 | 1.0612
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 8.644% | 11.71% | 12.76% | 12.31% | 11.99%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 22.3015 | 30.2 | 32.9136 | 31.7579 | 30.9255
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 2.6822 | 3.6353 | 3.9616 | 3.8227 | 3.7224
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 2.5448 | 3.5418 | 3.8786 | 3.7355 | 3.6319
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.94878 | 0.97428 | 0.97905 | 0.97717 | 0.97569
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0521 | 1.0529 | 1.0528 | 1.0529 | 1.0529
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Contingency Outage | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | GA-NS-1_Garbutt-Neil Smith No 1 66 kV
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 90.53% | 95.86% | 95.7% | 95.41% | 95.32%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 162.0553 | 171.5885 | 171.2941 | 170.7883 | 170.6216
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 21.4285 | 21.6445 | 21.7027 | 21.7379 | 21.7943
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 6.4113 | 9.6668 | 9.4339 | 9.1778 | 8.9842
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.29546 | 0.44247 | 0.43056 | 0.41811 | 0.40815
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 179 | 179 | 179 | 179 | 179
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.1558 | 1.103 | 1.1078 | 1.1129 | 1.1168
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
SW | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 6.715% | 6.715% | 6.715% | 6.715% | 6.715%
SW | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 43.6505 | 43.6504 | 43.6502 | 43.6501 | 43.65
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 10.5406 | 10.5408 | 10.5411 | 10.5412 | 10.5414
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 8.1193 | 8.1193 | 8.1193 | 8.1193 | 8.1193
SW | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.77027 | 0.77026 | 0.77024 | 0.77023 | 0.77022
SW | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 650 | 650 | 650 | 650
SW | 7235_Bulli Creek - Waggamba 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7235_Bulli Creek - Waggamba 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0562 | 1.0562 | 1.0562 | 1.0563 | 1.0563
SW | 7235_Bulli Creek - Waggamba 132 kV | Contingency Outage | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV
SW | 3196_Tara 33 kV | % of Rated A | 8.065% | 8.042% | 8.036% | 8.046% | 8.064%
SW | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1
SW | 3196_Tara 33 kV | Loading (A) | 7.5006 | 7.4791 | 7.4734 | 7.4827 | 7.4993
SW | 3196_Tara 33 kV | Loading (MVA) | 0.43065 | 0.42965 | 0.42952 | 0.43032 | 0.43143
SW | 3196_Tara 33 kV | Loading (MW) | 0.05008 | 0.029595 | 0.011007 | 0.0077355 | 0.023185
SW | 3196_Tara 33 kV | Power Factor | 0.11629 | 0.068883 | 0.025621 | 0.017954 | 0.053718
SW | 3196_Tara 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW | 3196_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3196_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0045 | 1.0051 | 1.0055 | 1.0061 | 1.0065
SW | 3196_Tara 33 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW | 3203_Miles 33 kV | % of Rated A | 2.808% | 2.531% | 3.287% | 4.118% | 4.829%
SW | 3203_Miles 33 kV | Limiting Line Name | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1
SW | 3203_Miles 33 kV | Loading (A) | 9.9689 | 8.9854 | 11.6705 | 14.6181 | 17.144
SW | 3203_Miles 33 kV | Loading (MVA) | 0.58325 | 0.52621 | 0.68357 | 0.85632 | 1.0044
SW | 3203_Miles 33 kV | Loading (MW) | 0.54029 | 0.4396 | 0.62124 | 0.80925 | 0.96602
SW | 3203_Miles 33 kV | Power Factor | 0.92634 | 0.8351 | 0.90859 | 0.94485 | 0.96162
SW | 3203_Miles 33 kV | Rating (A) | 355 | 355 | 355 | 355 | 355
SW | 3203_Miles 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3203_Miles 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0236 | 1.0246 | 1.0248 | 1.0249 | 1.025
SW | 3203_Miles 33 kV | Contingency Outage | F030C | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV
SW | F060T_Tara 33 kV | % of Rated A | 8.581% | 8.668% | 8.76% | 8.866% | 8.961%
SW | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 63522_1 | TR_LINE 63522_1 | TR_LINE 63522_1 | TR_LINE 63522_1 | TR_LINE 63522_1
SW | F060T_Tara 33 kV | Loading (A) | 7.9802 | 8.0612 | 8.1469 | 8.2454 | 8.3342
SW | F060T_Tara 33 kV | Loading (MVA) | 0.45665 | 0.46164 | 0.46685 | 0.47288 | 0.47823
SW | F060T_Tara 33 kV | Loading (MW) | 0.084439 | 0.10494 | 0.12355 | 0.14232 | 0.15781
SW | F060T_Tara 33 kV | Power Factor | 0.18344 | 0.22583 | 0.26315 | 0.29945 | 0.32845
SW | F060T_Tara 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW | F060T_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F060T_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0011 | 1.0019 | 1.0026 | 1.0034 | 1.0039
SW | F060T_Tara 33 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW | F067C_Kogan 33 kV | % of Rated A | 52.56% | 52.55% | 52.55% | 52.54% | 52.54%
SW | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1
SW | F067C_Kogan 33 kV | Loading (A) | 48.8784 | 48.8734 | 48.8678 | 48.8642 | 48.8603
SW | F067C_Kogan 33 kV | Loading (MVA) | 2.7626 | 2.7626 | 2.7625 | 2.7625 | 2.7625
SW | F067C_Kogan 33 kV | Loading (MW) | 2.7379 | 2.7379 | 2.7379 | 2.7379 | 2.7379
SW | F067C_Kogan 33 kV | Power Factor | 0.99107 | 0.99107 | 0.99107 | 0.99108 | 0.99108
SW | F067C_Kogan 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW | F067C_Kogan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F067C_Kogan 33 kV | Min Voltage at Constrained Conductor (pu) | 0.98847 | 0.98856 | 0.98866 | 0.98873 | 0.9888
SW | F067C_Kogan 33 kV | Contingency Outage | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV
SW | F069C_Brigalow 33 kV | % of Rated A | 14.44% | 14.68% | 14.86% | 15.03% | 15.19%
SW | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 28408_1
SW | F069C_Brigalow 33 kV | Loading (A) | 12.7093 | 12.9175 | 13.0759 | 13.2291 | 13.363
SW | F069C_Brigalow 33 kV | Loading (MVA) | 0.73309 | 0.74519 | 0.75442 | 0.76333 | 0.77113
SW | F069C_Brigalow 33 kV | Loading (MW) | 0.73154 | 0.74368 | 0.75295 | 0.76189 | 0.76972
SW | F069C_Brigalow 33 kV | Power Factor | 0.99787 | 0.99797 | 0.99805 | 0.99812 | 0.99818
SW | F069C_Brigalow 33 kV | Rating (A) | 88 | 88 | 88 | 88 | 88
SW | F069C_Brigalow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F069C_Brigalow 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0092 | 1.0093 | 1.0094 | 1.0095 | 1.0096
SW | F069C_Brigalow 33 kV | Contingency Outage | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV
SW | F073C_Fairymeadow 33 kV | % of Rated A | 3.891% | 3.891% | 3.89% | 3.89% | 3.89%
SW | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1
SW | F073C_Fairymeadow 33 kV | Loading (A) | 3.6186 | 3.6183 | 3.6181 | 3.6179 | 3.6177
SW | F073C_Fairymeadow 33 kV | Loading (MVA) | 0.20808 | 0.20808 | 0.20809 | 0.20809 | 0.20809
SW | F073C_Fairymeadow 33 kV | Loading (MW) | 0.20356 | 0.20355 | 0.20355 | 0.20356 | 0.20356
SW | F073C_Fairymeadow 33 kV | Power Factor | 0.97827 | 0.97825 | 0.97822 | 0.97821 | 0.97819
SW | F073C_Fairymeadow 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW | F073C_Fairymeadow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F073C_Fairymeadow 33 kV | Min Voltage at Constrained Conductor (pu) | 1.006 | 1.0061 | 1.0062 | 1.0063 | 1.0063
SW | F073C_Fairymeadow 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV
SW | F074C_Miles-Condamine 33 kV | % of Rated A | 7.311% | 7.168% | 7.006% | 6.877% | 6.874%
SW | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 22686_1 | TR_LINE 22686_1
SW | F074C_Miles-Condamine 33 kV | Loading (A) | 10.4543 | 10.2509 | 10.0184 | 6.3961 | 6.3924
SW | F074C_Miles-Condamine 33 kV | Loading (MVA) | 0.59502 | 0.58059 | 0.56766 | 0.35899 | 0.35898
SW | F074C_Miles-Condamine 33 kV | Loading (MW) | 0.59204 | 0.578 | 0.56495 | 0.3033 | 0.30329
SW | F074C_Miles-Condamine 33 kV | Power Factor | 0.995 | 0.99553 | 0.99523 | 0.84278 | 0.8428
SW | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 143 | 143 | 93 | 93
SW | F074C_Miles-Condamine 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F074C_Miles-Condamine 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99559 | 0.99073 | 0.99115 | 0.98196 | 0.98249
SW | F074C_Miles-Condamine 33 kV | Contingency Outage | F076C_Dulacca 33 kV | F030C | F217R_St George 66 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW | F075S_St George Town 33 kV | % of Rated A | 5.31% | 6.109% | 6.816% | 7.529% | 8.099%
SW | F075S_St George Town 33 kV | Limiting Line Name | TR_LINE 25573_1 | TR_LINE 25573_1 | TR_LINE 25573_1 | TR_LINE 25573_1 | TR_LINE 25573_1
SW | F075S_St George Town 33 kV | Loading (A) | 10.3552 | 11.9129 | 13.2916 | 14.6815 | 15.7921
SW | F075S_St George Town 33 kV | Loading (MVA) | 0.59241 | 0.6816 | 0.76055 | 0.84016 | 0.90379
SW | F075S_St George Town 33 kV | Loading (MW) | 0.59203 | 0.6813 | 0.76031 | 0.83997 | 0.90363
SW | F075S_St George Town 33 kV | Power Factor | 0.99933 | 0.99954 | 0.99967 | 0.99976 | 0.99981
SW | F075S_St George Town 33 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
SW | F075S_St George Town 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F075S_St George Town 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0009 | 1.001 | 1.001 | 1.0011 | 1.0012
SW | F075S_St George Town 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW | F077C_Wandoan 33 kV | % of Rated A | 7.893% | 7.404% | 7.168% | 7.162% | 7.157%
SW | F077C_Wandoan 33 kV | Limiting Line Name | TR_LINE 155280_1 | TR_LINE 155280_1 | TR_LINE 24905_1 | TR_LINE 24905_1 | TR_LINE 24905_1
SW | F077C_Wandoan 33 kV | Loading (A) | 13.654 | 12.8088 | 12.4003 | 12.3909 | 12.3823
SW | F077C_Wandoan 33 kV | Loading (MVA) | 0.77371 | 0.72642 | 0.70345 | 0.70344 | 0.70343
SW | F077C_Wandoan 33 kV | Loading (MW) | 0.7464 | 0.69722 | 0.58836 | 0.58836 | 0.58836
SW | F077C_Wandoan 33 kV | Power Factor | 0.96323 | 0.95843 | 0.83637 | 0.83637 | 0.83638
SW | F077C_Wandoan 33 kV | Rating (A) | 173 | 173 | 173 | 173 | 173
SW | F077C_Wandoan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F077C_Wandoan 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99138 | 0.9922 | 0.99249 | 0.99323 | 0.99391
SW | F077C_Wandoan 33 kV | Contingency Outage | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW | F077S_Main Camp 33 kV | % of Rated A | 29.16% | 29.16% | 29.17% | 29.18% | 29.18%
SW | F077S_Main Camp 33 kV | Limiting Line Name | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26905_1
SW | F077S_Main Camp 33 kV | Loading (A) | 80.7696 | 80.7863 | 80.8013 | 80.8158 | 80.8277
SW | F077S_Main Camp 33 kV | Loading (MVA) | 4.6167 | 4.6169 | 4.6171 | 4.6173 | 4.6174
SW | F077S_Main Camp 33 kV | Loading (MW) | 4.0929 | 4.093 | 4.093 | 4.093 | 4.0931
SW | F077S_Main Camp 33 kV | Power Factor | 0.88654 | 0.88651 | 0.88649 | 0.88646 | 0.88644
SW | F077S_Main Camp 33 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
SW | F077S_Main Camp 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F077S_Main Camp 33 kV | Min Voltage at Constrained Conductor (pu) | 0.99994 | 0.99977 | 0.99963 | 0.99948 | 0.99937
SW | F077S_Main Camp 33 kV | Contingency Outage | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV
SW | F079S_St George Meatworks 33 kV | % of Rated A | 12.25% | 12.24% | 12.24% | 12.24% | 12.24%
SW | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1
SW | F079S_St George Meatworks 33 kV | Loading (A) | 7.4695 | 7.4691 | 7.4688 | 7.4685 | 7.4683
SW | F079S_St George Meatworks 33 kV | Loading (MVA) | 0.42902 | 0.42898 | 0.42894 | 0.4289 | 0.42888
SW | F079S_St George Meatworks 33 kV | Loading (MW) | 0.21008 | 0.21007 | 0.21007 | 0.21007 | 0.21007
SW | F079S_St George Meatworks 33 kV | Power Factor | 0.48966 | 0.48971 | 0.48975 | 0.48978 | 0.48981
SW | F079S_St George Meatworks 33 kV | Rating (A) | 61 | 61 | 61 | 61 | 61
SW | F079S_St George Meatworks 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F079S_St George Meatworks 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0049 | 1.0048 | 1.0048 | 1.0047 | 1.0047
SW | F079S_St George Meatworks 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW | F083C_Chinchilla 33 kV | % of Rated A | 11.02% | 12.81% | 14.5% | 16.23% | 17.71%
SW | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 27121_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1
SW | F083C_Chinchilla 33 kV | Loading (A) | 36.8184 | 42.7719 | 48.4325 | 54.2215 | 59.1411
SW | F083C_Chinchilla 33 kV | Loading (MVA) | 2.1174 | 2.4654 | 2.7928 | 3.1277 | 3.4125
SW | F083C_Chinchilla 33 kV | Loading (MW) | 2.1124 | 2.4653 | 2.7926 | 3.1274 | 3.4121
SW | F083C_Chinchilla 33 kV | Power Factor | 0.99762 | 0.99995 | 0.99993 | 0.99991 | 0.99989
SW | F083C_Chinchilla 33 kV | Rating (A) | 334 | 334 | 334 | 334 | 334
SW | F083C_Chinchilla 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F083C_Chinchilla 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0061 | 1.0084 | 1.0087 | 1.0091 | 1.0094
SW | F083C_Chinchilla 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG
SW | F106R_Roma East 33 kV | % of Rated A | 0.4767% | 0.9402% | 2.007% | 3.109% | 3.991%
SW | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_3 | TR_LINE 116092_1 | TR_LINE 116092_1 | TR_LINE 116092_1
SW | F106R_Roma East 33 kV | Loading (A) | 1.2203 | 2.407 | 5.1369 | 7.9595 | 10.2177
SW | F106R_Roma East 33 kV | Loading (MVA) | 0.070117 | 0.13838 | 0.29549 | 0.45809 | 0.58828
SW | F106R_Roma East 33 kV | Loading (MW) | 0.06736 | 0.13838 | 0.29549 | 0.45808 | 0.58827
SW | F106R_Roma East 33 kV | Power Factor | 0.96068 | 0.99999 | 1 | 1 | 0.99999
SW | F106R_Roma East 33 kV | Rating (A) | 256 | 256 | 256 | 256 | 256
SW | F106R_Roma East 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F106R_Roma East 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0053 | 1.0059 | 1.0064 | 1.0069 | 1.0073
SW | F106R_Roma East 33 kV | Contingency Outage | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV
SW | F127R_Roma West 33 kV | % of Rated A | 2.243% | 3.543% | 4.739% | 5.98% | 6.994%
SW | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1
SW | F127R_Roma West 33 kV | Loading (A) | 2.6014 | 4.1099 | 5.4968 | 6.937 | 8.1126
SW | F127R_Roma West 33 kV | Loading (MVA) | 0.14953 | 0.23634 | 0.31622 | 0.39923 | 0.46703
SW | F127R_Roma West 33 kV | Loading (MW) | 0.14799 | 0.23541 | 0.31557 | 0.39876 | 0.46666
SW | F127R_Roma West 33 kV | Power Factor | 0.98973 | 0.99606 | 0.99791 | 0.99879 | 0.99918
SW | F127R_Roma West 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW | F127R_Roma West 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F127R_Roma West 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0056 | 1.0061 | 1.0065 | 1.0069 | 1.0072
SW | F127R_Roma West 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW | F217R_St George 66 kV | % of Rated A | 19.89% | 19.87% | 19.84% | 19.82% | 19.8%
SW | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW | F217R_St George 66 kV | Loading (A) | 88.9171 | 88.7999 | 88.6943 | 88.5967 | 88.5156
SW | F217R_St George 66 kV | Loading (MVA) | 10.3425 | 10.3322 | 10.323 | 10.3144 | 10.3073
SW | F217R_St George 66 kV | Loading (MW) | 9.5911 | 9.587 | 9.5837 | 9.5802 | 9.5776
SW | F217R_St George 66 kV | Power Factor | 0.92735 | 0.92788 | 0.92838 | 0.92882 | 0.9292
SW | F217R_St George 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447
SW | F217R_St George 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F217R_St George 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0175 | 1.0178 | 1.0181 | 1.0184 | 1.0186
SW | F217R_St George 66 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW | F7164 | % of Rated A | 48.25% | 47.9% | 47.58% | 47.25% | 46.99%
SW | F7164 | Limiting Line Name | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1
SW | F7164 | Loading (A) | 83.467 | 82.8593 | 82.31 | 81.7487 | 81.297
SW | F7164 | Loading (MVA) | 20.2701 | 20.1261 | 19.9962 | 19.8626 | 19.7555
SW | F7164 | Loading (MW) | 18.3598 | 18.1961 | 18.049 | 17.8982 | 17.7774
SW | F7164 | Power Factor | 0.90576 | 0.90411 | 0.90262 | 0.9011 | 0.89987
SW | F7164 | Rating (A) | 173 | 173 | 173 | 173 | 173
SW | F7164 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7164 | Min Voltage at Constrained Conductor (pu) | 1.056 | 1.0564 | 1.0567 | 1.0571 | 1.0573
SW | F7164 | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW | F7174 | % of Rated A | 48.27% | 47.91% | 47.6% | 47.27% | 47.01%
SW | F7174 | Limiting Line Name | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1)
SW | F7174 | Loading (A) | 83.5008 | 82.8929 | 82.3433 | 81.7817 | 81.3297
SW | F7174 | Loading (MVA) | 20.2783 | 20.1342 | 20.0043 | 19.8706 | 19.7634
SW | F7174 | Loading (MW) | 18.3683 | 18.2045 | 18.0574 | 17.9065 | 17.7856
SW | F7174 | Power Factor | 0.90581 | 0.90416 | 0.90267 | 0.90115 | 0.89992
SW | F7174 | Rating (A) | 173 | 173 | 173 | 173 | 173
SW | F7174 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7174 | Min Voltage at Constrained Conductor (pu) | 1.056 | 1.0564 | 1.0567 | 1.0571 | 1.0573
SW | F7174 | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW | F7490 | % of Rated A | 22.63% | 22.49% | 22.36% | 22.22% | 22.11%
SW | F7490 | Limiting Line Name | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b
SW | F7490 | Loading (A) | 88.4945 | 87.9272 | 87.4139 | 86.8891 | 86.4667
SW | F7490 | Loading (MVA) | 21.474 | 21.3382 | 21.2157 | 21.0896 | 20.9885
SW | F7490 | Loading (MW) | 18.5795 | 18.4128 | 18.2632 | 18.1096 | 17.9867
SW | F7490 | Power Factor | 0.86521 | 0.86291 | 0.86083 | 0.8587 | 0.85698
SW | F7490 | Rating (A) | 391 | 391 | 391 | 391 | 391
SW | F7490 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7490 | Min Voltage at Constrained Conductor (pu) | 1.0614 | 1.0614 | 1.0616 | 1.0616 | 1.0617
SW | F7490 | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW | F7491 | % of Rated A | 22.61% | 22.46% | 22.33% | 22.2% | 22.09%
SW | F7491 | Limiting Line Name | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1
SW | F7491 | Loading (A) | 88.3938 | 87.8273 | 87.3147 | 86.7905 | 86.3687
SW | F7491 | Loading (MVA) | 21.4496 | 21.3139 | 21.1916 | 21.0657 | 20.9647
SW | F7491 | Loading (MW) | 18.557 | 18.3906 | 18.241 | 18.0877 | 17.9649
SW | F7491 | Power Factor | 0.86515 | 0.86284 | 0.86077 | 0.85863 | 0.85691
SW | F7491 | Rating (A) | 391 | 391 | 391 | 391 | 391
SW | F7491 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7491 | Min Voltage at Constrained Conductor (pu) | 1.0614 | 1.0614 | 1.0616 | 1.0616 | 1.0617
SW | F7491 | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW | 3153_Cecil Plains Road 33 kV | % of Rated A | 66.27% | 66.25% | 66.22% | 66.19% | 66.17%
SW | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2
SW | 3153_Cecil Plains Road 33 kV | Loading (A) | 61.6357 | 61.6102 | 61.5889 | 61.5583 | 61.5418
SW | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 3.5878 | 3.5877 | 3.5876 | 3.5876 | 3.5875
SW | 3153_Cecil Plains Road 33 kV | Loading (MW) | 3.5694 | 3.5693 | 3.5693 | 3.5693 | 3.5692
SW | 3153_Cecil Plains Road 33 kV | Power Factor | 0.99487 | 0.99488 | 0.99489 | 0.9949 | 0.9949
SW | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW | 3153_Cecil Plains Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3153_Cecil Plains Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0183 | 1.0187 | 1.0191 | 1.0195 | 1.0198
SW | 3153_Cecil Plains Road 33 kV | Contingency Outage | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV
SW | 3154_Central Dalby 1 33 kV | % of Rated A | 7.081% | 7.798% | 8.457% | 9.104% | 9.631%
SW | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1
SW | 3154_Central Dalby 1 33 kV | Loading (A) | 32.3603 | 35.6376 | 38.6464 | 41.6046 | 44.0146
SW | 3154_Central Dalby 1 33 kV | Loading (MVA) | 1.8918 | 2.0846 | 2.2616 | 2.4363 | 2.5784
SW | 3154_Central Dalby 1 33 kV | Loading (MW) | 1.8889 | 2.0808 | 2.2569 | 2.4306 | 2.5718
SW | 3154_Central Dalby 1 33 kV | Power Factor | 0.99847 | 0.99818 | 0.99791 | 0.99765 | 0.99744
SW | 3154_Central Dalby 1 33 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
SW | 3154_Central Dalby 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3154_Central Dalby 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0228 | 1.0234 | 1.0239 | 1.0245 | 1.0249
SW | 3154_Central Dalby 1 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV
SW | 3178_Wilkie Creek 33 kV | % of Rated A | 3.663% | 3.665% | 3.666% | 3.668% | 3.669%
SW | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1
SW | 3178_Wilkie Creek 33 kV | Loading (A) | 3.8832 | 3.8848 | 3.8862 | 3.8882 | 3.8893
SW | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.22241 | 0.2226 | 0.22276 | 0.22299 | 0.22311
SW | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0082367 | 0.008238 | 0.0082391 | 0.0082407 | 0.0082416
SW | 3178_Wilkie Creek 33 kV | Power Factor | 0.037033 | 0.037008 | 0.036986 | 0.036956 | 0.036939
SW | 3178_Wilkie Creek 33 kV | Rating (A) | 106 | 106 | 106 | 106 | 106
SW | 3178_Wilkie Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3178_Wilkie Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0021 | 1.0025 | 1.0029 | 1.0034 | 1.0036
SW | 3178_Wilkie Creek 33 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW | 3900_Peranga 33 kV | % of Rated A | 5.194% | 5.719% | 6.183% | 6.657% | 7.029%
SW | 3900_Peranga 33 kV | Limiting Line Name | TR_LINE 24115_1 | TR_LINE 24115_1 | TR_LINE 24115_1 | TR_LINE 24115_1 | TR_LINE 24115_1
SW | 3900_Peranga 33 kV | Loading (A) | 6.5964 | 7.2628 | 7.8522 | 8.4541 | 8.9269
SW | 3900_Peranga 33 kV | Loading (MVA) | 0.3875 | 0.42671 | 0.46138 | 0.49686 | 0.52469
SW | 3900_Peranga 33 kV | Loading (MW) | 0.38267 | 0.42259 | 0.45783 | 0.49383 | 0.52204
SW | 3900_Peranga 33 kV | Power Factor | 0.98612 | 0.9888 | 0.99061 | 0.99208 | 0.99304
SW | 3900_Peranga 33 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW | 3900_Peranga 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3900_Peranga 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0278 | 1.0279 | 1.028 | 1.0282 | 1.0283
SW | 3900_Peranga 33 kV | Contingency Outage | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV
SW | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 11.82% | 11.85% | 13.34% | 11.83% | 12.89%
SW | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 103.7962 | 104.0176 | 117.1252 | 103.8275 | 113.173
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 20.7849 | 20.8252 | 23.4544 | 20.7839 | 22.654
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 20.6139 | 20.6883 | 23.3726 | 20.5782 | 22.5016
SW | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.99086 | 0.99251 | 0.99594 | 0.98918 | 0.99241
SW | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 878 | 878 | 878 | 878
SW | 7233_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7233_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 1.051 | 1.0508 | 1.0506 | 1.0507 | 1.0505
SW | 7233_Middle Ridge-Torrington 110 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 11.82% | 11.85% | 13.34% | 11.83% | 12.89%
SW | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 103.8097 | 104.0295 | 117.1354 | 103.8425 | 113.1876
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 20.7877 | 20.8277 | 23.4565 | 20.7871 | 22.6569
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 20.6131 | 20.6875 | 23.3717 | 20.5774 | 22.5007
SW | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.99068 | 0.99235 | 0.9958 | 0.989 | 0.99224
SW | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 878 | 878 | 878 | 878
SW | 7234_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7234_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 1.051 | 1.0508 | 1.0506 | 1.0507 | 1.0505
SW | 7234_Middle Ridge-Torrington 110 kV | Contingency Outage | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV
SW | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 18.14% | 18.64% | 19.16% | 19.74% | 20.01%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 186.666 | 191.8548 | 197.1961 | 203.0927 | 205.8539
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 37.3763 | 38.4107 | 39.4743 | 40.6602 | 41.2077
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 17.4167 | 19.9159 | 22.2354 | 24.5632 | 25.6353
SW | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.46574 | 0.51831 | 0.56315 | 0.60402 | 0.62204
SW | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1029 | 1029 | 1029 | 1029
SW | 728_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 728_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0509 | 1.0506 | 1.0504 | 1.0504 | 1.0503
SW | 728_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 18.14% | 18.65% | 19.17% | 19.74% | 20.01%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 186.6816 | 191.8716 | 197.2138 | 203.1111 | 205.8731
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 37.3794 | 38.4141 | 39.4779 | 40.664 | 41.2117
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 17.4164 | 19.9156 | 22.235 | 24.5628 | 25.6349
SW | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.4657 | 0.51825 | 0.56309 | 0.60396 | 0.62197
SW | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1029 | 1029 | 1029 | 1029
SW | 730_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 730_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0509 | 1.0506 | 1.0504 | 1.0504 | 1.0503
SW | 730_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW | 7314_Dalby East 110 kV | % of Rated A | 4.568% | 4.569% | 4.57% | 4.571% | 4.572%
SW | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW | 7314_Dalby East 110 kV | Loading (A) | 12.6533 | 12.6558 | 12.6581 | 12.663 | 12.6656
SW | 7314_Dalby East 110 kV | Loading (MVA) | 2.5435 | 2.545 | 2.5463 | 2.5485 | 2.5497
SW | 7314_Dalby East 110 kV | Loading (MW) | 0.15936 | 0.13887 | 0.12029 | 0.10156 | 0.086121
SW | 7314_Dalby East 110 kV | Power Factor | 0.062654 | 0.054567 | 0.04724 | 0.039852 | 0.033777
SW | 7314_Dalby East 110 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
SW | 7314_Dalby East 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7314_Dalby East 110 kV | Min Voltage at Constrained Conductor (pu) | 1.055 | 1.0555 | 1.0558 | 1.0563 | 1.0566
SW | 7314_Dalby East 110 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 18.74% | 19.2% | 19.64% | 20.08% | 20.45%
SW | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1
SW | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 44.784 | 45.8963 | 46.93 | 47.993 | 48.8697
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 9.5401 | 9.7937 | 10.0289 | 10.2735 | 10.4732
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 4.609 | 5.0992 | 5.5309 | 5.953 | 6.2908
SW | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.48309 | 0.52063 | 0.55146 | 0.57942 | 0.60062
SW | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 239 | 239 | 239 | 239 | 239
SW | 790_Warwick-Stanthorpe 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 790_Warwick-Stanthorpe 110 kV | Min Voltage at Constrained Conductor (pu) | 1.1181 | 1.12 | 1.1216 | 1.1235 | 1.1248
SW | 790_Warwick-Stanthorpe 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | EB10_Acland 33 kV | % of Rated A | 4.844% | 4.845% | 4.845% | 4.845% | 4.846%
SW | EB10_Acland 33 kV | Limiting Line Name | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1
SW | EB10_Acland 33 kV | Loading (A) | 10.8029 | 10.8039 | 10.8052 | 10.8047 | 10.8056
SW | EB10_Acland 33 kV | Loading (MVA) | 0.62972 | 0.62973 | 0.62974 | 0.62974 | 0.62975
SW | EB10_Acland 33 kV | Loading (MW) | 0.52127 | 0.52127 | 0.52128 | 0.52128 | 0.52128
SW | EB10_Acland 33 kV | Power Factor | 0.82771 | 0.82771 | 0.8277 | 0.8277 | 0.82769
SW | EB10_Acland 33 kV | Rating (A) | 223 | 223 | 223 | 223 | 223
SW | EB10_Acland 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | EB10_Acland 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0198 | 1.0198 | 1.0197 | 1.0197 | 1.0196
SW | EB10_Acland 33 kV | Contingency Outage | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV
SW | F008D_Central Dalby 2 33 kV | % of Rated A | 6.434% | 7.086% | 7.684% | 8.272% | 8.751%
SW | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1
SW | F008D_Central Dalby 2 33 kV | Loading (A) | 34.2958 | 37.7672 | 40.9543 | 44.088 | 46.6411
SW | F008D_Central Dalby 2 33 kV | Loading (MVA) | 2.0038 | 2.2081 | 2.3958 | 2.5809 | 2.7315
SW | F008D_Central Dalby 2 33 kV | Loading (MW) | 2.0016 | 2.2062 | 2.3941 | 2.5795 | 2.7303
SW | F008D_Central Dalby 2 33 kV | Power Factor | 0.99854 | 0.99887 | 0.99911 | 0.99931 | 0.99945
SW | F008D_Central Dalby 2 33 kV | Rating (A) | 533 | 533 | 533 | 533 | 533
SW | F008D_Central Dalby 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F008D_Central Dalby 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0211 | 1.0216 | 1.0219 | 1.0224 | 1.0227
SW | F008D_Central Dalby 2 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV
SW | F019D_West Dalby No 1 33 kV | % of Rated A | 12.58% | 11.18% | 9.922% | 8.843% | 9.523%
SW | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 81367_1 | TR_LINE 81367_1
SW | F019D_West Dalby No 1 33 kV | Loading (A) | 47.1729 | 41.9376 | 37.209 | 33.1627 | 35.711
SW | F019D_West Dalby No 1 33 kV | Loading (MVA) | 2.75 | 2.446 | 2.171 | 1.9447 | 2.0947
SW | F019D_West Dalby No 1 33 kV | Loading (MW) | 2.7395 | 2.434 | 2.157 | 1.9445 | 2.0946
SW | F019D_West Dalby No 1 33 kV | Power Factor | 0.99611 | 0.99499 | 0.99337 | 0.99991 | 0.99996
SW | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 375 | 375 | 375 | 375
SW | F019D_West Dalby No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F019D_West Dalby No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0193 | 1.0199 | 1.0204 | 1.0259 | 1.0262
SW | F019D_West Dalby No 1 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW | F039D_West Dalby No 2 33 kV | % of Rated A | 15.33% | 14.99% | 15% | 15.04% | 15.1%
SW | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2
SW | F039D_West Dalby No 2 33 kV | Loading (A) | 51.3635 | 50.2004 | 50.237 | 50.3967 | 50.6017
SW | F039D_West Dalby No 2 33 kV | Loading (MVA) | 2.9962 | 2.9301 | 2.9362 | 2.9478 | 2.9613
SW | F039D_West Dalby No 2 33 kV | Loading (MW) | 2.9948 | 2.9287 | 2.9351 | 2.9467 | 2.9602
SW | F039D_West Dalby No 2 33 kV | Power Factor | 0.99952 | 0.99951 | 0.99962 | 0.99962 | 0.99962
SW | F039D_West Dalby No 2 33 kV | Rating (A) | 335 | 335 | 335 | 335 | 335
SW | F039D_West Dalby No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F039D_West Dalby No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0201 | 1.0207 | 1.0221 | 1.0229 | 1.0234
SW | F039D_West Dalby No 2 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV
SW | F095D_Kaimkillenbun 33 kV | % of Rated A | 6.09% | 6.686% | 7.241% | 7.784% | 8.234%
SW | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_LINE 23047_1 | TR_LINE 23047_1 | TR_LINE 23047_1 | TR_LINE 23047_1 | TR_LINE 23047_1
SW | F095D_Kaimkillenbun 33 kV | Loading (A) | 5.6639 | 6.2179 | 6.7345 | 7.2393 | 7.6576
SW | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 0.33124 | 0.36402 | 0.39464 | 0.42468 | 0.44956
SW | F095D_Kaimkillenbun 33 kV | Loading (MW) | 0.33117 | 0.36393 | 0.39451 | 0.42452 | 0.44937
SW | F095D_Kaimkillenbun 33 kV | Power Factor | 0.99979 | 0.99975 | 0.99968 | 0.99963 | 0.99958
SW | F095D_Kaimkillenbun 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW | F095D_Kaimkillenbun 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F095D_Kaimkillenbun 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0232 | 1.0243 | 1.0252 | 1.0263 | 1.0271
SW | F095D_Kaimkillenbun 33 kV | Contingency Outage | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV | 7314_Dalby East 110 kV
SW | F097D_Jandowae 33 kV | % of Rated A | 6.948% | 7.516% | 8.254% | 9.099% | 9.796%
SW | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 84666_1 | TR_LINE 84666_1 | TR_LINE 76815_4 | TR_LINE 76815_4 | TR_LINE 76815_4
SW | F097D_Jandowae 33 kV | Loading (A) | 9.9353 | 10.7475 | 11.8038 | 13.011 | 14.0084
SW | F097D_Jandowae 33 kV | Loading (MVA) | 0.57952 | 0.62757 | 0.68784 | 0.75884 | 0.81745
SW | F097D_Jandowae 33 kV | Loading (MW) | 0.54598 | 0.59707 | 0.65844 | 0.73275 | 0.7937
SW | F097D_Jandowae 33 kV | Power Factor | 0.94211 | 0.9514 | 0.95724 | 0.9656 | 0.97093
SW | F097D_Jandowae 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW | F097D_Jandowae 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F097D_Jandowae 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0205 | 1.0216 | 1.0195 | 1.0204 | 1.0209
SW | F097D_Jandowae 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV
SW | F099D_Warra 33 kV | % of Rated A | 39.44% | 39.32% | 39.22% | 39.1% | 39.01%
SW | F099D_Warra 33 kV | Limiting Line Name | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1
SW | F099D_Warra 33 kV | Loading (A) | 65.0736 | 64.8739 | 64.7051 | 64.5077 | 64.3604
SW | F099D_Warra 33 kV | Loading (MVA) | 3.782 | 3.7732 | 3.7658 | 3.7572 | 3.7505
SW | F099D_Warra 33 kV | Loading (MW) | 3.7712 | 3.7625 | 3.7549 | 3.7463 | 3.7396
SW | F099D_Warra 33 kV | Power Factor | 0.99716 | 0.99715 | 0.99711 | 0.99711 | 0.9971
SW | F099D_Warra 33 kV | Rating (A) | 165 | 165 | 165 | 165 | 165
SW | F099D_Warra 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F099D_Warra 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0163 | 1.017 | 1.0177 | 1.0185 | 1.019
SW | F099D_Warra 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV
SW | F2060_Sladevale 1 33kV | % of Rated A | 7.813% | 8.039% | 8.251% | 8.465% | 8.636%
SW | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW | F2060_Sladevale 1 33kV | Loading (A) | 49.6143 | 51.05 | 52.3945 | 53.7533 | 54.8394
SW | F2060_Sladevale 1 33kV | Loading (MVA) | 3.1434 | 3.24 | 3.3302 | 3.4224 | 3.4956
SW | F2060_Sladevale 1 33kV | Loading (MW) | 1.8457 | 2.0046 | 2.1476 | 2.2871 | 2.3959
SW | F2060_Sladevale 1 33kV | Power Factor | 0.58714 | 0.6187 | 0.64488 | 0.66825 | 0.68539
SW | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635
SW | F2060_Sladevale 1 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2060_Sladevale 1 33kV | Min Voltage at Constrained Conductor (pu) | 1.1085 | 1.1104 | 1.112 | 1.1139 | 1.1152
SW | F2060_Sladevale 1 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | F2325_Broxburn 33 kV | % of Rated A | 1.551% | 2.638% | 3.586% | 4.534% | 5.278%
SW | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 60091_1
SW | F2325_Broxburn 33 kV | Loading (A) | 5.18 | 8.8121 | 11.9762 | 15.1448 | 17.6277
SW | F2325_Broxburn 33 kV | Loading (MVA) | 0.31176 | 0.53063 | 0.72142 | 0.91289 | 1.0634
SW | F2325_Broxburn 33 kV | Loading (MW) | 0.3046 | 0.52696 | 0.71932 | 0.91194 | 1.0627
SW | F2325_Broxburn 33 kV | Power Factor | 0.97668 | 0.99247 | 0.99624 | 0.9979 | 0.99861
SW | F2325_Broxburn 33 kV | Rating (A) | 334 | 334 | 334 | 334 | 334
SW | F2325_Broxburn 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2325_Broxburn 33 kV | Min Voltage at Constrained Conductor (pu) | 1.053 | 1.0535 | 1.0539 | 1.0546 | 1.0549
SW | F2325_Broxburn 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F2450_Carrington Road 33 kV | % of Rated A | 7.34% | 7.968% | 8.491% | 8.984% | 9.342%
SW | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW | F2450_Carrington Road 33 kV | Loading (A) | 24.7354 | 26.8508 | 28.6139 | 30.2767 | 31.4833
SW | F2450_Carrington Road 33 kV | Loading (MVA) | 1.454 | 1.5779 | 1.6812 | 1.7802 | 1.851
SW | F2450_Carrington Road 33 kV | Loading (MW) | 1.4538 | 1.5777 | 1.681 | 1.7799 | 1.8507
SW | F2450_Carrington Road 33 kV | Power Factor | 0.99988 | 0.99986 | 0.99985 | 0.99984 | 0.99983
SW | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337
SW | F2450_Carrington Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2450_Carrington Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0284 | 1.0281 | 1.0279 | 1.0287 | 1.0286
SW | F2450_Carrington Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW | F2460_Cecil Plains 33 kV | % of Rated A | 30.91% | 31.1% | 31.29% | 31.49% | 31.67%
SW | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW | F2460_Cecil Plains 33 kV | Loading (A) | 44.2001 | 44.4748 | 44.742 | 45.0354 | 45.2884
SW | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.8051 | 2.8235 | 2.8413 | 2.8616 | 2.8785
SW | F2460_Cecil Plains 33 kV | Loading (MW) | 1.3942 | 1.4292 | 1.4629 | 1.4987 | 1.5296
SW | F2460_Cecil Plains 33 kV | Power Factor | 0.49065 | 0.49976 | 0.50843 | 0.51723 | 0.52487
SW | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW | F2460_Cecil Plains 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2460_Cecil Plains 33 kV | Min Voltage at Constrained Conductor (pu) | 1.1103 | 1.1107 | 1.111 | 1.1117 | 1.112
SW | F2460_Cecil Plains 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F4132_Shirley Road 33 kV
SW | F2520_Clifton 33 kV | % of Rated A | 27.43% | 28.35% | 29.23% | 30.13% | 30.86%
SW | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1
SW | F2520_Clifton 33 kV | Loading (A) | 33.4604 | 34.5862 | 35.6573 | 36.7552 | 37.6539
SW | F2520_Clifton 33 kV | Loading (MVA) | 2.1332 | 2.2088 | 2.2806 | 2.3547 | 2.4051
SW | F2520_Clifton 33 kV | Loading (MW) | 1.2048 | 1.3283 | 1.4403 | 1.5505 | 1.6395
SW | F2520_Clifton 33 kV | Power Factor | 0.5647 | 0.60129 | 0.63147 | 0.65837 | 0.68161
SW | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122
SW | F2520_Clifton 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2520_Clifton 33 kV | Min Voltage at Constrained Conductor (pu) | 1.1154 | 1.1173 | 1.119 | 1.1208 | 1.1175
SW | F2520_Clifton 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F4132_Shirley Road 33 kV
SW | F2777_East Stanthorpe 33 kV | % of Rated A | 1.622% | 1.625% | 1.628% | 1.631% | 1.632%
SW | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW | F2777_East Stanthorpe 33 kV | Loading (A) | 2.4984 | 2.5028 | 2.5066 | 2.511 | 2.514
SW | F2777_East Stanthorpe 33 kV | Loading (MVA) | 0.15829 | 0.15885 | 0.15933 | 0.15989 | 0.16027
SW | F2777_East Stanthorpe 33 kV | Loading (MW) | 6.6397e-05 | 6.6632e-05 | 6.6834e-05 | 6.7069e-05 | 6.7229e-05
SW | F2777_East Stanthorpe 33 kV | Power Factor | 0.00041763 | 0.00041763 | 0.00041763 | 0.00041763 | 0.00041763
SW | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 154 | 154 | 154 | 154
SW | F2777_East Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2777_East Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.1084 | 1.1104 | 1.1121 | 1.114 | 1.1154
SW | F2777_East Stanthorpe 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | % of Rated A | 70.79% | 74.26% | 77.41% | 80.56% | 83.13%
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 195683_1 | TR_LINE 195683_1 | TR_LINE 195683_1 | TR_LINE 195683_1 | TR_LINE 195683_1
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Loading (A) | 109.0148 | 114.3556 | 119.2046 | 124.0629 | 128.0206
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Loading (MVA) | 6.6528 | 7.0052 | 7.3254 | 7.649 | 7.9117
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Loading (MW) | 4.5894 | 5.0751 | 5.5027 | 5.9209 | 6.2555
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Power Factor | 0.6898 | 0.72448 | 0.75118 | 0.77408 | 0.79067
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Rating (A) | 154 | 154 | 154 | 154 | 154
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0621 | 1.0658 | 1.0689 | 1.0722 | 1.0745
SW | F2777_East Stanthorpe 33 kV ¦ F3970_Pozieres 33 kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F2780_East Warwick No 1 33 kV | % of Rated A | 18.17% | 18.86% | 19.58% | 20.36% | 21.01%
SW | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW | F2780_East Warwick No 1 33 kV | Loading (A) | 96.2962 | 99.9464 | 103.7676 | 107.8998 | 111.3731
SW | F2780_East Warwick No 1 33 kV | Loading (MVA) | 5.896 | 6.1191 | 6.3542 | 6.6102 | 6.8238
SW | F2780_East Warwick No 1 33 kV | Loading (MW) | 2.0614 | 3.6253 | 4.0365 | 4.4534 | 4.7883
SW | F2780_East Warwick No 1 33 kV | Power Factor | 0.3496 | 0.59245 | 0.63524 | 0.67371 | 0.7017
SW | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 530 | 530 | 530 | 530
SW | F2780_East Warwick No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2780_East Warwick No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0711 | 1.071 | 1.0712 | 1.0717 | 1.0718
SW | F2780_East Warwick No 1 33 kV | Contingency Outage | F2785_East Warwick No 2 33 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F2785_East Warwick No 2 33 kV | % of Rated A | 18.16% | 18.76% | 19.48% | 20.26% | 20.91%
SW | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW | F2785_East Warwick No 2 33 kV | Loading (A) | 96.2591 | 99.4533 | 103.2556 | 107.3674 | 110.8235
SW | F2785_East Warwick No 2 33 kV | Loading (MVA) | 5.8937 | 6.089 | 6.323 | 6.5776 | 6.7903
SW | F2785_East Warwick No 2 33 kV | Loading (MW) | 2.0614 | 3.6053 | 4.0145 | 4.4293 | 4.7627
SW | F2785_East Warwick No 2 33 kV | Power Factor | 0.34974 | 0.5921 | 0.6349 | 0.67339 | 0.70139
SW | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 530 | 530 | 530 | 530
SW | F2785_East Warwick No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2785_East Warwick No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0711 | 1.071 | 1.0712 | 1.0717 | 1.0718
SW | F2785_East Warwick No 2 33 kV | Contingency Outage | F2780_East Warwick No 1 33 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F3040 Hampton Street | % of Rated A | 0.3092% | 0.3092% | 0.3091% | 0.3091% | 0.3091%
SW | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW | F3040 Hampton Street | Loading (A) | 1.5462 | 1.5459 | 1.5456 | 1.5457 | 1.5455
SW | F3040 Hampton Street | Loading (MVA) | 0.093647 | 0.093618 | 0.093582 | 0.093597 | 0.093573
SW | F3040 Hampton Street | Loading (MW) | 0.0013198 | 0.0013194 | 0.0013188 | 0.0013191 | 0.0013187
SW | F3040 Hampton Street | Power Factor | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534
SW | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500
SW | F3040 Hampton Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3040 Hampton Street | Min Voltage at Constrained Conductor (pu) | 1.0597 | 1.0595 | 1.0593 | 1.0594 | 1.0592
SW | F3040 Hampton Street | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F4132_Shirley Road 33 kV
SW | F3095_Highfields 33 kV | % of Rated A | 1.702% | 1.992% | 2.222% | 2.431% | 2.569%
SW | F3095_Highfields 33 kV | Limiting Line Name | TR_LINE 24111_1 | TR_LINE 24111_1 | TR_LINE 24111_1 | TR_LINE 24111_1 | TR_LINE 24111_1
SW | F3095_Highfields 33 kV | Loading (A) | 4.2221 | 4.9393 | 5.5104 | 6.0294 | 6.3703
SW | F3095_Highfields 33 kV | Loading (MVA) | 0.24942 | 0.29174 | 0.3254 | 0.35608 | 0.37615
SW | F3095_Highfields 33 kV | Loading (MW) | 0.24714 | 0.28997 | 0.32395 | 0.35487 | 0.37509
SW | F3095_Highfields 33 kV | Power Factor | 0.99053 | 0.99355 | 0.99512 | 0.99614 | 0.99668
SW | F3095_Highfields 33 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
SW | F3095_Highfields 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3095_Highfields 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0336 | 1.0334 | 1.0331 | 1.0332 | 1.0331
SW | F3095_Highfields 33 kV | Contingency Outage | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | % of Rated A | 71.12% | 75.54% | 79.5% | 28.54% | 29.73%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 216737_1 | TR_LINE 216737_1 | TR_LINE 216737_1 | TR_LINE 216402_1 | TR_LINE 216402_1
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (A) | 176.3831 | 187.3448 | 197.1602 | 48.2331 | 50.2508
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 10.5569 | 11.2146 | 11.8029 | 2.8887 | 3.0109
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MW) | 10.5522 | 11.2073 | 11.7927 | 2.8873 | 3.0092
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Power Factor | 0.99952 | 0.9993 | 0.99907 | 0.9995 | 0.99945
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Rating (A) | 248 | 248 | 248 | 169 | 169
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0465 | 1.0467 | 1.0467 | 1.0472 | 1.0477
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Contingency Outage | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | 7448_South Toowoomba-TWCE 110 kV | 7448_South Toowoomba-TWCE 110 kV
SW | F3255_Jennings Street 33 kV | % of Rated A | 11.68% | 13.65% | 15.57% | 17.42% | 18.88%
SW | F3255_Jennings Street 33 kV | Limiting Line Name | TR_LINE 120572_1 | TR_LINE 120572_1 | TR_LINE 120572_1 | TR_LINE 120572_1 | TR_LINE 120572_1
SW | F3255_Jennings Street 33 kV | Loading (A) | 72.0744 | 84.2414 | 96.0406 | 107.492 | 116.4903
SW | F3255_Jennings Street 33 kV | Loading (MVA) | 4.3707 | 5.1086 | 5.824 | 6.5199 | 7.0654
SW | F3255_Jennings Street 33 kV | Loading (MW) | 4.3686 | 5.1048 | 5.8179 | 6.5109 | 7.0535
SW | F3255_Jennings Street 33 kV | Power Factor | 0.99952 | 0.99925 | 0.99895 | 0.99861 | 0.99831
SW | F3255_Jennings Street 33 kV | Rating (A) | 617 | 617 | 617 | 617 | 617
SW | F3255_Jennings Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3255_Jennings Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0609 | 1.061 | 1.0609 | 1.0612 | 1.0611
SW | F3255_Jennings Street 33 kV | Contingency Outage | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV
SW | F3315_Sladevale 2 33kV | % of Rated A | 7.426% | 7.464% | 7.503% | 7.546% | 7.583%
SW | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW | F3315_Sladevale 2 33kV | Loading (A) | 47.1538 | 47.397 | 47.6426 | 47.9195 | 48.1546
SW | F3315_Sladevale 2 33kV | Loading (MVA) | 2.9878 | 3.0083 | 3.0284 | 3.0512 | 3.0697
SW | F3315_Sladevale 2 33kV | Loading (MW) | 0.42367 | 0.50166 | 0.57518 | 0.64829 | 0.70926
SW | F3315_Sladevale 2 33kV | Power Factor | 0.14059 | 0.16554 | 0.18872 | 0.21127 | 0.22985
SW | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635
SW | F3315_Sladevale 2 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3315_Sladevale 2 33kV | Min Voltage at Constrained Conductor (pu) | 1.1085 | 1.1105 | 1.1121 | 1.114 | 1.1153
SW | F3315_Sladevale 2 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | F3530_Millmerran 33 kV | % of Rated A | 1.322% | 1.608% | 2.542% | 3.677% | 4.615%
SW | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1
SW | F3530_Millmerran 33 kV | Loading (A) | 1.6794 | 2.0423 | 3.2281 | 4.6695 | 5.8616
SW | F3530_Millmerran 33 kV | Loading (MVA) | 0.098519 | 0.11988 | 0.18777 | 0.26866 | 0.33746
SW | F3530_Millmerran 33 kV | Loading (MW) | 0.028456 | 0.073862 | 0.16347 | 0.25327 | 0.32553
SW | F3530_Millmerran 33 kV | Power Factor | 0.28884 | 0.61615 | 0.87057 | 0.94271 | 0.96465
SW | F3530_Millmerran 33 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW | F3530_Millmerran 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3530_Millmerran 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0263 | 1.0269 | 1.0177 | 1.0066 | 1.0072
SW | F3530_Millmerran 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F3815 North Street No 1 33 kV | % of Rated A | 3.793% | 21.51% | 17.8% | 14.02% | 11%
SW | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 48564_1 | TR_LINE 48564_1 | TR_LINE 48564_1 | TR_LINE 48564_1 | TR_LINE 48564_1
SW | F3815 North Street No 1 33 kV | Loading (A) | 8.3832 | 47.5335 | 39.3365 | 30.9909 | 24.3029
SW | F3815 North Street No 1 33 kV | Loading (MVA) | 0.49503 | 2.7938 | 2.3137 | 1.8247 | 1.4318
SW | F3815 North Street No 1 33 kV | Loading (MW) | 0.48736 | 2.7933 | 2.3128 | 1.8232 | 1.4296
SW | F3815 North Street No 1 33 kV | Power Factor | 0.98451 | 0.99982 | 0.99959 | 0.99917 | 0.99846
SW | F3815 North Street No 1 33 kV | Rating (A) | 221 | 221 | 221 | 221 | 221
SW | F3815 North Street No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3815 North Street No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0331 | 1.028 | 1.0288 | 1.0299 | 1.0306
SW | F3815 North Street No 1 33 kV | Contingency Outage | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV
SW | F3820_Boundary Road 33 kV | % of Rated A | 2.111% | 7.121% | 5.981% | 4.835% | 3.943%
SW | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW | F3820_Boundary Road 33 kV | Loading (A) | 14.5651 | 49.1344 | 41.2701 | 33.3605 | 27.2072
SW | F3820_Boundary Road 33 kV | Loading (MVA) | 0.86061 | 2.8813 | 2.4194 | 1.9569 | 1.5957
SW | F3820_Boundary Road 33 kV | Loading (MW) | 0.50082 | 2.8059 | 2.3256 | 1.8362 | 1.4427
SW | F3820_Boundary Road 33 kV | Power Factor | 0.58194 | 0.97383 | 0.96124 | 0.93834 | 0.90414
SW | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690
SW | F3820_Boundary Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3820_Boundary Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0337 | 1.0259 | 1.0256 | 1.0262 | 1.0261
SW | F3820_Boundary Road 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW | F3830_Norwin 33 kV | % of Rated A | 9.532% | 9.95% | 10.36% | 10.81% | 11.21%
SW | F3830_Norwin 33 kV | Limiting Line Name | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1
SW | F3830_Norwin 33 kV | Loading (A) | 11.0576 | 11.5425 | 12.017 | 12.5406 | 12.9979
SW | F3830_Norwin 33 kV | Loading (MVA) | 0.6655 | 0.69501 | 0.72385 | 0.75588 | 0.78369
SW | F3830_Norwin 33 kV | Loading (MW) | 0.63289 | 0.66415 | 0.69455 | 0.72816 | 0.75727
SW | F3830_Norwin 33 kV | Power Factor | 0.94999 | 0.95454 | 0.95843 | 0.96218 | 0.96511
SW | F3830_Norwin 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW | F3830_Norwin 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3830_Norwin 33 kV | Min Voltage at Constrained Conductor (pu) | 1.053 | 1.0535 | 1.0538 | 1.0545 | 1.0549
SW | F3830_Norwin 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | % of Rated A | 23.96% | 24.02% | 24.1% | 24.21% | 24.3%
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Loading (A) | 50.5603 | 50.6848 | 50.8419 | 51.0893 | 51.2822
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Loading (MVA) | 2.9767 | 2.9827 | 2.9911 | 3.0075 | 3.0183
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Loading (MW) | 0.13987 | 0.24031 | 0.32911 | 0.42071 | 0.49326
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Power Factor | 0.046792 | 0.080372 | 0.10984 | 0.1397 | 0.16323
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor (pu) | 1.03 | 1.0296 | 1.0293 | 1.0299 | 1.0297
SW | F3830_Norwin 33 kV ¦ F3980_Purrawunda 33 kV | Contingency Outage | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV | F3830_Norwin 33 kV
SW | F3855 Omaras Road 33 kV | % of Rated A | 17.62% | 17.63% | 17.63% | 17.62% | 17.62%
SW | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW | F3855 Omaras Road 33 kV | Loading (A) | 41.0486 | 41.0671 | 41.0794 | 41.0544 | 41.0611
SW | F3855 Omaras Road 33 kV | Loading (MVA) | 2.4005 | 2.4005 | 2.4004 | 2.4005 | 2.4005
SW | F3855 Omaras Road 33 kV | Loading (MW) | 2.4004 | 2.4004 | 2.4004 | 2.4004 | 2.4004
SW | F3855 Omaras Road 33 kV | Power Factor | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997
SW | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233
SW | F3855 Omaras Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3855 Omaras Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0231 | 1.0226 | 1.0223 | 1.0229 | 1.0228
SW | F3855 Omaras Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW | F3867_Pampas 33 kV | % of Rated A | 0.6722% | 0.9686% | 1.719% | 2.568% | 3.251%
SW | F3867_Pampas 33 kV | Limiting Line Name | TR_LINE 177041_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_CABLE 106_1
SW | F3867_Pampas 33 kV | Loading (A) | 3.5625 | 2.9058 | 5.1581 | 7.7044 | 9.7526
SW | F3867_Pampas 33 kV | Loading (MVA) | 0.21921 | 0.17522 | 0.31126 | 0.46539 | 0.58948
SW | F3867_Pampas 33 kV | Loading (MW) | 0.029457 | 0.1448 | 0.29537 | 0.45565 | 0.582
SW | F3867_Pampas 33 kV | Power Factor | 0.13438 | 0.82573 | 0.94858 | 0.97881 | 0.98709
SW | F3867_Pampas 33 kV | Rating (A) | 530 | 300 | 300 | 300 | 300
SW | F3867_Pampas 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3867_Pampas 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0765 | 1.055 | 1.0557 | 1.0568 | 1.0575
SW | F3867_Pampas 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F3910_Perseverence Creek 1 33 kV | % of Rated A | 23.55% | 25.22% | 26.78% | 28.22% | 29.39%
SW | F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 216402_1 | TR_LINE 216402_1 | TR_LINE 216402_1 | TR_LINE 216402_1 | TR_LINE 216402_1
SW | F3910_Perseverence Creek 1 33 kV | Loading (A) | 39.7927 | 42.6272 | 45.2526 | 47.6976 | 49.6736
SW | F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 2.4013 | 2.5755 | 2.7372 | 2.8888 | 3.0109
SW | F3910_Perseverence Creek 1 33 kV | Loading (MW) | 2.4005 | 2.5745 | 2.736 | 2.8874 | 3.0094
SW | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.99966 | 0.99961 | 0.99957 | 0.99952 | 0.99948
SW | F3910_Perseverence Creek 1 33 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
SW | F3910_Perseverence Creek 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0553 | 1.0566 | 1.0577 | 1.059 | 1.0599
SW | F3910_Perseverence Creek 1 33 kV | Contingency Outage | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV | F3095_Highfields 33 kV
SW | F3970_Pozieres 33 kV | % of Rated A | 2.123% | 2.922% | 3.64% | 4.412% | 5.014%
SW | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 23974_1 | TR_LINE 221370_1 | TR_LINE 221370_1 | TR_LINE 221370_1 | TR_LINE 221370_1
SW | F3970_Pozieres 33 kV | Loading (A) | 3.2699 | 4.1788 | 5.205 | 6.3087 | 7.1703
SW | F3970_Pozieres 33 kV | Loading (MVA) | 0.20947 | 0.26802 | 0.334 | 0.40514 | 0.46065
SW | F3970_Pozieres 33 kV | Loading (MW) | 0.18984 | 0.2659 | 0.33234 | 0.40381 | 0.45951
SW | F3970_Pozieres 33 kV | Power Factor | 0.90632 | 0.99208 | 0.99502 | 0.99671 | 0.99752
SW | F3970_Pozieres 33 kV | Rating (A) | 154 | 143 | 143 | 143 | 143
SW | F3970_Pozieres 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor (pu) | 1.1207 | 1.1221 | 1.1227 | 1.1235 | 1.124
SW | F3970_Pozieres 33 kV | Contingency Outage | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV
SW | F3980_Purrawunda 33 kV | % of Rated A | 23.15% | 23.07% | 23.01% | 23.01% | 22.98%
SW | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | F3980_Purrawunda 33 kV | Loading (A) | 48.8483 | 48.6795 | 48.5606 | 48.5458 | 48.488
SW | F3980_Purrawunda 33 kV | Loading (MVA) | 2.8863 | 2.8744 | 2.8659 | 2.8688 | 2.8646
SW | F3980_Purrawunda 33 kV | Loading (MW) | 0.49065 | 0.42095 | 0.36205 | 0.30358 | 0.25968
SW | F3980_Purrawunda 33 kV | Power Factor | 0.16999 | 0.14645 | 0.12633 | 0.10582 | 0.090653
SW | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
SW | F3980_Purrawunda 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0337 | 1.033 | 1.0325 | 1.0339 | 1.0336
SW | F3980_Purrawunda 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW | F4005_Racecourse 33 kV | % of Rated A | 5.631% | 6.859% | 8.047% | 9.274% | 10.33%
SW | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1
SW | F4005_Racecourse 33 kV | Loading (A) | 39.7582 | 48.4236 | 56.8112 | 65.4721 | 72.9325
SW | F4005_Racecourse 33 kV | Loading (MVA) | 2.342 | 2.8516 | 3.3452 | 3.858 | 4.2976
SW | F4005_Racecourse 33 kV | Loading (MW) | 2.3419 | 2.8515 | 3.345 | 3.8577 | 4.2972
SW | F4005_Racecourse 33 kV | Power Factor | 0.99997 | 0.99996 | 0.99994 | 0.99992 | 0.9999
SW | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706
SW | F4005_Racecourse 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4005_Racecourse 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0306 | 1.0303 | 1.0302 | 1.0309 | 1.0309
SW | F4005_Racecourse 33 kV | Contingency Outage | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV
SW | F4015_Ramsay Street 33 kV | % of Rated A | 12.01% | 14.04% | 16% | 17.91% | 19.41%
SW | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_LINE 170027_1 | TR_LINE 170027_1 | TR_LINE 170027_1 | TR_LINE 170027_1 | TR_LINE 170027_1
SW | F4015_Ramsay Street 33 kV | Loading (A) | 72.0631 | 84.2253 | 96.0191 | 107.4646 | 116.458
SW | F4015_Ramsay Street 33 kV | Loading (MVA) | 4.3708 | 5.1087 | 5.8241 | 6.5201 | 7.0656
SW | F4015_Ramsay Street 33 kV | Loading (MW) | 4.3685 | 5.1048 | 5.8178 | 6.5108 | 7.0533
SW | F4015_Ramsay Street 33 kV | Power Factor | 0.99949 | 0.99921 | 0.9989 | 0.99855 | 0.99824
SW | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 600 | 600 | 600
SW | F4015_Ramsay Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4015_Ramsay Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.061 | 1.061 | 1.061 | 1.0612 | 1.0612
SW | F4015_Ramsay Street 33 kV | Contingency Outage | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV
SW | F4132_Shirley Road 33 kV | % of Rated A | 53.1% | 56.26% | 59.09% | 39.27% | 40.39%
SW | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1
SW | F4132_Shirley Road 33 kV | Loading (A) | 223.0075 | 236.2782 | 248.18 | 164.9158 | 169.6196
SW | F4132_Shirley Road 33 kV | Loading (MVA) | 13.1992 | 13.9823 | 14.6855 | 9.7422 | 10.0197
SW | F4132_Shirley Road 33 kV | Loading (MW) | 13.1916 | 13.9717 | 14.6719 | 9.7398 | 10.0168
SW | F4132_Shirley Road 33 kV | Power Factor | 0.99942 | 0.99925 | 0.99907 | 0.99975 | 0.99971
SW | F4132_Shirley Road 33 kV | Rating (A) | 420 | 420 | 420 | 420 | 420
SW | F4132_Shirley Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4132_Shirley Road 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0355 | 1.0353 | 1.0352 | 1.0335 | 1.0335
SW | F4132_Shirley Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW | F4245_Stanthorpe 33 kV | % of Rated A | 36.65% | 37.95% | 39.14% | 40.33% | 41.42%
SW | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1
SW | F4245_Stanthorpe 33 kV | Loading (A) | 107.0131 | 110.8033 | 114.277 | 117.7589 | 120.9603
SW | F4245_Stanthorpe 33 kV | Loading (MVA) | 7.3637 | 7.6444 | 7.9017 | 7.6136 | 7.8453
SW | F4245_Stanthorpe 33 kV | Loading (MW) | 4.5643 | 4.9882 | 5.3626 | 5.7218 | 6.0119
SW | F4245_Stanthorpe 33 kV | Power Factor | 0.61976 | 0.65245 | 0.67859 | 0.75145 | 0.76624
SW | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292
SW | F4245_Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4245_Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 1.2039 | 1.207 | 1.2097 | 1.1312 | 1.1347
SW | F4245_Stanthorpe 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW | F4470 Vacy Street | % of Rated A | 0.4543% | 0.4542% | 0.4541% | 0.4542% | 0.4541%
SW | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW | F4470 Vacy Street | Loading (A) | 2.2714 | 2.271 | 2.2706 | 2.2708 | 2.2705
SW | F4470 Vacy Street | Loading (MVA) | 0.13757 | 0.13753 | 0.13748 | 0.1375 | 0.13746
SW | F4470 Vacy Street | Loading (MW) | 0.0023915 | 0.0023907 | 0.0023898 | 0.0023902 | 0.0023896
SW | F4470 Vacy Street | Power Factor | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605
SW | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500
SW | F4470 Vacy Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4470 Vacy Street | Min Voltage at Constrained Conductor (pu) | 1.0597 | 1.0595 | 1.0593 | 1.0594 | 1.0592
SW | F4470 Vacy Street | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F4132_Shirley Road 33 kV
SW | F4605_West Warwick 33 kV | % of Rated A | 10.55% | 11.66% | 12.67% | 13.63% | 14.42%
SW | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW | F4605_West Warwick 33 kV | Loading (A) | 41.0514 | 45.3482 | 49.273 | 53.0132 | 56.0749
SW | F4605_West Warwick 33 kV | Loading (MVA) | 2.4904 | 2.7517 | 2.9904 | 3.2188 | 3.4052
SW | F4605_West Warwick 33 kV | Loading (MW) | 2.4897 | 2.7513 | 2.9901 | 3.2187 | 3.4051
SW | F4605_West Warwick 33 kV | Power Factor | 0.99973 | 0.99985 | 0.99992 | 0.99996 | 0.99999
SW | F4605_West Warwick 33 kV | Rating (A) | 389 | 389 | 389 | 389 | 389
SW | F4605_West Warwick 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4605_West Warwick 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0613 | 1.0616 | 1.0617 | 1.0622 | 1.0624
SW | F4605_West Warwick 33 kV | Contingency Outage | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV | F4245_Stanthorpe 33 kV
SW | F4685_Wyalla Street 33 kV | % of Rated A | 5.762% | 7.017% | 8.232% | 9.487% | 10.57%
SW | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1
SW | F4685_Wyalla Street 33 kV | Loading (A) | 39.7545 | 48.4182 | 56.8038 | 65.4624 | 72.9206
SW | F4685_Wyalla Street 33 kV | Loading (MVA) | 2.342 | 2.8516 | 3.3452 | 3.858 | 4.2976
SW | F4685_Wyalla Street 33 kV | Loading (MW) | 2.3419 | 2.8515 | 3.345 | 3.8577 | 4.2972
SW | F4685_Wyalla Street 33 kV | Power Factor | 0.99997 | 0.99996 | 0.99994 | 0.99992 | 0.9999
SW | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690
SW | F4685_Wyalla Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4685_Wyalla Street 33 kV | Min Voltage at Constrained Conductor (pu) | 1.0307 | 1.0304 | 1.0303 | 1.0311 | 1.0311
SW | F4685_Wyalla Street 33 kV | Contingency Outage | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV
SW | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 9.573% | 8.954% | 8.555% | 8.344% | 8.31%
SW | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 25.2716 | 23.6378 | 22.586 | 22.0284 | 21.938
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 5.0538 | 4.7266 | 4.5157 | 4.4044 | 4.3859
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 2.4103 | 1.6418 | 0.94144 | 0.25135 | 0.30705
SW | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.47693 | 0.34736 | 0.20848 | 0.057069 | 0.068544
SW | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 264 | 264 | 264 | 264
SW | F5540_7244 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5540_7244 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0496 | 1.0495 | 1.0494 | 1.0494 | 1.0493
SW | F5540_7244 Tangkam-Dalby 110 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV
SW | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 19.78% | 18.48% | 17.64% | 17.2% | 17.13%
SW | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 25.1175 | 23.4706 | 22.4086 | 21.8441 | 21.7514
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 5.023 | 4.6932 | 4.4803 | 4.3676 | 4.3486
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 2.4087 | 1.6406 | 0.94034 | 0.25035 | 0.30569
SW | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.47954 | 0.34956 | 0.20988 | 0.05732 | 0.06936
SW | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW | F5545_7245 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5545_7245 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0496 | 1.0495 | 1.0494 | 1.0494 | 1.0493
SW | F5545_7245 Tangkam-Dalby 110 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 22.79% | 22.93% | 23.08% | 23.27% | 23.44%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 65.4207 | 65.8137 | 66.2418 | 66.7976 | 67.2763
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 12.865 | 12.948 | 13.0366 | 13.1542 | 13.2524
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 1.4579 | 1.9425 | 2.3676 | 2.8088 | 3.1602
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.11331 | 0.15002 | 0.18161 | 0.21353 | 0.23846
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 287 | 287 | 287 | 287
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0321 | 1.0326 | 1.0329 | 1.0336 | 1.0339
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 22.81% | 22.95% | 23.1% | 23.29% | 23.46%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 65.4748 | 65.8685 | 66.2962 | 66.8515 | 67.3296
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 12.876 | 12.9592 | 13.0477 | 13.1653 | 13.2633
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 1.4567 | 1.9411 | 2.3663 | 2.8074 | 3.1588
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.11296 | 0.14974 | 0.18136 | 0.21324 | 0.23816
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 287 | 287 | 287 | 287
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0322 | 1.0326 | 1.033 | 1.0336 | 1.0339
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV
SW | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 46.21% | 47.42% | 48.59% | 49.83% | 50.87%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 118.7718 | 121.8766 | 124.8681 | 128.053 | 130.7284
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 23.8017 | 24.4194 | 25.0136 | 25.6535 | 26.1878
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 10.6886 | 12.1062 | 13.3754 | 14.6392 | 15.6552
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.44753 | 0.49418 | 0.5331 | 0.56899 | 0.59616
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 257 | 257 | 257 | 257
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0518 | 1.0516 | 1.0514 | 1.0515 | 1.0513
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 15.58% | 15.98% | 16.38% | 16.8% | 17.15%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 118.8808 | 121.9612 | 124.9529 | 128.1593 | 130.8675
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 23.9389 | 24.5555 | 25.1532 | 25.8012 | 26.3429
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 11.1924 | 12.6393 | 13.9373 | 15.2323 | 16.2752
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.46725 | 0.51443 | 0.55379 | 0.59006 | 0.6175
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 763 | 763 | 763 | 763
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 1.0569 | 1.0568 | 1.0566 | 1.0567 | 1.0565
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV
WB | 6112_Agnes Water 66 kV | % of Rated A | 6.417% | 7.077% | 7.733% | 8.39% | 8.943%
WB | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
WB | 6112_Agnes Water 66 kV | Loading (A) | 18.2253 | 20.0992 | 21.9621 | 23.8274 | 25.3977
WB | 6112_Agnes Water 66 kV | Loading (MVA) | 2.1028 | 2.3135 | 2.5287 | 2.7438 | 2.9249
WB | 6112_Agnes Water 66 kV | Loading (MW) | 1.8067 | 2.0473 | 2.2841 | 2.5169 | 2.7104
WB | 6112_Agnes Water 66 kV | Power Factor | 0.8592 | 0.88496 | 0.90329 | 0.9173 | 0.92666
WB | 6112_Agnes Water 66 kV | Rating (A) | 284 | 284 | 284 | 284 | 284
WB | 6112_Agnes Water 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6112_Agnes Water 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0093 | 1.0069 | 1.0072 | 1.0073 | 1.0074
WB | 6112_Agnes Water 66 kV | Contingency Outage | 6316_ISCI - Childers 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 4.104% | 4.098% | 4.093% | 4.088% | 4.083%
WB | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 15.5135 | 15.4922 | 15.4729 | 15.4526 | 15.435
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 3.7226 | 3.7174 | 3.7133 | 3.7083 | 3.704
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 1.8567 | 1.8464 | 1.8363 | 1.8265 | 1.8179
WB | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.49878 | 0.49668 | 0.49453 | 0.49254 | 0.49081
WB | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
WB | 7188_Gin Gin - Korenan QR 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7188_Gin Gin - Korenan QR 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0495 | 1.0495 | 1.0497 | 1.0496 | 1.0496
WB | 7188_Gin Gin - Korenan QR 132 kV | Contingency Outage | 6112_Agnes Water 66 kV | 6112_Agnes Water 66 kV | 6112_Agnes Water 66 kV | 6112_Agnes Water 66 kV | 6112_Agnes Water 66 kV
WB | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 53.23% | 56.59% | 59.54% | 62.27% | 64.33%
WB | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 211.3296 | 224.6792 | 236.3709 | 247.2121 | 255.39
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 24.5459 | 26.1082 | 27.4914 | 28.7639 | 29.7216
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 22.5528 | 24.2944 | 25.8146 | 27.2057 | 28.2467
WB | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.9188 | 0.93053 | 0.93901 | 0.94583 | 0.95038
WB | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 397 | 397 | 397 | 397
WB | 6205_East Bundaberg-BUCE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6205_East Bundaberg-BUCE 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0157 | 1.0162 | 1.0171 | 1.0175 | 1.0177
WB | 6205_East Bundaberg-BUCE 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 64.06% | 67.34% | 70.33% | 73.25% | 75.54%
WB | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 254.331 | 267.3362 | 279.2252 | 290.7916 | 299.8752
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 29.4949 | 31.0187 | 32.4283 | 33.7864 | 34.8497
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 22.1999 | 24.2836 | 26.1279 | 27.8712 | 29.2107
WB | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.75267 | 0.78287 | 0.80571 | 0.82492 | 0.83819
WB | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 397 | 397 | 397 | 397
WB | 6302_Bundaberg Central - WEBU 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6302_Bundaberg Central - WEBU 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0062 | 1.0063 | 1.0069 | 1.007 | 1.007
WB | 6302_Bundaberg Central - WEBU 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB | 6366_Gootchie 66 kV | % of Rated A | 16.03% | 17.47% | 18.88% | 20.19% | 21.24%
WB | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 50338_1 | TR_LINE 50338_1 | TR_LINE 50338_1 | TR_LINE 50338_1 | TR_LINE 50338_1
WB | 6366_Gootchie 66 kV | Loading (A) | 21.1647 | 23.0657 | 24.9152 | 26.6456 | 28.0326
WB | 6366_Gootchie 66 kV | Loading (MVA) | 3.1562 | 3.441 | 3.7182 | 3.9776 | 4.1855
WB | 6366_Gootchie 66 kV | Loading (MW) | 2.9469 | 3.2531 | 3.5481 | 3.8219 | 4.0402
WB | 6366_Gootchie 66 kV | Power Factor | 0.93367 | 0.94538 | 0.95423 | 0.96084 | 0.96525
WB | 6366_Gootchie 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | 6366_Gootchie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6366_Gootchie 66 kV | Min Voltage at Constrained Conductor (pu) | 1.3045 | 1.305 | 1.3054 | 1.3058 | 1.3061
WB | 6366_Gootchie 66 kV | Contingency Outage | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 30.2% | 29.23% | 28.38% | 27.36% | 26.61%
WB | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 205.0897 | 198.4449 | 192.705 | 185.7466 | 180.6527
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 49.0814 | 47.4877 | 46.1208 | 44.4545 | 43.2347
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 29.3227 | 26.9859 | 24.4095 | 21.826 | 19.83
WB | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.59743 | 0.56827 | 0.52925 | 0.49097 | 0.45866
WB | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 679 | 679 | 679 | 679
WB | 7187_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7187_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0467 | 1.0467 | 1.0468 | 1.0468 | 1.0468
WB | 7187_Gin Gin - Bundaberg 132 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB | 7190_Woolooga-Mungar 132 kV | % of Rated A | 2.711% | 2.711% | 2.711% | 2.711% | 2.711%
WB | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2
WB | 7190_Woolooga-Mungar 132 kV | Loading (A) | 15.2922 | 15.292 | 15.2918 | 15.2916 | 15.2914
WB | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 3.6946 | 3.6944 | 3.6943 | 3.6942 | 3.6941
WB | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 1.3023 | 1.3023 | 1.3023 | 1.3023 | 1.3023
WB | 7190_Woolooga-Mungar 132 kV | Power Factor | 0.35251 | 0.35252 | 0.35253 | 0.35254 | 0.35255
WB | 7190_Woolooga-Mungar 132 kV | Rating (A) | 564 | 564 | 564 | 564 | 564
WB | 7190_Woolooga-Mungar 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7190_Woolooga-Mungar 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0567 | 1.0567 | 1.0567 | 1.0566 | 1.0566
WB | 7190_Woolooga-Mungar 132 kV | Contingency Outage | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 1.223% | 1.223% | 1.222% | 1.222% | 1.222%
WB | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 10.8351 | 10.8345 | 10.8288 | 10.8276 | 10.8269
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 2.6505 | 2.6506 | 2.6507 | 2.6507 | 2.6507
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 2.6003 | 2.6003 | 2.6003 | 2.6003 | 2.6003
WB | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.98093 | 0.98093 | 0.98088 | 0.98087 | 0.98087
WB | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 886 | 886 | 886 | 886
WB | 7204_Bundaberg - Clayton 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7204_Bundaberg - Clayton 132 kV | Min Voltage at Constrained Conductor (pu) | 1.07 | 1.07 | 1.0706 | 1.0708 | 1.0708
WB | 7204_Bundaberg - Clayton 132 kV | Contingency Outage | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV
WB | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 93.67% | 93.08% | 93.22% | 93.02% | 92.86%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 232.3086 | 230.8406 | 231.188 | 230.6818 | 230.3027
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 56.9034 | 56.5497 | 56.6656 | 56.5502 | 56.4607
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 55.0956 | 54.7869 | 54.851 | 54.7827 | 54.7241
WB | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.9656 | 0.96637 | 0.96545 | 0.96631 | 0.96687
WB | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB | 7215_Bundaberg - ISIS No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7215_Bundaberg - ISIS No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.068 | 1.068 | 1.0687 | 1.0688 | 1.0687
WB | 7215_Bundaberg - ISIS No 1 132 kV | Contingency Outage | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV
WB | 7315_Aramara 132 kV | % of Rated A | 33.2% | 34.59% | 36.03% | 37.41% | 38.49%
WB | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1
WB | 7315_Aramara 132 kV | Loading (A) | 362.5261 | 377.7686 | 393.4344 | 408.5585 | 420.298
WB | 7315_Aramara 132 kV | Loading (MVA) | 87.4724 | 91.1382 | 94.9482 | 98.5806 | 101.3987
WB | 7315_Aramara 132 kV | Loading (MW) | 86.1301 | 89.9337 | 93.6864 | 97.4582 | 100.3764
WB | 7315_Aramara 132 kV | Power Factor | 0.98465 | 0.98678 | 0.98671 | 0.98861 | 0.98992
WB | 7315_Aramara 132 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
WB | 7315_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7315_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0553 | 1.0551 | 1.0555 | 1.0553 | 1.0551
WB | 7315_Aramara 132 kV | Contingency Outage | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV
WB | 7316_Aramara 132 kV | % of Rated A | 33.2% | 34.59% | 36.03% | 37.41% | 38.49%
WB | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1
WB | 7316_Aramara 132 kV | Loading (A) | 362.5167 | 377.7588 | 393.4242 | 408.5479 | 420.2871
WB | 7316_Aramara 132 kV | Loading (MVA) | 87.47 | 91.1357 | 94.9456 | 98.5779 | 101.3958
WB | 7316_Aramara 132 kV | Loading (MW) | 86.1278 | 89.9312 | 93.6839 | 97.4555 | 100.3736
WB | 7316_Aramara 132 kV | Power Factor | 0.98466 | 0.98678 | 0.98671 | 0.98861 | 0.98992
WB | 7316_Aramara 132 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
WB | 7316_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7316_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0553 | 1.0551 | 1.0555 | 1.0553 | 1.0551
WB | 7316_Aramara 132 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 93.61% | 93.02% | 93.16% | 92.95% | 92.8%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 232.1506 | 230.6837 | 231.0312 | 230.5253 | 230.1465
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 56.8651 | 56.5116 | 56.6275 | 56.5122 | 56.4228
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 55.0587 | 54.7502 | 54.8142 | 54.746 | 54.6874
WB | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.96809 | 0.9687 | 0.96785 | 0.96862 | 0.96912
WB | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB | 7328_Bundaberg - ISIS No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7328_Bundaberg - ISIS No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0712 | 1.0713 | 1.0719 | 1.072 | 1.0721
WB | 7328_Bundaberg - ISIS No 2 132 kV | Contingency Outage | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV
WB | 7329_Maryborough 132 kV | % of Rated A | 27.76% | 30.01% | 32.65% | 34.63% | 36.19%
WB | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1
WB | 7329_Maryborough 132 kV | Loading (A) | 156.5829 | 169.2403 | 184.1225 | 195.3294 | 204.1215
WB | 7329_Maryborough 132 kV | Loading (MVA) | 38.0738 | 41.1508 | 44.8266 | 47.5673 | 49.7142
WB | 7329_Maryborough 132 kV | Loading (MW) | 33.3122 | 37.1133 | 40.5681 | 43.8306 | 46.3416
WB | 7329_Maryborough 132 kV | Power Factor | 0.87362 | 0.90058 | 0.90404 | 0.9208 | 0.93172
WB | 7329_Maryborough 132 kV | Rating (A) | 564 | 564 | 564 | 564 | 564
WB | 7329_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7329_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0635 | 1.0634 | 1.0642 | 1.064 | 1.0638
WB | 7329_Maryborough 132 kV | Contingency Outage | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV
WB | 7330_Maryborough 132 kV | % of Rated A | 27.76% | 30.01% | 32.65% | 34.63% | 36.19%
WB | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1
WB | 7330_Maryborough 132 kV | Loading (A) | 156.5815 | 169.2389 | 184.1209 | 195.3277 | 204.1198
WB | 7330_Maryborough 132 kV | Loading (MVA) | 38.074 | 41.151 | 44.8268 | 47.5674 | 49.7143
WB | 7330_Maryborough 132 kV | Loading (MW) | 33.3121 | 37.1131 | 40.5679 | 43.8305 | 46.3414
WB | 7330_Maryborough 132 kV | Power Factor | 0.87362 | 0.90057 | 0.90404 | 0.9208 | 0.93172
WB | 7330_Maryborough 132 kV | Rating (A) | 564 | 564 | 564 | 564 | 564
WB | 7330_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7330_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0635 | 1.0634 | 1.0642 | 1.064 | 1.0638
WB | 7330_Maryborough 132 kV | Contingency Outage | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV
WB | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 8.304% | 8.856% | 9.404% | 9.958% | 10.43%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 20.5951 | 21.9631 | 23.3211 | 24.6959 | 25.8659
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 4.9757 | 5.3061 | 5.6341 | 5.9661 | 6.2486
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 3.6486 | 4.1122 | 4.5511 | 4.9789 | 5.3331
WB | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.73265 | 0.77432 | 0.80704 | 0.83374 | 0.85264
WB | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB | 764_Woolooga-Kilkivan No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 764_Woolooga-Kilkivan No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0567 | 1.0567 | 1.0567 | 1.0566 | 1.0566
WB | 764_Woolooga-Kilkivan No 1 132 kV | Contingency Outage | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 8.305% | 8.856% | 9.404% | 9.958% | 10.43%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 20.5952 | 21.9632 | 23.3212 | 24.6959 | 25.8659
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 4.9757 | 5.3061 | 5.6341 | 5.9661 | 6.2486
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 3.6485 | 4.1122 | 4.5511 | 4.9789 | 5.333
WB | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.73264 | 0.77431 | 0.80703 | 0.83374 | 0.85263
WB | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB | 765_Woolooga-Kilkivan No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 765_Woolooga-Kilkivan No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0567 | 1.0567 | 1.0567 | 1.0566 | 1.0566
WB | 765_Woolooga-Kilkivan No 2 132 kV | Contingency Outage | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | 784_ISIS 132 kV | % of Rated A | 90.46% | 91.02% | 92.01% | 93.32% | 94.35%
WB | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB | 784_ISIS 132 kV | Loading (A) | 224.3433 | 225.73 | 228.1903 | 231.4384 | 233.999
WB | 784_ISIS 132 kV | Loading (MVA) | 54.9487 | 55.2947 | 55.9346 | 56.7353 | 57.3668
WB | 784_ISIS 132 kV | Loading (MW) | 54.7271 | 55.0969 | 55.7178 | 56.5369 | 57.1833
WB | 784_ISIS 132 kV | Power Factor | 0.99593 | 0.99639 | 0.99608 | 0.99645 | 0.99674
WB | 784_ISIS 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB | 784_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 784_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0701 | 1.0702 | 1.0709 | 1.0709 | 1.071
WB | 784_ISIS 132 kV | Contingency Outage | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV
WB | 785_ISIS 132 kV | % of Rated A | 90.78% | 91.35% | 92.34% | 93.66% | 94.69%
WB | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB | 785_ISIS 132 kV | Loading (A) | 225.145 | 226.5372 | 229.0064 | 232.2668 | 234.8371
WB | 785_ISIS 132 kV | Loading (MVA) | 55.1433 | 55.4906 | 56.1328 | 56.9366 | 57.5705
WB | 785_ISIS 132 kV | Loading (MW) | 54.9241 | 55.2952 | 55.9185 | 56.7407 | 57.3894
WB | 785_ISIS 132 kV | Power Factor | 0.99602 | 0.99648 | 0.99618 | 0.99656 | 0.99685
WB | 785_ISIS 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB | 785_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 785_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0712 | 1.0713 | 1.072 | 1.0721 | 1.0722
WB | 785_ISIS 132 kV | Contingency Outage | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV
WB | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 72.37% | 70.02% | 68% | 65.54% | 63.75%
WB | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 204.8066 | 198.1688 | 192.44 | 185.4923 | 180.408
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 49.0142 | 47.4222 | 46.0578 | 44.3941 | 43.1766
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 29.2076 | 26.87 | 24.2925 | 21.7082 | 19.7116
WB | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.59514 | 0.56609 | 0.52707 | 0.48884 | 0.45651
WB | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 283 | 283 | 283 | 283
WB | 786_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 786_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 1.0468 | 1.0467 | 1.0468 | 1.0468 | 1.0468
WB | 786_Gin Gin - Bundaberg 132 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 11.34% | 12.9% | 14.33% | 15.77% | 16.95%
WB | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1
WB | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 62.1612 | 70.6806 | 78.5463 | 86.4065 | 92.9021
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 7.5081 | 8.538 | 9.4928 | 10.4468 | 11.235
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 7.2591 | 8.3397 | 9.3288 | 10.3113 | 11.1198
WB | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.96586 | 0.97574 | 0.98204 | 0.98659 | 0.98944
WB | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M001_Tarong-Kingaroy East 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M001_Tarong-Kingaroy East 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0566 | 1.0566 | 1.0566 | 1.0567 | 1.0567
WB | M001_Tarong-Kingaroy East 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 11.34% | 12.9% | 14.33% | 15.77% | 16.95%
WB | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2
WB | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 62.1517 | 70.6728 | 78.5397 | 86.4011 | 92.8974
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 7.507 | 8.5433 | 9.5246 | 10.5044 | 11.3138
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 7.3029 | 8.3965 | 9.3993 | 10.3968 | 11.2187
WB | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.96602 | 0.97585 | 0.98213 | 0.98666 | 0.9895
WB | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M002_Tarong-Kingaroy West 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M002_Tarong-Kingaroy West 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0566 | 1.0566 | 1.0566 | 1.0567 | 1.0567
WB | M002_Tarong-Kingaroy West 66 kV | Contingency Outage | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV
WB | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 31.8% | 34.26% | 36.53% | 38.67% | 40.41%
WB | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7254(2) | TR_LINE 7254(2) | TR_LINE 7254(2) | TR_LINE 7254(2) | TR_LINE 7254(2)
WB | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 41.9754 | 45.2269 | 48.2161 | 51.0467 | 53.3464
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 5.1113 | 5.5146 | 5.8857 | 6.2376 | 6.5238
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 5.0997 | 5.5052 | 5.8781 | 6.2315 | 6.5187
WB | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.99578 | 0.99677 | 0.9975 | 0.99805 | 0.99842
WB | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M003_Kingaroy- Yarraman 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M003_Kingaroy- Yarraman 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0613 | 1.0618 | 1.0622 | 1.0627 | 1.063
WB | M003_Kingaroy- Yarraman 66 kV | Contingency Outage | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA
WB | M004_Murgon-Kingaroy 66 kV | % of Rated A | 6.4% | 6.47% | 6.545% | 6.628% | 6.708%
WB | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB | M004_Murgon-Kingaroy 66 kV | Loading (A) | 10.8156 | 10.9341 | 11.0604 | 11.2016 | 11.3357
WB | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 1.6112 | 1.6299 | 1.6498 | 1.6718 | 1.6927
WB | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 0.4271 | 0.48991 | 0.55029 | 0.61194 | 0.66625
WB | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.26506 | 0.30056 | 0.33355 | 0.36601 | 0.39358
WB | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
WB | M004_Murgon-Kingaroy 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M004_Murgon-Kingaroy 66 kV | Min Voltage at Constrained Conductor (pu) | 1.3032 | 1.304 | 1.3048 | 1.3056 | 1.3063
WB | M004_Murgon-Kingaroy 66 kV | Contingency Outage | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV
WB | M005 KINGAROY-BOONDOOMA | % of Rated A | 1.651% | 1.66% | 1.67% | 1.682% | 1.695%
WB | M005 KINGAROY-BOONDOOMA | Limiting Line Name | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7239_1 (FDR-M005)
WB | M005 KINGAROY-BOONDOOMA | Loading (A) | 9.0463 | 9.0945 | 9.1511 | 9.2199 | 9.2869
WB | M005 KINGAROY-BOONDOOMA | Loading (MVA) | 1.1047 | 1.1116 | 1.1194 | 1.1286 | 1.1375
WB | M005 KINGAROY-BOONDOOMA | Loading (MW) | 0.11508 | 0.15578 | 0.19484 | 0.23505 | 0.2694
WB | M005 KINGAROY-BOONDOOMA | Power Factor | 0.10417 | 0.14014 | 0.17406 | 0.20825 | 0.23683
WB | M005 KINGAROY-BOONDOOMA | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M005 KINGAROY-BOONDOOMA | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M005 KINGAROY-BOONDOOMA | Min Voltage at Constrained Conductor (pu) | 1.0683 | 1.0692 | 1.07 | 1.0708 | 1.0715
WB | M005 KINGAROY-BOONDOOMA | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB | M007_Proston 66 kV | % of Rated A | 5.716% | 5.938% | 6.171% | 6.426% | 6.662%
WB | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1
WB | M007_Proston 66 kV | Loading (A) | 5.6585 | 5.879 | 6.1095 | 6.3614 | 6.5956
WB | M007_Proston 66 kV | Loading (MVA) | 0.84316 | 0.87661 | 0.91153 | 0.94969 | 0.98517
WB | M007_Proston 66 kV | Loading (MW) | 0.42753 | 0.49035 | 0.55073 | 0.61239 | 0.66671
WB | M007_Proston 66 kV | Power Factor | 0.50703 | 0.55935 | 0.60417 | 0.64481 | 0.67672
WB | M007_Proston 66 kV | Rating (A) | 99 | 99 | 99 | 99 | 99
WB | M007_Proston 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M007_Proston 66 kV | Min Voltage at Constrained Conductor (pu) | 1.3035 | 1.3044 | 1.3051 | 1.306 | 1.3066
WB | M007_Proston 66 kV | Contingency Outage | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV
WB | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 11.06% | 12.24% | 13.49% | 14.87% | 16.11%
WB | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 20.0112 | 22.159 | 24.4174 | 26.9133 | 29.1631
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 2.9595 | 3.2769 | 3.6107 | 3.9796 | 4.312
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 1.8027 | 2.2929 | 2.7554 | 3.2308 | 3.6389
WB | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.60896 | 0.69953 | 0.76292 | 0.81162 | 0.84366
WB | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 181 | 181 | 181 | 181
WB | M008_Kilkivan-Murgon No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M008_Kilkivan-Murgon No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2937 | 1.2936 | 1.2936 | 1.2935 | 1.2934
WB | M008_Kilkivan-Murgon No 1 66 kV | Contingency Outage | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV | M009_Kilkivan-Murgon No 2 66 kV
WB | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 11.48% | 12.49% | 13.57% | 14.81% | 15.93%
WB | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 19.4 | 21.1017 | 22.9396 | 25.0208 | 26.9259
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 2.8633 | 3.1144 | 3.3855 | 3.6924 | 3.9733
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 1.5175 | 1.961 | 2.3798 | 2.8125 | 3.1847
WB | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.52645 | 0.62567 | 0.6984 | 0.75658 | 0.79589
WB | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
WB | M009_Kilkivan-Murgon No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M009_Kilkivan-Murgon No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2911 | 1.2911 | 1.291 | 1.2909 | 1.2909
WB | M009_Kilkivan-Murgon No 2 66 kV | Contingency Outage | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV | M008_Kilkivan-Murgon No 1 66 kV
WB | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 2.933% | 3.286% | 3.646% | 4.003% | 4.297%
WB | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1
WB | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 7.303 | 8.1813 | 9.0795 | 9.9684 | 10.6995
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 0.86848 | 0.95789 | 1.0655 | 1.1699 | 1.2558
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 0.59645 | 0.73905 | 0.87383 | 1.0001 | 1.1007
WB | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.68676 | 0.77153 | 0.82011 | 0.85488 | 0.87651
WB | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB | M010_Maryborough - Owanyilla 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M010_Maryborough - Owanyilla 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0403 | 1.0242 | 1.0266 | 1.0267 | 1.0267
WB | M010_Maryborough - Owanyilla 66 kV | Contingency Outage | 7329_Maryborough 132 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV
WB | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 28.92% | 31.07% | 33.12% | 35% | 36.49%
WB | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 42253_1 | TR_LINE 42253_1 | TR_LINE 42253_1 | TR_LINE 42253_1 | TR_LINE 42253_1
WB | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 38.1775 | 41.0151 | 43.7209 | 46.2056 | 48.1703
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 5.6553 | 6.0754 | 6.4758 | 6.8456 | 7.1431
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 5.5234 | 5.9643 | 6.3833 | 6.7669 | 7.0696
WB | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.97103 | 0.97566 | 0.97924 | 0.98198 | 0.98385
WB | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M011_Kilkivan-Maryborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M011_Kilkivan-Maryborough 66 kV | Min Voltage at Constrained Conductor (pu) | 1.2958 | 1.2958 | 1.2957 | 1.2956 | 1.2955
WB | M011_Kilkivan-Maryborough 66 kV | Contingency Outage | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB | M012_Maryborough-Rocky St 66 kV | % of Rated A | 14.66% | 14.7% | 15.08% | 16% | 16.76%
WB | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB | M012_Maryborough-Rocky St 66 kV | Loading (A) | 80.3536 | 80.5599 | 82.6275 | 87.6527 | 91.8496
WB | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 9.4647 | 9.4891 | 9.757 | 10.3514 | 10.8505
WB | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 0.05395 | 1.1424 | 8.3815 | 9.096 | 9.6812
WB | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.0042485 | 0.11893 | 0.85753 | 0.87728 | 0.89107
WB | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M012_Maryborough-Rocky St 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M012_Maryborough-Rocky St 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0304 | 1.0304 | 1.033 | 1.0329 | 1.0328
WB | M012_Maryborough-Rocky St 66 kV | Contingency Outage | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M017_Rocky St - Maryborough City 66 kV | M017_Rocky St - Maryborough City 66 kV | M017_Rocky St - Maryborough City 66 kV
WB | M014_Torquay-Pialba 66 kV | % of Rated A | 29.02% | 30.75% | 0% | 0% | 0%
WB | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Loading (A) | 176.4326 | 186.9313 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Loading (MVA) | 21.4184 | 22.7089 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Loading (MW) | 20.2063 | 21.5975 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Power Factor | 0.94341 | 0.95106 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 608 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Time | 12:00:00 | 12:00:00 | 0:00 | 0:00 | 0:00
WB | M014_Torquay-Pialba 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0619 | 1.0627 | 0 | 0 | 0
WB | M014_Torquay-Pialba 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | 0 | 0 | 0
WB | M014_Torquay-SOPI 66 kV | % of Rated A | 0% | 0% | 33.16% | 34.53% | 35.52%
WB | M014_Torquay-SOPI 66 kV | Limiting Line Name | 0 | 0 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB | M014_Torquay-SOPI 66 kV | Loading (A) | 0 | 0 | 201.619 | 209.9334 | 215.9597
WB | M014_Torquay-SOPI 66 kV | Loading (MVA) | 0 | 0 | 24.6793 | 25.7097 | 26.4555
WB | M014_Torquay-SOPI 66 kV | Loading (MW) | 0 | 0 | 22.8152 | 23.9481 | 24.7635
WB | M014_Torquay-SOPI 66 kV | Power Factor | 0 | 0 | 0.92447 | 0.93148 | 0.93605
WB | M014_Torquay-SOPI 66 kV | Rating (A) | 0 | 0 | 608 | 608 | 608
WB | M014_Torquay-SOPI 66 kV | Time | 0:00 | 0:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M014_Torquay-SOPI 66 kV | Min Voltage at Constrained Conductor (pu) | 0 | 0 | 1.0707 | 1.0713 | 1.0716
WB | M014_Torquay-SOPI 66 kV | Contingency Outage | 0 | 0 | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.904% | 1.905% | 1.911% | 1.911% | 1.911%
WB | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1
WB | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.5139 | 2.5145 | 2.5219 | 2.5222 | 2.5222
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 0.2989 | 0.29903 | 0.30079 | 0.30086 | 0.30087
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 0.0011425 | 0.001143 | 0.0011497 | 0.00115 | 0.00115
WB | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224 | 0.0038224
WB | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M015_Maryborough-Howard No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M015_Maryborough-Howard No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0401 | 1.0403 | 1.0434 | 1.0435 | 1.0435
WB | M015_Maryborough-Howard No 1 66 kV | Contingency Outage | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV
WB | M016_Maryborough-Howard No 2 66 kV | % of Rated A | 3.809% | 3.809% | 3.817% | 3.817% | 3.817%
WB | M016_Maryborough-Howard No 2 66 kV | Limiting Line Name | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2
WB | M016_Maryborough-Howard No 2 66 kV | Loading (A) | 5.028 | 5.028 | 5.0387 | 5.0383 | 5.038
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MVA) | 0.59253 | 0.59255 | 0.59505 | 0.59497 | 0.59489
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MW) | 0.00011463 | 0.00011463 | 0.00011511 | 0.0001151 | 0.00011508
WB | M016_Maryborough-Howard No 2 66 kV | Power Factor | 0.0001842 | 0.0001842 | 0.00018419 | 0.00018419 | 0.00018419
WB | M016_Maryborough-Howard No 2 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M016_Maryborough-Howard No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M016_Maryborough-Howard No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0309 | 1.0309 | 1.0331 | 1.033 | 1.0329
WB | M016_Maryborough-Howard No 2 66 kV | Contingency Outage | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV | M015_Maryborough-Howard No 1 66 kV
WB | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 13.17% | 14.11% | 15.02% | 15.93% | 16.69%
WB | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1
WB | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 72.1895 | 77.3281 | 82.3225 | 87.3011 | 91.4579
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 8.5623 | 9.1743 | 9.7898 | 10.3835 | 10.8792
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 6.8513 | 7.6299 | 8.3723 | 9.0856 | 9.6698
WB | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.80016 | 0.83165 | 0.85519 | 0.87499 | 0.88883
WB | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M017_Rocky St - Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M017_Rocky St - Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0376 | 1.0378 | 1.0403 | 1.0405 | 1.0406
WB | M017_Rocky St - Maryborough City 66 kV | Contingency Outage | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV
WB | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 15.24% | 15.33% | 15.64% | 16.07% | 16.52%
WB | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1
WB | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 83.5321 | 84.0266 | 85.7153 | 88.0425 | 90.5348
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 9.8438 | 9.9023 | 10.1226 | 10.3967 | 10.6903
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 0.28733 | 1.4631 | 2.5795 | 3.6612 | 4.5401
WB | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.027775 | 0.14633 | 0.25338 | 0.35066 | 0.42316
WB | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M018_Maryborough-Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M018_Maryborough-Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0309 | 1.0309 | 1.0331 | 1.033 | 1.0329
WB | M018_Maryborough-Maryborough City 66 kV | Contingency Outage | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV
WB | M019_Maryborough City-Walkers 66 kV | % of Rated A | 14.08% | 14.08% | 14.04% | 14.04% | 14.04%
WB | M019_Maryborough City-Walkers 66 kV | Limiting Line Name | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1
WB | M019_Maryborough City-Walkers 66 kV | Loading (A) | 77.1539 | 77.1372 | 76.9523 | 76.9391 | 76.9307
WB | M019_Maryborough City-Walkers 66 kV | Loading (MVA) | 9.0509 | 9.0509 | 9.0506 | 9.0506 | 9.0506
WB | M019_Maryborough City-Walkers 66 kV | Loading (MW) | 9.0392 | 9.0392 | 9.0391 | 9.0391 | 9.039
WB | M019_Maryborough City-Walkers 66 kV | Power Factor | 0.99871 | 0.99871 | 0.99872 | 0.99872 | 0.99872
WB | M019_Maryborough City-Walkers 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M019_Maryborough City-Walkers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M019_Maryborough City-Walkers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0262 | 1.0264 | 1.0288 | 1.029 | 1.0291
WB | M019_Maryborough City-Walkers 66 kV | Contingency Outage | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV | M023_6242 (Pialba-Point Vernon) 66 kV
WB | M020_Maryborough-Torquay 66 kV | % of Rated A | 50.72% | 54.09% | 57.33% | 60.09% | 62.17%
WB | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1
WB | M020_Maryborough-Torquay 66 kV | Loading (A) | 308.3716 | 328.8678 | 348.5424 | 365.3728 | 378.0071
WB | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 36.8933 | 39.3532 | 41.9362 | 43.9644 | 45.4841
WB | M020_Maryborough-Torquay 66 kV | Loading (MW) | 36.4454 | 38.9763 | 41.2377 | 43.3426 | 44.9157
WB | M020_Maryborough-Torquay 66 kV | Power Factor | 0.98786 | 0.99042 | 0.98334 | 0.98586 | 0.9875
WB | M020_Maryborough-Torquay 66 kV | Rating (A) | 608 | 608 | 608 | 608 | 608
WB | M020_Maryborough-Torquay 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M020_Maryborough-Torquay 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0465 | 1.0468 | 1.0525 | 1.0526 | 1.0525
WB | M020_Maryborough-Torquay 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | % of Rated A | 29.35% | 31.11% | 33.31% | 34.72% | 35.73%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Limiting Line Name | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (A) | 177.5877 | 188.2091 | 201.5339 | 210.0281 | 216.1823
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MVA) | 21.4497 | 22.7448 | 24.5159 | 25.56 | 26.316
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MW) | 20.2351 | 21.6298 | 22.8544 | 23.9903 | 24.8083
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Power Factor | 0.94338 | 0.95098 | 0.93223 | 0.93859 | 0.94271
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Rating (A) | 605 | 605 | 605 | 605 | 605
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 1.055 | 1.0555 | 1.0622 | 1.0626 | 1.0628
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Contingency Outage | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV
WB | M022_Howard - ISIS 66 kV | % of Rated A | 7.842% | 8.384% | 8.846% | 9.247% | 9.537%
WB | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB | M022_Howard - ISIS 66 kV | Loading (A) | 42.9738 | 45.9462 | 48.4778 | 50.6741 | 52.2625
WB | M022_Howard - ISIS 66 kV | Loading (MVA) | 5.0325 | 5.3813 | 5.6823 | 5.9405 | 6.1271
WB | M022_Howard - ISIS 66 kV | Loading (MW) | 5.0255 | 5.3731 | 5.6727 | 5.9297 | 6.1154
WB | M022_Howard - ISIS 66 kV | Power Factor | 0.99862 | 0.99846 | 0.99832 | 0.99819 | 0.99809
WB | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M022_Howard - ISIS 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M022_Howard - ISIS 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0221 | 1.0222 | 1.0228 | 1.0229 | 1.0229
WB | M022_Howard - ISIS 66 kV | Contingency Outage | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV
WB | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 19.41% | 20.33% | 21.08% | 21.79% | 22.29%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 117.4589 | 123.0121 | 127.5179 | 131.8525 | 134.869
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 14.1045 | 14.7795 | 15.3931 | 15.9218 | 16.2897
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 13.2528 | 13.9798 | 14.6211 | 15.1855 | 15.577
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.93962 | 0.94589 | 0.94985 | 0.95376 | 0.95625
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 605 | 605 | 605 | 605
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0504 | 1.051 | 1.0559 | 1.0563 | 1.0565
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Contingency Outage | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV
WB | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 21.24% | 21.45% | 21.4% | 21.75% | 22.1%
WB | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 28.0398 | 28.3098 | 28.2502 | 28.711 | 29.1745
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 3.2504 | 3.2818 | 3.29 | 3.3458 | 3.4016
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 0.38192 | 0.58675 | 0.775 | 0.97396 | 1.1448
WB | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.10968 | 0.17088 | 0.2277 | 0.28309 | 0.32837
WB | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M024_Gayndah - Mundubbera 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M024_Gayndah - Mundubbera 66 kV | Min Voltage at Constrained Conductor (pu) | 1.014 | 1.0141 | 1.0188 | 1.0194 | 1.0199
WB | M024_Gayndah - Mundubbera 66 kV | Contingency Outage | M030_Farnsfield - Childers 66 kV | M028_Childers - Gayndah 66 kV | M047_Mount Rawdon Tee 66 kV | M047_Mount Rawdon Tee 66 kV | M047_Mount Rawdon Tee 66 kV
WB | M025_Eidsvold 66 kV | % of Rated A | 2.92% | 3.179% | 3.456% | 3.771% | 4.061%
WB | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1
WB | M025_Eidsvold 66 kV | Loading (A) | 3.1242 | 3.4015 | 3.6979 | 4.0355 | 4.3457
WB | M025_Eidsvold 66 kV | Loading (MVA) | 0.36717 | 0.40017 | 0.42732 | 0.46698 | 0.50348
WB | M025_Eidsvold 66 kV | Loading (MW) | 0.20617 | 0.2606 | 0.31206 | 0.36473 | 0.41073
WB | M025_Eidsvold 66 kV | Power Factor | 0.56148 | 0.65119 | 0.73026 | 0.78101 | 0.81575
WB | M025_Eidsvold 66 kV | Rating (A) | 107 | 107 | 107 | 107 | 107
WB | M025_Eidsvold 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M025_Eidsvold 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0281 | 1.0291 | 1.0109 | 1.0123 | 1.0135
WB | M025_Eidsvold 66 kV | Contingency Outage | M047_Mount Rawdon Tee 66 kV | M047_Mount Rawdon Tee 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV
WB | M026_ISIS - Bundaberg 66 kV | % of Rated A | 16.71% | 17.58% | 18.37% | 19.07% | 19.61%
WB | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2
WB | M026_ISIS - Bundaberg 66 kV | Loading (A) | 22.0528 | 23.2081 | 24.252 | 25.1664 | 25.8809
WB | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 2.5779 | 2.713 | 2.837 | 2.9442 | 3.0279
WB | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 2.5686 | 2.7053 | 2.8308 | 2.939 | 3.0233
WB | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.99617 | 0.99692 | 0.99759 | 0.99801 | 0.9983
WB | M026_ISIS - Bundaberg 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M026_ISIS - Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M026_ISIS - Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0226 | 1.0226 | 1.0233 | 1.0233 | 1.0233
WB | M026_ISIS - Bundaberg 66 kV | Contingency Outage | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV | M024_Gayndah - Mundubbera 66 kV
WB | M026b_FORMER_ISIS - Bundaberg 66kV | % of Rated A | 0.2428% | 0.2428% | 0.243% | 0.243% | 0.243%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Limiting Line Name | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (A) | 1.0658 | 1.0659 | 1.0666 | 1.0667 | 1.0667
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MVA) | 0.12261 | 0.12264 | 0.12281 | 0.12282 | 0.12283
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MW) | 1.9238e-06 | 1.9243e-06 | 1.927e-06 | 1.9271e-06 | 1.9273e-06
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Power Factor | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Rating (A) | 439 | 439 | 439 | 439 | 439
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Min Voltage at Constrained Conductor (pu) | 1.0064 | 1.0065 | 1.0072 | 1.0072 | 1.0073
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB | M027_ISIS - Childers 66 kV | % of Rated A | 13.09% | 13.72% | 14.3% | 14.87% | 15.34%
WB | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1
WB | M027_ISIS - Childers 66 kV | Loading (A) | 33.7768 | 35.3968 | 36.8816 | 38.3737 | 39.5709
WB | M027_ISIS - Childers 66 kV | Loading (MVA) | 3.9667 | 4.1573 | 4.3348 | 4.5105 | 4.6514
WB | M027_ISIS - Childers 66 kV | Loading (MW) | 2.6663 | 2.9479 | 3.1948 | 3.4344 | 3.6214
WB | M027_ISIS - Childers 66 kV | Power Factor | 0.67108 | 0.70795 | 0.73583 | 0.76018 | 0.77729
WB | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
WB | M027_ISIS - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M027_ISIS - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0273 | 1.0274 | 1.0282 | 1.0282 | 1.0283
WB | M027_ISIS - Childers 66 kV | Contingency Outage | 6315_ISCM - ISCI 66 kV | 6315_ISCM - ISCI 66 kV | 6315_ISCM - ISCI 66 kV | 6315_ISCM - ISCI 66 kV | 6315_ISCM - ISCI 66 kV
WB | M028_GAYN TEE DEGI FDR 66kV | % of Rated A | 7.363% | 7.369% | 7.348% | 7.564% | 7.778%
WB | M028_GAYN TEE DEGI FDR 66kV | Limiting Line Name | TR_LINE 12103276_2(New M028) | TR_LINE 12103276_2(New M028) | TR_LINE 12103276_2(New M028) | TR_LINE 12103276_2(New M028) | TR_LINE 12103276_2(New M028)
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (A) | 40.3501 | 40.3798 | 40.2672 | 41.4532 | 42.622
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MVA) | 4.7261 | 4.7293 | 4.7191 | 4.8578 | 4.9945
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MW) | 1.5543 | 1.5578 | 1.5173 | 1.9193 | 2.2579
WB | M028_GAYN TEE DEGI FDR 66kV | Power Factor | 0.3239 | 0.32442 | 0.31656 | 0.38996 | 0.44676
WB | M028_GAYN TEE DEGI FDR 66kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M028_GAYN TEE DEGI FDR 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M028_GAYN TEE DEGI FDR 66kV | Min Voltage at Constrained Conductor (pu) | 1.0246 | 1.0245 | 1.0252 | 1.0251 | 1.0251
WB | M028_GAYN TEE DEGI FDR 66kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV
WB | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 0.8168% | 0.8556% | 0.9043% | 0.9546% | 0.9936%
WB | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 205843_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 4.1823 | 1.6514 | 1.7452 | 1.8424 | 1.9176
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 0.48115 | 0.18742 | 0.19816 | 0.20921 | 0.21774
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 0.1724 | 0.18522 | 0.19609 | 0.20724 | 0.21586
WB | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.35811 | 0.98823 | 0.98949 | 0.9906 | 0.99135
WB | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 512 | 193 | 193 | 193 | 193
WB | M029_Bundaberg - Farnsfield 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M029_Bundaberg - Farnsfield 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0064 | 0.9928 | 0.99327 | 0.99329 | 0.99328
WB | M029_Bundaberg - Farnsfield 66 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV
WB | M030_Farnsfield - Childers 66 kV | % of Rated A | 17.35% | 17.46% | 17.57% | 17.69% | 17.78%
WB | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB | M030_Farnsfield - Childers 66 kV | Loading (A) | 22.9017 | 23.0435 | 23.1969 | 23.3482 | 23.4759
WB | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 2.714 | 2.7314 | 2.7521 | 2.7706 | 2.7861
WB | M030_Farnsfield - Childers 66 kV | Loading (MW) | 0.6348 | 0.70206 | 0.76267 | 0.82468 | 0.87404
WB | M030_Farnsfield - Childers 66 kV | Power Factor | 0.23308 | 0.25621 | 0.27629 | 0.29682 | 0.31287
WB | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M030_Farnsfield - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M030_Farnsfield - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0367 | 1.0369 | 1.0379 | 1.038 | 1.0382
WB | M030_Farnsfield - Childers 66 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 25.46% | 26.59% | 27.68% | 28.48% | 29.4%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 33.6064 | 35.1027 | 36.5403 | 37.597 | 38.8141
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 3.8392 | 4.0106 | 4.1773 | 4.298 | 4.4373
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 2.4147 | 2.6845 | 2.9305 | 3.1687 | 3.3608
WB | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.62895 | 0.66935 | 0.70154 | 0.73726 | 0.75738
WB | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB | M032_Bundaberg-South Kolan No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M032_Bundaberg-South Kolan No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99935 | 0.99947 | 1 | 1 | 1.0001
WB | M032_Bundaberg-South Kolan No 1 66 kV | Contingency Outage | M034_Monduran Dam 66 kV | M034_Monduran Dam 66 kV | M034_Monduran Dam 66 kV | M034_Monduran Dam 66 kV | M034_Monduran Dam 66 kV
WB | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 4.883% | 5.116% | 5.315% | 5.491% | 5.62%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 26.7567 | 28.033 | 29.1282 | 30.0918 | 30.7973
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 3.0397 | 3.1849 | 3.3111 | 3.4208 | 3.5011
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 3.0382 | 3.1831 | 3.3091 | 3.4186 | 3.4987
WB | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.99948 | 0.99943 | 0.99939 | 0.99935 | 0.99932
WB | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB | M035_Bundaberg-South Kolan No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M035_Bundaberg-South Kolan No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99296 | 0.99299 | 0.99349 | 0.99352 | 0.99352
WB | M035_Bundaberg-South Kolan No 2 66 kV | Contingency Outage | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV
WB | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 58.55% | 61.46% | 64.11% | 66.69% | 68.71%
WB | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 257.0289 | 269.795 | 281.4467 | 292.7682 | 301.6291
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 30.2617 | 31.818 | 33.2531 | 34.6325 | 35.7139
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 22.3028 | 24.4088 | 26.2731 | 28.0353 | 29.3891
WB | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.737 | 0.76714 | 0.79009 | 0.80951 | 0.8229
WB | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 439 | 439 | 439 | 439
WB | M036_Bundaberg-South Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M036_Bundaberg-South Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99656 | 0.99664 | 0.99713 | 0.99707 | 0.99706
WB | M036_Bundaberg-South Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB | M037_South - East Bundaberg 66 kV | % of Rated A | 62.65% | 64.39% | 67.23% | 70.09% | 72.24%
WB | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB | M037_South - East Bundaberg 66 kV | Loading (A) | 141.5995 | 145.5308 | 151.9487 | 158.4045 | 163.2687
WB | M037_South - East Bundaberg 66 kV | Loading (MVA) | 16.8576 | 17.3562 | 17.9143 | 18.6921 | 19.277
WB | M037_South - East Bundaberg 66 kV | Loading (MW) | 7.1468 | 8.2077 | 17.1779 | 18.0049 | 18.6247
WB | M037_South - East Bundaberg 66 kV | Power Factor | 0.42182 | 0.47103 | 0.95889 | 0.96323 | 0.96616
WB | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 226 | 226 | 226 | 226
WB | M037_South - East Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M037_South - East Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0373 | 1.0387 | 1.0262 | 1.0269 | 1.0273
WB | M037_South - East Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 26.22% | 27.01% | 28.39% | 29.76% | 30.87%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 211.2984 | 217.7297 | 228.7988 | 239.8975 | 248.7943
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 24.061 | 24.794 | 26.067 | 27.332 | 28.343
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 15.7365 | 16.8131 | 18.625 | 20.3662 | 21.7181
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.65402 | 0.67811 | 0.71451 | 0.74514 | 0.76626
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99596 | 0.99598 | 0.99645 | 0.99646 | 0.99636
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Contingency Outage | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 26.04% | 26.83% | 28.19% | 29.56% | 30.65%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 209.8677 | 216.2497 | 227.2329 | 238.2455 | 247.0733
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 23.9999 | 24.7339 | 26.0083 | 27.2748 | 28.2871
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 15.6254 | 16.6964 | 18.4993 | 20.2321 | 21.5776
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.65106 | 0.67504 | 0.71128 | 0.74179 | 0.76281
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 0.99597 | 0.99599 | 0.99646 | 0.99647 | 0.99637
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Contingency Outage | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV
WB | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 21.23% | 18.48% | 19.55% | 20.53% | 21.27%
WB | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 47.9788 | 41.7659 | 44.1758 | 46.4041 | 48.0687
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 5.4866 | 4.7732 | 5.0528 | 5.3091 | 5.5008
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 4.8447 | 4.0458 | 4.3629 | 4.6503 | 4.8627
WB | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.88301 | 0.8476 | 0.86346 | 0.8759 | 0.88399
WB | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 226 | 226 | 226 | 226
WB | M041_West Bundaberg-Meadowvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M041_West Bundaberg-Meadowvale 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0002 | 0.9997 | 1.0005 | 1.0007 | 1.0009
WB | M041_West Bundaberg-Meadowvale 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 12.66% | 13.54% | 14.31% | 15.03% | 15.59%
WB | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 14.0534 | 15.034 | 15.8818 | 16.6784 | 17.3036
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 1.6071 | 1.7182 | 1.8169 | 1.9088 | 1.9811
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 1.6046 | 1.7163 | 1.8153 | 1.9074 | 1.9797
WB | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.99754 | 0.99797 | 0.99827 | 0.99852 | 0.99868
WB | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 111 | 111 | 111 | 111
WB | M042_Meadowvale-Gooburrum 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M042_Meadowvale-Gooburrum 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0004 | 0.99978 | 1.0006 | 1.0009 | 1.0011
WB | M042_Meadowvale-Gooburrum 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB | M046_Tarong-Caboonbah 66 kV | % of Rated A | 7.296% | 7.295% | 7.295% | 7.295% | 7.295%
WB | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1
WB | M046_Tarong-Caboonbah 66 kV | Loading (A) | 18.166 | 18.1653 | 18.1647 | 18.1641 | 18.1638
WB | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 2.1915 | 2.1915 | 2.1915 | 2.1915 | 2.1916
WB | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 2.0816 | 2.0816 | 2.0816 | 2.0816 | 2.0816
WB | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.94987 | 0.94986 | 0.94985 | 0.94984 | 0.94984
WB | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB | M046_Tarong-Caboonbah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M046_Tarong-Caboonbah 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0553 | 1.0553 | 1.0554 | 1.0554 | 1.0555
WB | M046_Tarong-Caboonbah 66 kV | Contingency Outage | M003_Kingaroy- Yarraman 66 kV | M003_Kingaroy- Yarraman 66 kV | M003_Kingaroy- Yarraman 66 kV | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA
WB | M049_ISIS - Gayndah 66 kV | % of Rated A | 22.38% | 21.68% | 20.9% | 20.26% | 19.73%
WB | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB | M049_ISIS - Gayndah 66 kV | Loading (A) | 89.3034 | 86.5172 | 83.4101 | 80.8483 | 78.7086
WB | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 10.448 | 10.1232 | 9.7651 | 9.4659 | 9.2155
WB | M049_ISIS - Gayndah 66 kV | Loading (MW) | 9.6773 | 9.3029 | 8.9594 | 8.6127 | 8.3206
WB | M049_ISIS - Gayndah 66 kV | Power Factor | 0.92623 | 0.91897 | 0.91749 | 0.90987 | 0.90289
WB | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
WB | M049_ISIS - Gayndah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M049_ISIS - Gayndah 66 kV | Min Voltage at Constrained Conductor (pu) | 1.0167 | 1.0178 | 1.0186 | 1.0195 | 1.0202
WB | M049_ISIS - Gayndah 66 kV | Contingency Outage | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV | M028_Childers - Gayndah 66 kV
WB | M051_Tarong Tie 66 kV | % of Rated A | 16.92% | 18.18% | 19.34% | 20.44% | 21.31%
WB | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1
WB | M051_Tarong Tie 66 kV | Loading (A) | 18.1082 | 19.4549 | 20.6986 | 21.8678 | 22.8069
WB | M051_Tarong Tie 66 kV | Loading (MVA) | 2.2212 | 2.3894 | 2.5449 | 2.6919 | 2.8116
WB | M051_Tarong Tie 66 kV | Loading (MW) | 2.2089 | 2.3807 | 2.5395 | 2.689 | 2.8092
WB | M051_Tarong Tie 66 kV | Power Factor | 0.99132 | 0.99303 | 0.9943 | 0.99529 | 0.99597
WB | M051_Tarong Tie 66 kV | Rating (A) | 107 | 107 | 107 | 107 | 107
WB | M051_Tarong Tie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M051_Tarong Tie 66 kV | Min Voltage at Constrained Conductor (pu) | 1.073 | 1.0744 | 1.0756 | 1.0767 | 1.0776
WB | M051_Tarong Tie 66 kV | Contingency Outage | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 23.01% | 24.48% | 25.74% | 26.9% | 27.79%
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 94.3298 | 100.3521 | 105.5534 | 110.2899 | 113.9253
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 10.8928 | 11.5954 | 12.2088 | 12.7633 | 13.1888
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 10.885 | 11.586 | 12.1979 | 12.7508 | 13.1751
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.99928 | 0.99919 | 0.9991 | 0.99902 | 0.99896
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 410 | 410 | 410 | 410
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Min Voltage at Constrained Conductor (pu) | 1.01 | 1.0106 | 1.0116 | 1.0121 | 1.0125
WB | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Contingency Outage | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV