## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extend that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
The Network Modeling Team makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be taken into account when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modeling Team obtain these forecast values as populated by the Strategic Forecasting Team, the accuracy of these values are as per their quality assurance processes.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The studies results contained are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using PowerFactory 2024 SP5. The reported studies were calculated in PowerFactory 2024 SP5
· For the Energex network the model is running from External Grids representing the Powerlink Network at the common coupling points.
· For the Ergon network the model is running using the current years Powerlink Transmission TAPR model connected to the Ergon Subtransmission Model at the points of connection between the two utilities.
· The Mount Isa North West Power System network is running self contained within the Ergon Subtransmission model and is supplied by the large required generators in the system
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model as required by the study (most generation is excluded due to current settings)
· The Forecasts are extracted from SIFT or Tableau depending on where the current data is stored. 10PoE and 50PoE Forecasts from SIFT the Minimum Forecasts and Ergon Energy Daily Load Profiles are from Tableau
· Python automation was used to pull demand forecasts into PowerFactory model
· Load Flow studies were run for each of the following senarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLF_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Export Packaged Master Model
2. Import and Activate Extracted Model
3. Activate Load Characterstic Application Study Case
4. Run appropraite Forecast Load script for the given study
5. Run the DAPR Feeder Association Script to identify elements required for the new Feeder Voltage Attributes
6. Run The Setup Task Automation Script to create the command required for each individual year/Time Combination
7. Run the Task Automation Command with Parallel Computing turned on to calculate multiple studies at once
7. Repeat 4-6 for other characterstic combinations (such as SEQ Night Forecasts after running SEQ Day forecasts) required in the report.
8. Run a Python Interpreter that reads the output files and produces the formatted document
This entire process is completed with the RunExternalPowerFactoryGooey custom tool to run PowerFactory in external mode to minimise failed calculations due to momentary license outages.
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.
NNC | Normal Network Configuration
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor at the constrained conductor. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## Important Info MINLF_EE_NNC
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extend that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be taken into account when making network sugmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modeling Team obtain these forecast values as populated by the Strategic Forecasting Team, the accuracy of these values are as per their quality assurance processes.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The studies results contained are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using PowerFactory 2021 SP4. The reported studies were calculated in PowerFactory 2024 SP4
· Ergon Energy network the model is running from External Grids representing the Powerlink Network at the common coupling points.
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model as required by the study (most generation is excluded due to current settings)
· Obtain 10PoE and 50PoE demand forecasts from SIFT and minimum demand forecast from Tableau
· Using Python automation to pull demand forecasts into PowerFactory model
· Run Load Flow studies for each of the following senarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLoad_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Export Packaged Master Model
2. Import and Activate Extracted Model
3. Activate Load Characterstic Application Study Case
4. Run Forecast Load script for required conditions
5. Run the DAPR Feeder Association Script to identify elements required for the new Feeder Voltage Attributes
6. Run The Setup Task Automation Script to create the command required for each individual year/Time Combination
7. Run the Task Automation Command with Parallel Computing turned on to calculate multiple studies at once
7. Repeat 5 and 6 for WD
8. Run a Python Interpreter that reads the output files and produces the formatted document
This entire process is completed with the RunExternalPowerFactoryGooey custom tool to run PowerFactory in external mode to minimise failed calculations due to momentary license outages.
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.
NNC | Normal Network Configuration
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor along the feeder at 10PoE Peak Load. Where the Power Factor is either 0 or blank, the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## 25_12_1-MinLF_EE_NNC
Region | PF Feeder Obj Name | Variable | 2026 SD | 2027 SD | 2028 SD | 2029 SD | 2030 SD
CA | 6011_Blackwater - Comet 66 kV | % of Rated A | 13.1% | 34.03% | 34.48% | 35.07% | 35.66%
CA | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1
CA | 6011_Blackwater - Comet 66 kV | Loading (A) | 3628% | 9427% | 9550% | 9715% | 9879%
CA | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 443.8% | 1157% | 1172% | 1192% | 1212%
CA | 6011_Blackwater - Comet 66 kV | Loading (MW) | 202% | 87.13% | 167% | 249.8% | 318.4%
CA | 6011_Blackwater - Comet 66 kV | Power Factor | 45.5% | 7.526% | 14.24% | 20.94% | 26.25%
CA | 6011_Blackwater - Comet 66 kV | Rating (A) | 27700% | 27700% | 27700% | 27700% | 27700%
CA | 6011_Blackwater - Comet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6011_Blackwater - Comet 66 kV | Min Voltage at Constrained Conductor (pu) | 107% | 107.3% | 107.4% | 107.4% | 107.4%
CA | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 12.7% | 12.48% | 12.27% | 12% | 11.77%
CA | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 3530% | 3469% | 3410% | 3335% | 3272%
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 431.8% | 423.7% | 416.6% | 407.3% | 399.7%
CA | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 418.2% | 409.8% | 402.4% | 392.8% | 384.8%
CA | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 96.84% | 96.73% | 96.6% | 96.43% | 96.28%
CA | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 27800% | 27800% | 27800% | 27800% | 27800%
CA | 6012_Blackwater - Bedford Weir 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6012_Blackwater - Bedford Weir 66 kV | Min Voltage at Constrained Conductor (pu) | 107% | 106.8% | 106.9% | 106.9% | 106.9%
CA | 6014_Blackwater - South Blackwater 66 kV | % of Rated A | 12.66% | 28.9% | 28.89% | 28.88% | 28.87%
CA | 6014_Blackwater - South Blackwater 66 kV | Limiting Line Name | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (A) | 6280% | 14332% | 14328% | 14324% | 14322%
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MVA) | 768.4% | 1753% | 1752% | 1752% | 1752%
CA | 6014_Blackwater - South Blackwater 66 kV | Loading (MW) | 766.4% | 1753% | 1752% | 1752% | 1751%
CA | 6014_Blackwater - South Blackwater 66 kV | Power Factor | 99.74% | 99.99% | 99.99% | 99.99% | 99.99%
CA | 6014_Blackwater - South Blackwater 66 kV | Rating (A) | 49600% | 49600% | 49600% | 49600% | 49600%
CA | 6014_Blackwater - South Blackwater 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6014_Blackwater - South Blackwater 66 kV | Min Voltage at Constrained Conductor (pu) | 107% | 107% | 107% | 107% | 107%
CA | 6056_Comet - Emerald 66 kV | % of Rated A | 10.61% | 32.54% | 32.75% | 33.12% | 33.53%
CA | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1
CA | 6056_Comet - Emerald 66 kV | Loading (A) | 2939% | 9013% | 9073% | 9174% | 9288%
CA | 6056_Comet - Emerald 66 kV | Loading (MVA) | 364.4% | 1141% | 1150% | 1165% | 1181%
CA | 6056_Comet - Emerald 66 kV | Loading (MW) | 84.33% | 12.16% | 67.56% | 149.9% | 218.5%
CA | 6056_Comet - Emerald 66 kV | Power Factor | 23.14% | 1.064% | 5.873% | 12.87% | 18.5%
CA | 6056_Comet - Emerald 66 kV | Rating (A) | 27700% | 27700% | 27700% | 27700% | 27700%
CA | 6056_Comet - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6056_Comet - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 108.5% | 110.7% | 110.9% | 111.1% | 111.2%
CA | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 9.783% | 9.768% | 9.741% | 9.712% | 9.688%
CA | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 2720% | 2716% | 2708% | 2700% | 2693%
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 331.7% | 330.7% | 329.9% | 328.9% | 328.1%
CA | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 321.2% | 320.3% | 319.3% | 318.4% | 317.5%
CA | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 96.83% | 96.83% | 96.81% | 96.79% | 96.77%
CA | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 27800% | 27800% | 27800% | 27800% | 27800%
CA | 6058_Bedford Weir - Bingegang 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6058_Bedford Weir - Bingegang 66 kV | Min Voltage at Constrained Conductor (pu) | 106.7% | 106.5% | 106.6% | 106.6% | 106.6%
CA | 6059_Leichardt - Cook Colliery 66 kV | % of Rated A | 35.29% | 81.12% | 81.09% | 81.06% | 81.04%
CA | 6059_Leichardt - Cook Colliery 66 kV | Limiting Line Name | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (A) | 5046% | 11600% | 11596% | 11592% | 11589%
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MVA) | 612.1% | 1396% | 1396% | 1395% | 1395%
CA | 6059_Leichardt - Cook Colliery 66 kV | Loading (MW) | 610.8% | 1394% | 1394% | 1393% | 1393%
CA | 6059_Leichardt - Cook Colliery 66 kV | Power Factor | 99.8% | 99.84% | 99.84% | 99.84% | 99.84%
CA | 6059_Leichardt - Cook Colliery 66 kV | Rating (A) | 14300% | 14300% | 14300% | 14300% | 14300%
CA | 6059_Leichardt - Cook Colliery 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6059_Leichardt - Cook Colliery 66 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 104.2% | 104.2% | 104.2% | 104.2%
CA | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 25.78% | 25.88% | 25.85% | 25.69% | 25.49%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 6264% | 6289% | 6281% | 6242% | 6195%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 756.6% | 753.4% | 750.6% | 746% | 742.1%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 753% | 749.9% | 747.2% | 742.5% | 738.6%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 99.52% | 99.54% | 99.54% | 99.53% | 99.52%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 24300% | 24300% | 24300% | 24300% | 24300%
CA | 6065_Lilyvale - Tieri Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6065_Lilyvale - Tieri Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 104.8% | 104.5% | 104.5% | 104.8%
CA | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 20.48% | 26.84% | 26.65% | 26.9% | 27.52%
CA | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 6982% | 9152% | 9086% | 9174% | 9383%
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 843.4% | 1107% | 1086% | 1096% | 1135%
CA | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 165.5% | 14.82% | 94.96% | 177.9% | 247.2%
CA | 6067 Lilyvale - Emerald 66 kV | Power Factor | 19.62% | 0.1271% | 7.272% | 14.74% | 20.27%
CA | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 34100% | 34100% | 34100% | 34100% | 34100%
CA | 6067 Lilyvale - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6067 Lilyvale - Emerald 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 105.8% | 104.5% | 104.5% | 105.8%
CA | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 15.71% | 4.165% | 4.226% | 4.323% | 4.427%
CA | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_CABLE 562_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38974_1 | TR_LINE 38974_1
CA | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 1571% | 1533% | 1555% | 1591% | 1629%
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 194.9% | 191.7% | 194.8% | 199.5% | 204.6%
CA | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 1.759% | 19.6% | 36.89% | 55.1% | 70.32%
CA | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.8268% | 10.23% | 18.94% | 27.62% | 34.38%
CA | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 10000% | 36800% | 36800% | 36800% | 36800%
CA | 6079_Barcaldine - Longreach 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6079_Barcaldine - Longreach 66 kV | Min Voltage at Constrained Conductor (pu) | 108.5% | 109.4% | 109.6% | 109.7% | 109.8%
CA | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 3.56% | 3.624% | 3.675% | 3.738% | 3.8%
CA | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 1374% | 1399% | 1419% | 1443% | 1467%
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 168.3% | 172.6% | 175.3% | 178.5% | 181.7%
CA | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 28.4% | 37.63% | 46.97% | 56.7% | 65.25%
CA | 6080_Barcaldine - Blackall 66 kV | Power Factor | 16.88% | 21.8% | 26.79% | 31.76% | 35.9%
CA | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 38600% | 38600% | 38600% | 38600% | 38600%
CA | 6080_Barcaldine - Blackall 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6080_Barcaldine - Blackall 66 kV | Min Voltage at Constrained Conductor (pu) | 107.1% | 108% | 108.1% | 108.3% | 108.4%
CA | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 1.333% | 1.308% | 1.282% | 1.24% | 1.203%
CA | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 323.8% | 318% | 311.5% | 301.2% | 292.3%
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 39% | 37.98% | 37.11% | 35.89% | 34.92%
CA | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 37.1% | 36.08% | 35.19% | 33.89% | 32.84%
CA | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 95.11% | 95.01% | 94.81% | 94.44% | 94.05%
CA | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 24300% | 24300% | 24300% | 24300% | 24300%
CA | 6085_Tieri Tee - Tieri 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6085_Tieri Tee - Tieri 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 104.5% | 104.2% | 104.2% | 104.5%
CA | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 24.44% | 24.57% | 24.57% | 24.45% | 24.3%
CA | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 5940% | 5971% | 5970% | 5942% | 5904%
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 715.3% | 713.1% | 711.2% | 707.9% | 705.1%
CA | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 713.2% | 711.2% | 709.3% | 706% | 703.1%
CA | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 99.72% | 99.73% | 99.73% | 99.73% | 99.72%
CA | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 24300% | 24300% | 24300% | 24300% | 24300%
CA | 6086_Tieri Tee - Middlemount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6086_Tieri Tee - Middlemount 66 kV | Min Voltage at Constrained Conductor (pu) | 104.4% | 103.5% | 103.3% | 103.3% | 103.5%
CA | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 17.61% | 17.56% | 17.46% | 17.32% | 17.25%
CA | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 12468% | 12433% | 12364% | 12264% | 12213%
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 3025% | 3017% | 3000% | 2976% | 2963%
CA | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 1290% | 1264% | 1211% | 1154% | 1111%
CA | 7153_Lilyvale - Clermont 132 kV | Power Factor | 42.64% | 41.91% | 40.35% | 38.79% | 37.51%
CA | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 70800% | 70800% | 70800% | 70800% | 70800%
CA | 7153_Lilyvale - Clermont 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7153_Lilyvale - Clermont 132 kV | Min Voltage at Constrained Conductor (pu) | 106.1% | 106.1% | 106.1% | 106.1% | 106.1%
CA | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 22.29% | 22.46% | 22.49% | 22.54% | 22.58%
CA | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 8023% | 8085% | 8098% | 8113% | 8127%
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 2028% | 2057% | 2061% | 2066% | 2070%
CA | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 49.81% | 8.525% | 35.52% | 78.52% | 115.2%
CA | 7154_Clermont - Barcaldine 132 kV | Power Factor | 2.366% | 0.2841% | 1.587% | 3.665% | 5.428%
CA | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 36000% | 36000% | 36000% | 36000% | 36000%
CA | 7154_Clermont - Barcaldine 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7154_Clermont - Barcaldine 132 kV | Min Voltage at Constrained Conductor (pu) | 110.5% | 111.3% | 111.3% | 111.4% | 111.4%
CA | 7286_Blackwater - Memooloo 132 kV | % of Rated A | 15.67% | 15.62% | 15.58% | 15.53% | 15.5%
CA | 7286_Blackwater - Memooloo 132 kV | Limiting Line Name | TR_LINE 62090_1 | TR_LINE 62090_1 | TR_LINE 62090_1 | TR_LINE 62090_1 | TR_LINE 62090_1
CA | 7286_Blackwater - Memooloo 132 kV | Loading (A) | 11048% | 11014% | 10983% | 10951% | 10924%
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MVA) | 2677% | 2669% | 2662% | 2654% | 2647%
CA | 7286_Blackwater - Memooloo 132 kV | Loading (MW) | 2624% | 2615% | 2607% | 2599% | 2592%
CA | 7286_Blackwater - Memooloo 132 kV | Power Factor | 98% | 97.97% | 97.95% | 97.93% | 97.91%
CA | 7286_Blackwater - Memooloo 132 kV | Rating (A) | 70500% | 70500% | 70500% | 70500% | 70500%
CA | 7286_Blackwater - Memooloo 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7286_Blackwater - Memooloo 132 kV | Min Voltage at Constrained Conductor (pu) | 106% | 106% | 106% | 106% | 106%
CA | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 10.22% | 10.17% | 10.12% | 10.08% | 10.04%
CA | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1
CA | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 7205% | 7170% | 7138% | 7105% | 7077%
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 1740% | 1732% | 1724% | 1716% | 1710%
CA | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 1730% | 1721% | 1714% | 1706% | 1699%
CA | 7450_Memooloo - Rolleston 132 kV | Power Factor | 99.4% | 99.39% | 99.38% | 99.38% | 99.37%
CA | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 70500% | 70500% | 70500% | 70500% | 70500%
CA | 7450_Memooloo - Rolleston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7450_Memooloo - Rolleston 132 kV | Min Voltage at Constrained Conductor (pu) | 105.4% | 105.4% | 105.4% | 105.4% | 105.4%
CA | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 4.569% | 9.327% | 9.339% | 9.369% | 9.393%
CA | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 1832% | 3740% | 3745% | 3757% | 3767%
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 218.9% | 448.2% | 448.8% | 450.3% | 451.5%
CA | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 218.8% | 443.1% | 443.8% | 445.4% | 446.8%
CA | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 99.86% | 98.65% | 98.67% | 98.7% | 98.74%
CA | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 40100% | 40100% | 40100% | 40100% | 40100%
CA | 6001_Glenmore - Parkhurst 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6001_Glenmore - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 104.5% | 104.8% | 104.8% | 104.9% | 104.9%
CA | 6003_Glenmore - Berserker 66 kV | % of Rated A | 23% | 30.95% | 32.3% | 33.76% | 35.03%
CA | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1
CA | 6003_Glenmore - Berserker 66 kV | Loading (A) | 9222% | 12412% | 12952% | 13538% | 14047%
CA | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 1103% | 1491% | 1557% | 1627% | 1689%
CA | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 244.1% | 844.6% | 968.6% | 1092% | 1193%
CA | 6003_Glenmore - Berserker 66 kV | Power Factor | 22.13% | 56.63% | 62.22% | 67.1% | 70.66%
CA | 6003_Glenmore - Berserker 66 kV | Rating (A) | 40100% | 40100% | 40100% | 40100% | 40100%
CA | 6003_Glenmore - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6003_Glenmore - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 105.1% | 105.1% | 105.1% | 105.1%
CA | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 9.095% | 15.96% | 15.91% | 15.85% | 15.82%
CA | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_CABLE 301_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_LINE 139203_1
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 3383% | 5857% | 5838% | 5817% | 5807%
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 404.7% | 703.9% | 701.9% | 699.4% | 698.3%
CA | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 117.3% | 145.4% | 133.7% | 119% | 110.6%
CA | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 28.99% | 20.66% | 19.05% | 17.01% | 15.84%
CA | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 37200% | 36700% | 36700% | 36700% | 36700%
CA | 6004_Glenmore - Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6004_Glenmore - Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 105.1% | 105.2% | 105.2% | 105.2%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 14.78% | 21.24% | 21.21% | 21.2% | 21.2%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 5897% | 8476% | 8461% | 8457% | 8459%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 705.2% | 1017% | 1015% | 1015% | 1015%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 179.7% | 23.9% | 16.68% | 56.8% | 85.96%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 25.48% | 2.325% | 1.617% | 5.569% | 8.44%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 39900% | 39900% | 39900% | 39900% | 39900%
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6005_Rockhampton Glenmore-Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 105% | 105% | 105% | 105%
CA | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 3.558% | 15.29% | 16.15% | 16.89% | 17.39%
CA | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1
CA | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 1427% | 6130% | 6478% | 6774% | 6974%
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 170.7% | 738.2% | 780.3% | 816.2% | 840.4%
CA | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 170.3% | 738.1% | 780.1% | 816% | 840.1%
CA | 6006_Glenmore - Frenchville 66 kV | Power Factor | 99.77% | 99.98% | 99.97% | 99.97% | 99.97%
CA | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 40100% | 40100% | 40100% | 40100% | 40100%
CA | 6006_Glenmore - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6006_Glenmore - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 105.3% | 105.4% | 105.4% | 105.4%
CA | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 7.824% | 23.61% | 24.17% | 24.8% | 25.37%
CA | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 1033% | 3117% | 3191% | 3274% | 3349%
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 123.7% | 374.1% | 383.1% | 393.1% | 402.2%
CA | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 3.072% | 143.4% | 164.5% | 185.9% | 204.2%
CA | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 2.483% | 38.31% | 42.93% | 47.29% | 50.76%
CA | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6007_Biloela - Coominglah Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6007_Biloela - Coominglah Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 104.8% | 105% | 105% | 105% | 105%
CA | 6008_Biloela - Wowan 66 kV | % of Rated A | 6.307% | 92.3% | 91.32% | 90.25% | 89.25%
CA | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 21790_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1
CA | 6008_Biloela - Wowan 66 kV | Loading (A) | 832.5% | 12184% | 12054% | 11913% | 11781%
CA | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 99.7% | 1370% | 1357% | 1342% | 1328%
CA | 6008_Biloela - Wowan 66 kV | Loading (MW) | 6.694% | 1368% | 1355% | 1340% | 1326%
CA | 6008_Biloela - Wowan 66 kV | Power Factor | 6.714% | 99.85% | 99.85% | 99.86% | 99.86%
CA | 6008_Biloela - Wowan 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6008_Biloela - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6008_Biloela - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 104.8% | 97.35% | 97.44% | 97.54% | 97.63%
CA | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 21.96% | 31.09% | 31.41% | 31.55% | 31.57%
CA | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1
CA | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 5379% | 7617% | 7696% | 7729% | 7735%
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 641.4% | 908.5% | 917.9% | 921.6% | 922.4%
CA | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 510.9% | 789% | 794.4% | 793.8% | 790.8%
CA | 6019_Gladstone South - Friend St 66 kV | Power Factor | 79.66% | 86.85% | 86.56% | 86.13% | 85.73%
CA | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 24500% | 24500% | 24500% | 24500% | 24500%
CA | 6019_Gladstone South - Friend St 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6019_Gladstone South - Friend St 66 kV | Min Voltage at Constrained Conductor (pu) | 104.3% | 104.3% | 104.3% | 104.3% | 104.3%
CA | 6020_Gladstone South - BORE 66 kV | % of Rated A | 14.29% | 25.51% | 26.8% | 27.97% | 28.85%
CA | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1
CA | 6020_Gladstone South - BORE 66 kV | Loading (A) | 3015% | 5383% | 5654% | 5901% | 6088%
CA | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 360% | 642.8% | 675.2% | 704.7% | 727.1%
CA | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 349.8% | 642.7% | 675.2% | 704.7% | 727%
CA | 6020_Gladstone South - BORE 66 kV | Power Factor | 97.16% | 99.99% | 99.99% | 100% | 100%
CA | 6020_Gladstone South - BORE 66 kV | Rating (A) | 21100% | 21100% | 21100% | 21100% | 21100%
CA | 6020_Gladstone South - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6020_Gladstone South - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 104.4% | 104.5% | 104.5% | 104.5% | 104.5%
CA | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 2.595% | 8.221% | 8.612% | 8.974% | 9.255%
CA | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1
CA | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 1616% | 5122% | 5365% | 5591% | 5766%
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 192.9% | 612.6% | 641.7% | 668.7% | 689.6%
CA | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 115% | 574.8% | 605.5% | 633.7% | 655.5%
CA | 6022_Gladstone South - Calliope 66 kV | Power Factor | 59.61% | 93.8% | 94.3% | 94.72% | 95.01%
CA | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 62300% | 62300% | 62300% | 62300% | 62300%
CA | 6022_Gladstone South - Calliope 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6022_Gladstone South - Calliope 66 kV | Min Voltage at Constrained Conductor (pu) | 104.4% | 104.6% | 104.6% | 104.6% | 104.6%
CA | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 9.447% | 14.79% | 15.59% | 16.38% | 17.02%
CA | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22245_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 4166% | 6495% | 6846% | 7191% | 7471%
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 495.8% | 774.5% | 816.4% | 857.5% | 890.8%
CA | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 440% | 758.3% | 802.8% | 846% | 880.8%
CA | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 88.74% | 97.9% | 98.33% | 98.66% | 98.87%
CA | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 44100% | 43900% | 43900% | 43900% | 43900%
CA | 6023_Friend St-Clinton Industrial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6023_Friend St-Clinton Industrial 66 kV | Min Voltage at Constrained Conductor (pu) | 104.1% | 104.3% | 104.3% | 104.3% | 104.3%
CA | 6024_Awoonga - Calliope 66kV | % of Rated A | 13.22% | 19.83% | 18.57% | 17.43% | 16.57%
CA | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1
CA | 6024_Awoonga - Calliope 66kV | Loading (A) | 2234% | 3351% | 3138% | 2946% | 2800%
CA | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 267.2% | 401.3% | 376% | 353.2% | 335.9%
CA | 6024_Awoonga - Calliope 66kV | Loading (MW) | 257.1% | 339% | 308.8% | 280.8% | 258.9%
CA | 6024_Awoonga - Calliope 66kV | Power Factor | 96.22% | 84.48% | 82.12% | 79.5% | 77.08%
CA | 6024_Awoonga - Calliope 66kV | Rating (A) | 16900% | 16900% | 16900% | 16900% | 16900%
CA | 6024_Awoonga - Calliope 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6024_Awoonga - Calliope 66kV | Min Voltage at Constrained Conductor (pu) | 104.5% | 104.8% | 104.8% | 104.9% | 104.9%
CA | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 7.519% | 8.008% | 8.425% | 8.812% | 9.12%
CA | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 992.5% | 1057% | 1112% | 1163% | 1204%
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 120.4% | 127.5% | 134.2% | 140.4% | 145.4%
CA | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 116.9% | 124.3% | 131.2% | 137.6% | 142.7%
CA | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 97.1% | 97.53% | 97.81% | 98.03% | 98.18%
CA | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6029_Littlemore - Miriam Vale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6029_Littlemore - Miriam Vale 66 kV | Min Voltage at Constrained Conductor (pu) | 106.1% | 105.5% | 105.5% | 105.6% | 105.6%
CA | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.378% | 16% | 16.29% | 16.58% | 16.82%
CA | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 22120_1 | TR_LINE 22120_1 | TR_LINE 22120_1 | TR_LINE 22120_1
CA | 6030_Littlemore - Monto 66 kV | Loading (A) | 709.8% | 2112% | 2151% | 2188% | 2220%
CA | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 86.14% | 263.4% | 268.7% | 273.9% | 278.4%
CA | 6030_Littlemore - Monto 66 kV | Loading (MW) | 0.1575% | 135.8% | 144.7% | 153.1% | 160.1%
CA | 6030_Littlemore - Monto 66 kV | Power Factor | 0.1768% | 51.53% | 53.83% | 55.89% | 57.49%
CA | 6030_Littlemore - Monto 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6030_Littlemore - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6030_Littlemore - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 106.2% | 109.1% | 109.3% | 109.5% | 109.7%
CA | 6031_Calliope - Littlemore 66 kV | % of Rated A | 15.36% | 19.84% | 20.43% | 21.08% | 21.68%
CA | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA | 6031_Calliope - Littlemore 66 kV | Loading (A) | 2027% | 2618% | 2696% | 2783% | 2862%
CA | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 242.1% | 320.7% | 330.6% | 341.6% | 351.6%
CA | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 127.4% | 139% | 159.4% | 180.1% | 197.7%
CA | 6031_Calliope - Littlemore 66 kV | Power Factor | 52.58% | 43.33% | 48.19% | 52.71% | 56.22%
CA | 6031_Calliope - Littlemore 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6031_Calliope - Littlemore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6031_Calliope - Littlemore 66 kV | Min Voltage at Constrained Conductor (pu) | 104.5% | 107.2% | 107.3% | 107.4% | 107.5%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 8.429% | 23.33% | 23.93% | 24.59% | 25.19%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 69280_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 1779% | 3080% | 3158% | 3245% | 3325%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 212.8% | 368.7% | 378.1% | 388.6% | 398.2%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 200.4% | 148.8% | 170.3% | 192.1% | 210.7%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 94.16% | 40.32% | 45% | 49.4% | 52.88%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 21100% | 13200% | 13200% | 13200% | 13200%
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6032_Boyne Residential Tee-Awoonga 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 104.7% | 104.7% | 104.7% | 104.7%
CA | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 27.9% | 13.92% | 12.91% | 12.03% | 11.38%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 22222_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 4604% | 2937% | 2724% | 2538% | 2402%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 552% | 351.7% | 326.4% | 304.1% | 287.9%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 551.9% | 279.8% | 247.3% | 217.2% | 194%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 99.97% | 79.56% | 75.76% | 71.43% | 67.4%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 16500% | 21100% | 21100% | 21100% | 21100%
CA | 6034_Boyne Residential Tee - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6034_Boyne Residential Tee - BORE 66 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 104.8% | 104.8% | 104.8% | 104.9%
CA | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 1.809% | 29.71% | 31.25% | 32.66% | 33.74%
CA | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 16739_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 459.5% | 4902% | 5156% | 5389% | 5567%
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 54.71% | 586.2% | 616.7% | 644.6% | 665.9%
CA | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 0.02687% | 586% | 616.5% | 644.4% | 665.7%
CA | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.04853% | 99.97% | 99.97% | 99.96% | 99.96%
CA | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 25400% | 16500% | 16500% | 16500% | 16500%
CA | 6039_Clinton Industrial - Beecher 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6039_Clinton Industrial - Beecher 66 kV | Min Voltage at Constrained Conductor (pu) | 104.1% | 104.6% | 104.6% | 104.6% | 104.6%
CA | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 2.769% | 1.813% | 1.813% | 1.813% | 1.813%
CA | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 15181_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 16739_1
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 365.5% | 460.5% | 460.5% | 460.5% | 460.4%
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 43.53% | 54.94% | 54.93% | 54.93% | 54.92%
CA | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 0.01749% | 0.02698% | 0.02698% | 0.02698% | 0.02697%
CA | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.02683% | 0.04853% | 0.04853% | 0.04853% | 0.04853%
CA | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 13200% | 25400% | 25400% | 25400% | 25400%
CA | 6041_Yarwun - Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6041_Yarwun - Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 104.2% | 104.4% | 104.4% | 104.4% | 104.4%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 12.27% | 2.775% | 2.775% | 2.775% | 2.775%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 22122_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 1619% | 366.3% | 366.3% | 366.3% | 366.3%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 192.9% | 43.71% | 43.71% | 43.71% | 43.7%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 191.5% | 0.01757% | 0.01757% | 0.01757% | 0.01756%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 99.29% | 0.02683% | 0.02683% | 0.02683% | 0.02683%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6044_Raglan-East End Quarry/Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 104.2% | 104.4% | 104.4% | 104.4% | 104.4%
CA | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 4.019% | 12.22% | 12.22% | 12.21% | 12.21%
CA | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 530.6% | 1613% | 1612% | 1612% | 1612%
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 63.81% | 192.9% | 192.9% | 192.9% | 192.9%
CA | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 5.402% | 191.5% | 191.5% | 191.5% | 191.5%
CA | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 8.465% | 99.27% | 99.27% | 99.26% | 99.26%
CA | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6045_Coominglah Tee - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor (pu) | 105.2% | 104.6% | 104.7% | 104.7% | 104.7%
CA | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 79.44% | 4.056% | 4.204% | 4.49% | 4.829%
CA | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 22233_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 10486% | 535.4% | 555% | 592.7% | 637.4%
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 1226% | 64.76% | 67.18% | 71.78% | 77.24%
CA | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 1225% | 7.204% | 18.96% | 31.5% | 42.45%
CA | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 99.91% | 11.12% | 28.22% | 43.88% | 54.96%
CA | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
CA | 6046_Mt Morgan - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6046_Mt Morgan - Wowan 66 kV | Min Voltage at Constrained Conductor (pu) | 102.3% | 105.8% | 105.9% | 106% | 106%
CA | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 0.4802% | 87.33% | 87.02% | 86.72% | 86.45%
CA | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1
CA | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 73.95% | 11527% | 11487% | 11446% | 11411%
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 8.893% | 1221% | 1221% | 1221% | 1221%
CA | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 8.892% | 1221% | 1221% | 1221% | 1221%
CA | 6047_Coominglah Sub Tee 66 kV | Power Factor | 99.99% | 100% | 100% | 100% | 100%
CA | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 15400% | 13200% | 13200% | 13200% | 13200%
CA | 6047_Coominglah Sub Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6047_Coominglah Sub Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 105.2% | 92.69% | 93.01% | 93.34% | 93.63%
CA | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 10.84% | 0.5397% | 0.5956% | 0.6533% | 0.7062%
CA | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 13284_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 4347% | 83.12% | 91.72% | 100.6% | 108.8%
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 519.3% | 9.955% | 10.99% | 12.07% | 13.05%
CA | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 519.3% | 9.955% | 10.99% | 12.07% | 13.05%
CA | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 100% | 100% | 100% | 100% | 100%
CA | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 40100% | 15400% | 15400% | 15400% | 15400%
CA | 6050_Parkhurst - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6050_Parkhurst - Frenchville 66 kV | Min Voltage at Constrained Conductor (pu) | 104.5% | 104.8% | 104.8% | 104.9% | 105%
CA | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 30.4% | 15.3% | 16.17% | 16.9% | 17.4%
CA | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1
CA | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 6445% | 6136% | 6483% | 6779% | 6978%
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 784% | 738.2% | 780.3% | 816.2% | 840.4%
CA | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 752.2% | 738.1% | 780.1% | 816% | 840.1%
CA | 6051_Parkhurst - Keppel 66 kV | Power Factor | 95.85% | 99.98% | 99.97% | 99.97% | 99.97%
CA | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 21200% | 40100% | 40100% | 40100% | 40100%
CA | 6051_Parkhurst - Keppel 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6051_Parkhurst - Keppel 66 kV | Min Voltage at Constrained Conductor (pu) | 106.4% | 105.3% | 105.3% | 105.3% | 105.4%
CA | 6052_Pandoin - Kunwarara 66 kV | % of Rated A | 18.79% | 60.34% | 65.7% | 71.1% | 75.67%
CA | 6052_Pandoin - Kunwarara 66 kV | Limiting Line Name | TR_LINE 17424_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (A) | 6521% | 12792% | 13928% | 15073% | 16043%
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MVA) | 758.9% | 1589% | 1734% | 1881% | 2006%
CA | 6052_Pandoin - Kunwarara 66 kV | Loading (MW) | 758.2% | 1563% | 1712% | 1862% | 1989%
CA | 6052_Pandoin - Kunwarara 66 kV | Power Factor | 99.83% | 98.41% | 98.72% | 98.97% | 99.14%
CA | 6052_Pandoin - Kunwarara 66 kV | Rating (A) | 34700% | 21200% | 21200% | 21200% | 21200%
CA | 6052_Pandoin - Kunwarara 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6052_Pandoin - Kunwarara 66 kV | Min Voltage at Constrained Conductor (pu) | 101.1% | 108.4% | 108.6% | 108.9% | 109%
CA | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 14.65% | 18.96% | 18.96% | 18.95% | 18.95%
CA | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1 | TR_LINE 17424_1
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 7661% | 6578% | 6577% | 6577% | 6577%
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 911% | 759.1% | 759.1% | 759.1% | 759.1%
CA | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 537.7% | 758.4% | 758.4% | 758.4% | 758.4%
CA | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 58.88% | 99.82% | 99.82% | 99.82% | 99.82%
CA | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 52300% | 34700% | 34700% | 34700% | 34700%
CA | 6053_Parkhurst - Pandoin 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6053_Parkhurst - Pandoin 66 kV | Min Voltage at Constrained Conductor (pu) | 104% | 100.3% | 100.3% | 100.3% | 100.3%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 44.92% | 22.33% | 23.52% | 24.7% | 25.66%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 223719_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 7591% | 11678% | 12299% | 12918% | 13421%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 905.8% | 1400% | 1475% | 1550% | 1611%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 905.8% | 1157% | 1247% | 1336% | 1406%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 99.98% | 82.64% | 84.48% | 86.17% | 87.26%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 16900% | 52300% | 52300% | 52300% | 52300%
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6066_Bocoolima Tee -Wooderson 66 kV | Min Voltage at Constrained Conductor (pu) | 103.3% | 104.7% | 104.7% | 104.7% | 104.7%
CA | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 13.8% | 45.11% | 45.11% | 45.11% | 45.11%
CA | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | 6074_Lakes Creek | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 223719_1
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 5506% | 7624% | 7623% | 7623% | 7623%
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 662.8% | 906% | 905.9% | 905.9% | 905.9%
CA | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 655.5% | 905.9% | 905.9% | 905.9% | 905.9%
CA | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 98.89% | 99.98% | 99.98% | 99.98% | 99.98%
CA | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 39900% | 16900% | 16900% | 16900% | 16900%
CA | 6074_Lakes Creek - Tanby 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6074_Lakes Creek - Tanby 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 102.9% | 102.9% | 102.9% | 102.9%
CA | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.3213% | 32.21% | 34.99% | 37.79% | 40.17%
CA | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | 6074_Lakes Creek | 6074_Lakes Creek | 6074_Lakes Creek | 6074_Lakes Creek
CA | 6075_Keppel - Farnborough 66 kV | Loading (A) | 121.4% | 12853% | 13960% | 15079% | 16027%
CA | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 14.79% | 1561% | 1696% | 1833% | 1949%
CA | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 0.0003686% | 1526% | 1668% | 1810% | 1930%
CA | 6075_Keppel - Farnborough 66 kV | Power Factor | 0.0002192% | 97.8% | 98.33% | 98.75% | 99.03%
CA | 6075_Keppel - Farnborough 66 kV | Rating (A) | 37800% | 39900% | 39900% | 39900% | 39900%
CA | 6075_Keppel - Farnborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6075_Keppel - Farnborough 66 kV | Min Voltage at Constrained Conductor (pu) | 106.6% | 106.2% | 106.3% | 106.3% | 106.4%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 30.2% | 0.3277% | 0.3285% | 0.3292% | 0.3298%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 19629_1 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 6403% | 123.9% | 124.2% | 124.4% | 124.7%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 780% | 15.39% | 15.46% | 15.53% | 15.59%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 752.3% | 0.0003835% | 0.0003853% | 0.0003871% | 0.0003886%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 96.44% | 0.0002191% | 0.000219% | 0.0002192% | 0.0002194%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 21200% | 37800% | 37800% | 37800% | 37800%
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6082_Farnborough Tee - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 106.6% | 108.7% | 108.9% | 109.2% | 109.4%
CA | 6087_Glenmore - QMAG Tee 66 kV | % of Rated A | 12.76% | 60.21% | 65.58% | 71% | 75.58%
CA | 6087_Glenmore - QMAG Tee 66 kV | Limiting Line Name | TR_LINE 20862_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (A) | 5117% | 12765% | 13903% | 15051% | 16023%
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MVA) | 610.9% | 1586% | 1732% | 1879% | 2004%
CA | 6087_Glenmore - QMAG Tee 66 kV | Loading (MW) | 610.7% | 1563% | 1712% | 1862% | 1989%
CA | 6087_Glenmore - QMAG Tee 66 kV | Power Factor | 99.96% | 98.57% | 98.86% | 99.08% | 99.24%
CA | 6087_Glenmore - QMAG Tee 66 kV | Rating (A) | 40100% | 21200% | 21200% | 21200% | 21200%
CA | 6087_Glenmore - QMAG Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6087_Glenmore - QMAG Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 104.4% | 108.7% | 108.9% | 109.2% | 109.4%
CA | 6088_QMAG Tee - Parkhurst 66 kV | % of Rated A | 29.96% | 18.04% | 18.06% | 18.09% | 18.12%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Limiting Line Name | TR_LINE 20878_6 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1 | TR_LINE 20862_1
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (A) | 10397% | 7236% | 7241% | 7255% | 7266%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MVA) | 1242% | 867% | 867.7% | 869.5% | 870.9%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Loading (MW) | 1242% | 863% | 863.8% | 865.6% | 867.1%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Power Factor | 99.96% | 99.52% | 99.53% | 99.54% | 99.55%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Rating (A) | 34700% | 40100% | 40100% | 40100% | 40100%
CA | 6088_QMAG Tee - Parkhurst 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6088_QMAG Tee - Parkhurst 66 kV | Min Voltage at Constrained Conductor (pu) | 104.4% | 104.7% | 104.8% | 104.8% | 104.8%
CA | 6089_QMAG Tee - QMAG 66 kV | % of Rated A | 38.67% | 36.11% | 37.39% | 38.65% | 39.68%
CA | 6089_QMAG Tee - QMAG 66 kV | Limiting Line Name | TR_LINE 22236_1 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6 | TR_LINE 20878_6
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (A) | 15505% | 12531% | 12975% | 13413% | 13769%
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MVA) | 1850% | 1516% | 1570% | 1624% | 1668%
CA | 6089_QMAG Tee - QMAG 66 kV | Loading (MW) | 1850% | 1498% | 1554% | 1609% | 1653%
CA | 6089_QMAG Tee - QMAG 66 kV | Power Factor | 100% | 98.84% | 98.95% | 99.05% | 99.13%
CA | 6089_QMAG Tee - QMAG 66 kV | Rating (A) | 40100% | 34700% | 34700% | 34700% | 34700%
CA | 6089_QMAG Tee - QMAG 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6089_QMAG Tee - QMAG 66 kV | Min Voltage at Constrained Conductor (pu) | 104.4% | 105.7% | 105.8% | 105.8% | 105.8%
CA | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 13.94% | 38.55% | 38.54% | 38.54% | 38.54%
CA | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 160589_1 | TR_LINE 22236_1 | TR_LINE 22236_1 | TR_LINE 22236_1 | TR_LINE 22236_1
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 1840% | 15458% | 15455% | 15454% | 15453%
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 220.4% | 1850% | 1850% | 1850% | 1850%
CA | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 211% | 1850% | 1850% | 1850% | 1850%
CA | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 95.7% | 100% | 100% | 100% | 100%
CA | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 13200% | 40100% | 40100% | 40100% | 40100%
CA | 6090_Egan's Hill - Raglan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6090_Egan's Hill - Raglan 66 kV | Min Voltage at Constrained Conductor (pu) | 104.8% | 104.7% | 104.7% | 104.7% | 104.7%
CA | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 73.39% | 13.43% | 13% | 12.53% | 12.15%
CA | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 22265_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 10495% | 1772% | 1716% | 1654% | 1604%
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 1256% | 213.1% | 206.3% | 198.9% | 192.9%
CA | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 1255% | 203% | 195.9% | 187.9% | 181.5%
CA | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 99.92% | 95.27% | 94.92% | 94.5% | 94.12%
CA | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 14300% | 13200% | 13200% | 13200% | 13200%
CA | 6091_Egan's Hill - Gavial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6091_Egan's Hill - Gavial 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 105.2% | 105.2% | 105.2% | 105.2%
CA | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 79.48% | 73.2% | 73.19% | 73.19% | 73.19%
CA | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19767_1 | TR_LINE 22265_1 | TR_LINE 22265_1 | TR_LINE 22265_1 | TR_LINE 22265_1
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 10491% | 10467% | 10466% | 10466% | 10466%
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 1244% | 1256% | 1256% | 1256% | 1256%
CA | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 1243% | 1255% | 1255% | 1255% | 1255%
CA | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 99.91% | 99.92% | 99.92% | 99.92% | 99.92%
CA | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 13200% | 14300% | 14300% | 14300% | 14300%
CA | 6093_Gavial - Mt Morgan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6093_Gavial - Mt Morgan 66 kV | Min Voltage at Constrained Conductor (pu) | 102.3% | 104.9% | 105% | 105% | 105%
CA | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 24.7% | 79.27% | 79.26% | 79.26% | 79.26%
CA | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 4174% | 10463% | 10462% | 10462% | 10462%
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 501% | 1244% | 1244% | 1244% | 1244%
CA | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 500.9% | 1243% | 1243% | 1243% | 1243%
CA | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 99.98% | 99.9% | 99.9% | 99.9% | 99.9%
CA | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 16900% | 13200% | 13200% | 13200% | 13200%
CA | 6094_Malchi Tee - Malchi 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6094_Malchi Tee - Malchi 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 102.5% | 102.5% | 102.5% | 102.5%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 12.14% | 25.87% | 27.11% | 28.34% | 29.4%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20972_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 3011% | 4373% | 4582% | 4789% | 4968%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 360.5% | 526.8% | 552.1% | 577.2% | 598.8%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 99.99% | 526.7% | 552% | 577.1% | 598.7%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 27.74% | 99.98% | 99.98% | 99.97% | 99.97%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 24800% | 16900% | 16900% | 16900% | 16900%
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6095_Egan's Hill-Rockhampton South 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 105.1% | 105.1% | 105.1% | 105.1%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | % of Rated A | 9.422% | 23.9% | 23.99% | 24.08% | 24.19%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Limiting Line Name | TR_LINE 19717_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (A) | 3024% | 5928% | 5949% | 5972% | 6000%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MVA) | 363.3% | 713.2% | 715.9% | 718.7% | 722.2%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MW) | 324.3% | 146.1% | 157.3% | 168.7% | 181.7%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Power Factor | 89.26% | 20.41% | 21.9% | 23.4% | 25.1%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Rating (A) | 32100% | 24800% | 24800% | 24800% | 24800%
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6096_Egan's Hill - Lakes Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 105.2% | 105.3% | 105.3% | 105.3%
CA | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 7.443% | 31.48% | 33% | 34.64% | 36.08%
CA | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 21003_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1 | TR_LINE 19717_1
CA | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 1846% | 10106% | 10592% | 11118% | 11583%
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 221.2% | 1230% | 1290% | 1354% | 1412%
CA | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 90.65% | 642.8% | 754.2% | 864% | 954.6%
CA | 6097_Egan's Hill - Canning 66 kV | Power Factor | 40.99% | 52.23% | 58.44% | 63.75% | 67.59%
CA | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 24800% | 32100% | 32100% | 32100% | 32100%
CA | 6097_Egan's Hill - Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6097_Egan's Hill - Canning 66 kV | Min Voltage at Constrained Conductor (pu) | 104.8% | 106.4% | 106.5% | 106.5% | 106.6%
CA | 6100_Boat Creek - ICI 66 kV | % of Rated A | 7.767% | 18.26% | 18.2% | 18.14% | 18.07%
CA | 6100_Boat Creek - ICI 66 kV | Limiting Line Name | TR_LINE 50343_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1
CA | 6100_Boat Creek - ICI 66 kV | Loading (A) | 5748% | 4529% | 4514% | 4498% | 4481%
CA | 6100_Boat Creek - ICI 66 kV | Loading (MVA) | 671.6% | 545.3% | 543.6% | 541.7% | 539.8%
CA | 6100_Boat Creek - ICI 66 kV | Loading (MW) | 671.4% | 25.54% | 26.53% | 27.83% | 27.16%
CA | 6100_Boat Creek - ICI 66 kV | Power Factor | 99.96% | 4.577% | 4.775% | 5.032% | 4.925%
CA | 6100_Boat Creek - ICI 66 kV | Rating (A) | 74000% | 24800% | 24800% | 24800% | 24800%
CA | 6100_Boat Creek - ICI 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6100_Boat Creek - ICI 66 kV | Min Voltage at Constrained Conductor (pu) | 102.2% | 105.3% | 105.3% | 105.4% | 105.4%
CA | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 1.533% | 7.858% | 7.859% | 7.859% | 7.86%
CA | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16877_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 429.3% | 5815% | 5815% | 5816% | 5816%
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 50.16% | 671.6% | 671.6% | 671.6% | 671.6%
CA | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 50.02% | 671.3% | 671.3% | 671.4% | 671.4%
CA | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 99.73% | 99.96% | 99.96% | 99.96% | 99.96%
CA | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 28000% | 74000% | 74000% | 74000% | 74000%
CA | 6102_Boat Creek - Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6102_Boat Creek - Yarwun 66 kV | Min Voltage at Constrained Conductor (pu) | 102.2% | 101% | 101% | 101% | 101%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 83.48% | 1.551% | 1.551% | 1.551% | 1.551%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 23375% | 434.3% | 434.3% | 434.3% | 434.3%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 2720% | 50.15% | 50.15% | 50.15% | 50.15%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 2720% | 50.02% | 50.02% | 50.02% | 50.02%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 100% | 99.74% | 99.74% | 99.74% | 99.74%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 28000% | 28000% | 28000% | 28000% | 28000%
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor (pu) | 101.8% | 101% | 101% | 101% | 101%
CA | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 14.45% | 85.78% | 85.78% | 85.79% | 85.79%
CA | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1 | TR_LINE 16877_1
CA | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 5245% | 24017% | 24019% | 24021% | 24022%
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 623.6% | 2791% | 2791% | 2791% | 2791%
CA | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 263% | 2791% | 2791% | 2791% | 2791%
CA | 6109_Gladstone North - Clinton 66 kV | Power Factor | 42.17% | 100% | 100% | 100% | 100%
CA | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 36300% | 28000% | 28000% | 28000% | 28000%
CA | 6109_Gladstone North - Clinton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6109_Gladstone North - Clinton 66 kV | Min Voltage at Constrained Conductor (pu) | 104% | 100.9% | 100.9% | 100.9% | 100.9%
CA | 6110_Port Curtis 66 kV | % of Rated A | 17.68% | 84.47% | 84.47% | 84.48% | 84.49%
CA | 6110_Port Curtis 66 kV | Limiting Line Name | TR_LINE 61924_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA | 6110_Port Curtis 66 kV | Loading (A) | 6417% | 23651% | 23653% | 23654% | 23656%
CA | 6110_Port Curtis 66 kV | Loading (MVA) | 762.8% | 2720% | 2720% | 2720% | 2720%
CA | 6110_Port Curtis 66 kV | Loading (MW) | 734.9% | 2720% | 2720% | 2720% | 2720%
CA | 6110_Port Curtis 66 kV | Power Factor | 96.3% | 100% | 100% | 100% | 100%
CA | 6110_Port Curtis 66 kV | Rating (A) | 36300% | 28000% | 28000% | 28000% | 28000%
CA | 6110_Port Curtis 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6110_Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 104% | 100.6% | 100.6% | 100.6% | 100.6%
CA | 6111_Gladstone North - Port Curtis 66 kV | % of Rated A | 22.3% | 29.18% | 27.52% | 25.89% | 24.6%
CA | 6111_Gladstone North - Port Curtis 66 kV | Limiting Line Name | TR_LINE 60721_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (A) | 8093% | 10591% | 9991% | 9399% | 8930%
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MVA) | 962.4% | 1259% | 1187% | 1117% | 1061%
CA | 6111_Gladstone North - Port Curtis 66 kV | Loading (MW) | 948% | 1050% | 970.1% | 889% | 823.4%
CA | 6111_Gladstone North - Port Curtis 66 kV | Power Factor | 98.51% | 83.44% | 81.71% | 79.61% | 77.61%
CA | 6111_Gladstone North - Port Curtis 66 kV | Rating (A) | 36300% | 36300% | 36300% | 36300% | 36300%
CA | 6111_Gladstone North - Port Curtis 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6111_Gladstone North - Port Curtis 66 kV | Min Voltage at Constrained Conductor (pu) | 104% | 104% | 104% | 103.9% | 103.9%
CA | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 1.482% | 39.03% | 39.03% | 39.04% | 39.04%
CA | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 155369_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1 | TR_LINE 61924_1
CA | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 650.8% | 14168% | 14170% | 14171% | 14172%
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 79.38% | 1684% | 1684% | 1684% | 1684%
CA | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 1.32% | 1683% | 1683% | 1683% | 1683%
CA | 6298_Tanby - Yeppoon 66 kV | Power Factor | 1.663% | 99.96% | 99.96% | 99.96% | 99.96%
CA | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 43900% | 36300% | 36300% | 36300% | 36300%
CA | 6298_Tanby - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6298_Tanby - Yeppoon 66 kV | Min Voltage at Constrained Conductor (pu) | 106.7% | 103.9% | 103.9% | 103.9% | 103.8%
CA | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 11.09% | 39.06% | 39.06% | 39.07% | 39.07%
CA | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | TR_LINE 20950_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1 | TR_LINE 61923_1
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 4445% | 14178% | 14180% | 14182% | 14183%
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 533.6% | 1684% | 1684% | 1684% | 1684%
CA | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 324.3% | 1683% | 1683% | 1683% | 1683%
CA | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 60.77% | 99.96% | 99.96% | 99.96% | 99.96%
CA | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 40100% | 36300% | 36300% | 36300% | 36300%
CA | 6310_Lakes Creek - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6310_Lakes Creek - Berserker 66 kV | Min Voltage at Constrained Conductor (pu) | 105% | 103.8% | 103.8% | 103.8% | 103.8%
CA | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 13.73% | 19.4% | 21.29% | 23.25% | 24.93%
CA | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 12202% | 7333% | 8049% | 8787% | 9424%
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 2932% | 927.2% | 1021% | 1117% | 1201%
CA | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 2921% | 858.3% | 959.1% | 1062% | 1151%
CA | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 99.61% | 92.55% | 93.96% | 95.05% | 95.79%
CA | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 88900% | 37800% | 37800% | 37800% | 37800%
CA | 7290_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7290_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 110.6% | 110.9% | 111.2% | 111.5%
CA | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 13.79% | 21.8% | 23.21% | 24.66% | 25.87%
CA | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 20950_1 | TR_LINE 20950_1 | TR_LINE 20950_1 | TR_LINE 20950_1
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 12262% | 8741% | 9308% | 9888% | 10375%
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 2947% | 1056% | 1125% | 1195% | 1254%
CA | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 2935% | 887.4% | 974.4% | 1061% | 1133%
CA | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 99.6% | 84.04% | 86.64% | 88.79% | 90.31%
CA | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 88900% | 40100% | 40100% | 40100% | 40100%
CA | 7291_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 7291_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 105.7% | 105.7% | 105.7% | 105.7%
CA | 6026_Moura - Theodore 66 kV | % of Rated A | 5.172% | 32.22% | 32.2% | 32.19% | 32.18%
CA | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59683_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA | 6026_Moura - Theodore 66 kV | Loading (A) | 3770% | 28640% | 28628% | 28618% | 28609%
CA | 6026_Moura - Theodore 66 kV | Loading (MVA) | 444.9% | 6864% | 6861% | 6858% | 6855%
CA | 6026_Moura - Theodore 66 kV | Loading (MW) | 438.5% | 6767% | 6764% | 6761% | 6758%
CA | 6026_Moura - Theodore 66 kV | Power Factor | 98.55% | 98.58% | 98.58% | 98.58% | 98.58%
CA | 6026_Moura - Theodore 66 kV | Rating (A) | 72900% | 88900% | 88900% | 88900% | 88900%
CA | 6026_Moura - Theodore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA | 6026_Moura - Theodore 66 kV | Min Voltage at Constrained Conductor (pu) | 103.2% | 104.8% | 104.8% | 104.8% | 104.8%
FN | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 6.753% | 32.21% | 32.2% | 32.19% | 32.18%
FN | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 3958_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 2823% | 28637% | 28625% | 28615% | 28606%
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 677.6% | 6864% | 6860% | 6857% | 6855%
FN | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 671.5% | 6767% | 6763% | 6760% | 6758%
FN | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 99.11% | 98.59% | 98.59% | 98.59% | 98.59%
FN | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 41800% | 88900% | 88900% | 88900% | 88900%
FN | 7206 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7206 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 105% | 104.8% | 104.8% | 104.8% | 104.8%
FN | 7227 Woree-Cairns Terminal-Cairns City | % of Rated A | 6.761% | 6.062% | 6.062% | 6.061% | 6.061%
FN | 7227 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 176513_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (A) | 2826% | 1285% | 1285% | 1285% | 1285%
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 678.4% | 24.85% | 24.85% | 24.85% | 24.85%
FN | 7227 Woree-Cairns Terminal-Cairns City | Loading (MW) | 672.4% | 20.46% | 20.46% | 20.46% | 20.46%
FN | 7227 Woree-Cairns Terminal-Cairns City | Power Factor | 99.12% | 82.31% | 82.31% | 82.31% | 82.31%
FN | 7227 Woree-Cairns Terminal-Cairns City | Rating (A) | 41800% | 21200% | 21200% | 21200% | 21200%
FN | 7227 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7227 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor (pu) | 105% | 101.5% | 101.5% | 101.5% | 101.5%
FN | 7332_Cairns North 132 kV | % of Rated A | 7.528% | 5.082% | 4.987% | 4.881% | 4.793%
FN | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1
FN | 7332_Cairns North 132 kV | Loading (A) | 3561% | 3705% | 3635% | 3558% | 3494%
FN | 7332_Cairns North 132 kV | Loading (MVA) | 854.8% | 435.9% | 427.8% | 418.8% | 411.3%
FN | 7332_Cairns North 132 kV | Loading (MW) | 21.2% | 429.3% | 420.9% | 411.7% | 403.9%
FN | 7332_Cairns North 132 kV | Power Factor | 2.48% | 98.49% | 98.4% | 98.3% | 98.2%
FN | 7332_Cairns North 132 kV | Rating (A) | 47300% | 72900% | 72900% | 72900% | 72900%
FN | 7332_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7332_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 105% | 102.9% | 102.9% | 103% | 103%
FN | 7333_Cairns North 132 kV | % of Rated A | 7.224% | 13.15% | 12.93% | 12.55% | 12.24%
FN | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1
FN | 7333_Cairns North 132 kV | Loading (A) | 3417% | 5497% | 5403% | 5246% | 5117%
FN | 7333_Cairns North 132 kV | Loading (MVA) | 820.3% | 1319% | 1297% | 1259% | 1228%
FN | 7333_Cairns North 132 kV | Loading (MW) | 19.27% | 1319% | 1296% | 1258% | 1227%
FN | 7333_Cairns North 132 kV | Power Factor | 2.348% | 99.94% | 99.93% | 99.92% | 99.91%
FN | 7333_Cairns North 132 kV | Rating (A) | 47300% | 41800% | 41800% | 41800% | 41800%
FN | 7333_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7333_Cairns North 132 kV | Min Voltage at Constrained Conductor (pu) | 105% | 104.9% | 104.9% | 104.9% | 104.9%
FN | 3CRO_Croydon 66 kV | % of Rated A | 3.955% | 13.15% | 12.93% | 12.55% | 12.24%
FN | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1
FN | 3CRO_Croydon 66 kV | Loading (A) | 1807% | 5497% | 5403% | 5245% | 5117%
FN | 3CRO_Croydon 66 kV | Loading (MVA) | 217.4% | 1319% | 1297% | 1259% | 1228%
FN | 3CRO_Croydon 66 kV | Loading (MW) | 96% | 1319% | 1296% | 1258% | 1227%
FN | 3CRO_Croydon 66 kV | Power Factor | 44.15% | 99.94% | 99.94% | 99.92% | 99.91%
FN | 3CRO_Croydon 66 kV | Rating (A) | 45700% | 41800% | 41800% | 41800% | 41800%
FN | 3CRO_Croydon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3CRO_Croydon 66 kV | Min Voltage at Constrained Conductor (pu) | 105.2% | 105% | 105% | 105% | 105%
FN | 3NOR_Normanton 66 kV | % of Rated A | 4.436% | 15.12% | 15.3% | 15.57% | 15.85%
FN | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN | 3NOR_Normanton 66 kV | Loading (A) | 2027% | 7151% | 7237% | 7365% | 7497%
FN | 3NOR_Normanton 66 kV | Loading (MVA) | 241.1% | 1717% | 1737% | 1768% | 1800%
FN | 3NOR_Normanton 66 kV | Loading (MW) | 81.92% | 190.9% | 338.4% | 483.7% | 599.2%
FN | 3NOR_Normanton 66 kV | Power Factor | 33.59% | 11.12% | 19.48% | 27.36% | 33.29%
FN | 3NOR_Normanton 66 kV | Rating (A) | 45700% | 47300% | 47300% | 47300% | 47300%
FN | 3NOR_Normanton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3NOR_Normanton 66 kV | Min Voltage at Constrained Conductor (pu) | 104% | 105% | 105% | 105% | 105%
FN | 4KID_Ross - Kidston 132 kV | % of Rated A | 17.89% | 15.2% | 15.38% | 15.65% | 15.93%
FN | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN | 4KID_Ross - Kidston 132 kV | Loading (A) | 6352% | 7191% | 7276% | 7403% | 7533%
FN | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 1525% | 1726% | 1747% | 1777% | 1808%
FN | 4KID_Ross - Kidston 132 kV | Loading (MW) | 132.1% | 190.7% | 338.3% | 483.6% | 599.1%
FN | 4KID_Ross - Kidston 132 kV | Power Factor | 8.662% | 11.05% | 19.37% | 27.21% | 33.13%
FN | 4KID_Ross - Kidston 132 kV | Rating (A) | 35500% | 47300% | 47300% | 47300% | 47300%
FN | 4KID_Ross - Kidston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 4KID_Ross - Kidston 132 kV | Min Voltage at Constrained Conductor (pu) | 105% | 105% | 105% | 105% | 105%
FN | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 9.142% | 3.73% | 3.729% | 3.729% | 3.728%
FN | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 2724% | 1705% | 1704% | 1704% | 1704%
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 675.3% | 205.9% | 205.9% | 205.9% | 205.8%
FN | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 114.2% | 12.49% | 11.23% | 9.811% | 8.56%
FN | 7216_4GEO (Georgetown) 132 kV | Power Factor | 16.69% | 6.068% | 5.454% | 4.766% | 4.159%
FN | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 29800% | 45700% | 45700% | 45700% | 45700%
FN | 7216_4GEO (Georgetown) 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7216_4GEO (Georgetown) 132 kV | Min Voltage at Constrained Conductor (pu) | 108.4% | 105.7% | 105.7% | 105.7% | 105.7%
FN | 3AT1_Atherton No 1 66 kV | % of Rated A | 3.874% | 4.588% | 4.606% | 4.637% | 4.671%
FN | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN | 3AT1_Atherton No 1 66 kV | Loading (A) | 2123% | 2097% | 2105% | 2119% | 2135%
FN | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 263.6% | 249.4% | 250.5% | 252.2% | 254.1%
FN | 3AT1_Atherton No 1 66 kV | Loading (MW) | 21.43% | 71.34% | 61.18% | 49.76% | 39.92%
FN | 3AT1_Atherton No 1 66 kV | Power Factor | 8.125% | 28.2% | 24.03% | 19.34% | 15.32%
FN | 3AT1_Atherton No 1 66 kV | Rating (A) | 54800% | 45700% | 45700% | 45700% | 45700%
FN | 3AT1_Atherton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3AT1_Atherton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 108.6% | 104.1% | 104.1% | 104.1% | 104.1%
FN | 3AT2_Atherton No 2 66 kV | % of Rated A | 3.879% | 19.52% | 19.52% | 19.52% | 19.52%
FN | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN | 3AT2_Atherton No 2 66 kV | Loading (A) | 2125% | 6929% | 6929% | 6929% | 6929%
FN | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 263.9% | 1663% | 1663% | 1663% | 1663%
FN | 3AT2_Atherton No 2 66 kV | Loading (MW) | 21.43% | 262.7% | 262.5% | 262.6% | 262.6%
FN | 3AT2_Atherton No 2 66 kV | Power Factor | 8.113% | 14.03% | 14.02% | 14.03% | 14.02%
FN | 3AT2_Atherton No 2 66 kV | Rating (A) | 54800% | 35500% | 35500% | 35500% | 35500%
FN | 3AT2_Atherton No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3AT2_Atherton No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 108.6% | 105% | 105% | 105% | 105%
FN | 3CHI_Chillagoe 66 kV | % of Rated A | 2.575% | 10.87% | 10.88% | 10.89% | 10.9%
FN | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104006_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN | 3CHI_Chillagoe 66 kV | Loading (A) | 1411% | 3238% | 3242% | 3246% | 3249%
FN | 3CHI_Chillagoe 66 kV | Loading (MVA) | 176.1% | 803% | 803.9% | 805% | 805.8%
FN | 3CHI_Chillagoe 66 kV | Loading (MW) | 21.42% | 14.73% | 10.77% | 6.739% | 3.388%
FN | 3CHI_Chillagoe 66 kV | Power Factor | 12.16% | 1.528% | 1.033% | 0.5297% | 0.1126%
FN | 3CHI_Chillagoe 66 kV | Rating (A) | 54800% | 29800% | 29800% | 29800% | 29800%
FN | 3CHI_Chillagoe 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3CHI_Chillagoe 66 kV | Min Voltage at Constrained Conductor (pu) | 109.1% | 108.5% | 108.5% | 108.5% | 108.5%
FN | 3COO_Cooktown 66 kV | % of Rated A | 1.245% | 8.133% | 8.773% | 9.667% | 10.57%
FN | 3COO_Cooktown 66 kV | Limiting Line Name | TR_LINE 138000_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1
FN | 3COO_Cooktown 66 kV | Loading (A) | 496.8% | 4457% | 4807% | 5297% | 5792%
FN | 3COO_Cooktown 66 kV | Loading (MVA) | 60.27% | 553.7% | 597.7% | 659.2% | 721.2%
FN | 3COO_Cooktown 66 kV | Loading (MW) | 33.23% | 162.7% | 277.8% | 394.1% | 492.4%
FN | 3COO_Cooktown 66 kV | Power Factor | 55.13% | 29.36% | 46.47% | 59.77% | 68.25%
FN | 3COO_Cooktown 66 kV | Rating (A) | 39900% | 54800% | 54800% | 54800% | 54800%
FN | 3COO_Cooktown 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3COO_Cooktown 66 kV | Min Voltage at Constrained Conductor (pu) | 106.1% | 108.7% | 108.8% | 108.9% | 108.9%
FN | 3DIM_Dimbulah 66 kV | % of Rated A | 18.16% | 6.239% | 7.064% | 8.161% | 9.226%
FN | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 173520_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1
FN | 3DIM_Dimbulah 66 kV | Loading (A) | 3958% | 3419% | 3871% | 4472% | 5056%
FN | 3DIM_Dimbulah 66 kV | Loading (MVA) | 491.1% | 423.7% | 480% | 555.1% | 628%
FN | 3DIM_Dimbulah 66 kV | Loading (MW) | 491.1% | 165.4% | 280.5% | 396.8% | 495%
FN | 3DIM_Dimbulah 66 kV | Power Factor | 100% | 39.02% | 58.43% | 71.47% | 78.82%
FN | 3DIM_Dimbulah 66 kV | Rating (A) | 21800% | 54800% | 54800% | 54800% | 54800%
FN | 3DIM_Dimbulah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3DIM_Dimbulah 66 kV | Min Voltage at Constrained Conductor (pu) | 108.5% | 108.4% | 108.5% | 108.6% | 108.6%
FN | 3EVE_Evelyn 66 kV | % of Rated A | 3.07% | 2.576% | 2.575% | 2.576% | 2.576%
FN | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 4423_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1
FN | 3EVE_Evelyn 66 kV | Loading (A) | 798.2% | 1412% | 1411% | 1411% | 1412%
FN | 3EVE_Evelyn 66 kV | Loading (MVA) | 99.41% | 176.4% | 176.6% | 176.8% | 176.9%
FN | 3EVE_Evelyn 66 kV | Loading (MW) | 42.52% | 19.23% | 17.11% | 14.99% | 13.19%
FN | 3EVE_Evelyn 66 kV | Power Factor | 42.67% | 10.9% | 9.69% | 8.481% | 7.455%
FN | 3EVE_Evelyn 66 kV | Rating (A) | 26000% | 54800% | 54800% | 54800% | 54800%
FN | 3EVE_Evelyn 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3EVE_Evelyn 66 kV | Min Voltage at Constrained Conductor (pu) | 108.9% | 109.3% | 109.4% | 109.6% | 109.7%
FN | 3HLA_Helenvale 66 kV | % of Rated A | 3.112% | 1.119% | 1.056% | 1.075% | 1.162%
FN | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1
FN | 3HLA_Helenvale 66 kV | Loading (A) | 1176% | 446.6% | 421.5% | 429% | 463.6%
FN | 3HLA_Helenvale 66 kV | Loading (MVA) | 142.2% | 54.66% | 51.66% | 52.68% | 57.02%
FN | 3HLA_Helenvale 66 kV | Loading (MW) | 40.61% | 19.02% | 4.795% | 10.44% | 23.91%
FN | 3HLA_Helenvale 66 kV | Power Factor | 28.55% | 34.79% | 9.281% | 19.8% | 41.89%
FN | 3HLA_Helenvale 66 kV | Rating (A) | 37800% | 39900% | 39900% | 39900% | 39900%
FN | 3HLA_Helenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3HLA_Helenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 105.8% | 107.1% | 107.2% | 107.4% | 107.6%
FN | 3MO1_Mossman No 1 66 kV | % of Rated A | 27.55% | 18.43% | 18.41% | 18.39% | 18.38%
FN | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1
FN | 3MO1_Mossman No 1 66 kV | Loading (A) | 3637% | 4017% | 4013% | 4010% | 4007%
FN | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 454% | 491.1% | 491.1% | 491.1% | 491.1%
FN | 3MO1_Mossman No 1 66 kV | Loading (MW) | 260.2% | 491.1% | 491.1% | 491.1% | 491.1%
FN | 3MO1_Mossman No 1 66 kV | Power Factor | 57.31% | 100% | 100% | 100% | 100%
FN | 3MO1_Mossman No 1 66 kV | Rating (A) | 13200% | 21800% | 21800% | 21800% | 21800%
FN | 3MO1_Mossman No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3MO1_Mossman No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 109.2% | 106.9% | 107% | 107.1% | 107.2%
FN | 3MO2_Mossman No 2 66 kV | % of Rated A | 26.89% | 6.807% | 7.131% | 7.51% | 7.873%
FN | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 88171_2(1) | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN | 3MO2_Mossman No 2 66 kV | Loading (A) | 4545% | 1150% | 1205% | 1269% | 1331%
FN | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 564.2% | 143.9% | 151% | 159.2% | 167.1%
FN | 3MO2_Mossman No 2 66 kV | Loading (MW) | 250.4% | 58.02% | 73.28% | 88.6% | 101.8%
FN | 3MO2_Mossman No 2 66 kV | Power Factor | 44.38% | 40.32% | 48.54% | 55.65% | 60.93%
FN | 3MO2_Mossman No 2 66 kV | Rating (A) | 16900% | 16900% | 16900% | 16900% | 16900%
FN | 3MO2_Mossman No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3MO2_Mossman No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 108.6% | 109.4% | 109.6% | 109.7% | 109.9%
FN | 3MTG_Mt Garnet 66 kV | % of Rated A | 6.4% | 3.056% | 3.022% | 3.034% | 3.082%
FN | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 169447_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1
FN | 3MTG_Mt Garnet 66 kV | Loading (A) | 1082% | 1155% | 1142% | 1147% | 1165%
FN | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 135% | 140.9% | 139.5% | 140.2% | 142.6%
FN | 3MTG_Mt Garnet 66 kV | Loading (MW) | 78.83% | 23.89% | 7.094% | 10.72% | 26.48%
FN | 3MTG_Mt Garnet 66 kV | Power Factor | 58.4% | 16.96% | 5.087% | 7.621% | 18.54%
FN | 3MTG_Mt Garnet 66 kV | Rating (A) | 16900% | 37800% | 37800% | 37800% | 37800%
FN | 3MTG_Mt Garnet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3MTG_Mt Garnet 66 kV | Min Voltage at Constrained Conductor (pu) | 109.2% | 106.7% | 106.8% | 106.9% | 107.1%
FN | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 2.245% | 60.46% | 63.17% | 66.01% | 68.47%
FN | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 178964_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 379.3% | 7981% | 8338% | 8714% | 9037%
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 47.35% | 1003% | 1050% | 1098% | 1140%
FN | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 24.18% | 593.5% | 671.3% | 747.9% | 810.9%
FN | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 51.07% | 59.12% | 63.93% | 68.07% | 71.09%
FN | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 16900% | 13200% | 13200% | 13200% | 13200%
FN | 3RA1_Ravenshoe No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 3RA1_Ravenshoe No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 109.2% | 110% | 110.1% | 110.2% | 110.4%
FN | 7200_Craiglie No 2 132 kV | % of Rated A | 9.093% | 50.82% | 52.95% | 55.21% | 57.18%
FN | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1) | TR_LINE 88171_2(1)
FN | 7200_Craiglie No 2 132 kV | Loading (A) | 4110% | 8589% | 8949% | 9331% | 9663%
FN | 7200_Craiglie No 2 132 kV | Loading (MVA) | 1039% | 1066% | 1111% | 1160% | 1202%
FN | 7200_Craiglie No 2 132 kV | Loading (MW) | 37.92% | 597.9% | 679.8% | 760.6% | 826.9%
FN | 7200_Craiglie No 2 132 kV | Power Factor | 3.649% | 56.1% | 61.16% | 65.58% | 68.8%
FN | 7200_Craiglie No 2 132 kV | Rating (A) | 45200% | 16900% | 16900% | 16900% | 16900%
FN | 7200_Craiglie No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7200_Craiglie No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 110.6% | 108.5% | 108.6% | 108.7% | 108.8%
FN | 7201_Craiglie No 1 132 kV | % of Rated A | 9.077% | 7.197% | 7.165% | 7.246% | 7.403%
FN | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 3957_2 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1
FN | 7201_Craiglie No 1 132 kV | Loading (A) | 4103% | 1216% | 1211% | 1225% | 1251%
FN | 7201_Craiglie No 1 132 kV | Loading (MVA) | 1037% | 152.1% | 151.7% | 153.6% | 157.2%
FN | 7201_Craiglie No 1 132 kV | Loading (MW) | 36.61% | 16.78% | 2.367% | 21.74% | 38.41%
FN | 7201_Craiglie No 1 132 kV | Power Factor | 3.53% | 11.03% | 1.457% | 14.04% | 24.33%
FN | 7201_Craiglie No 1 132 kV | Rating (A) | 45200% | 16900% | 16900% | 16900% | 16900%
FN | 7201_Craiglie No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7201_Craiglie No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 110.6% | 109.4% | 109.6% | 109.7% | 109.9%
FN | 7285_4LAK (Lakeland) 132kV | % of Rated A | 8.036% | 6.437% | 6.578% | 6.744% | 6.906%
FN | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1
FN | 7285_4LAK (Lakeland) 132kV | Loading (A) | 4082% | 1088% | 1112% | 1140% | 1167%
FN | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 1041% | 136.1% | 139.3% | 143% | 146.6%
FN | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 37.85% | 34.35% | 44.3% | 54.1% | 62.48%
FN | 7285_4LAK (Lakeland) 132kV | Power Factor | 3.635% | 25.24% | 31.81% | 37.84% | 42.62%
FN | 7285_4LAK (Lakeland) 132kV | Rating (A) | 50800% | 16900% | 16900% | 16900% | 16900%
FN | 7285_4LAK (Lakeland) 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | 7285_4LAK (Lakeland) 132kV | Min Voltage at Constrained Conductor (pu) | 111.6% | 109.4% | 109.6% | 109.7% | 109.9%
FN | MOSS_7496 | % of Rated A | 2.113% | 15.58% | 15.62% | 15.71% | 15.82%
FN | MOSS_7496 | Limiting Line Name | TR_LINE 38738_a | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN | MOSS_7496 | Loading (A) | 800.8% | 7044% | 7060% | 7099% | 7149%
FN | MOSS_7496 | Loading (MVA) | 204.2% | 1783% | 1788% | 1800% | 1813%
FN | MOSS_7496 | Loading (MW) | 64.49% | 1.401% | 73.07% | 175.6% | 262.2%
FN | MOSS_7496 | Power Factor | 31.58% | 0.02601% | 4.033% | 9.702% | 14.41%
FN | MOSS_7496 | Rating (A) | 37900% | 45200% | 45200% | 45200% | 45200%
FN | MOSS_7496 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN | MOSS_7496 | Min Voltage at Constrained Conductor (pu) | 111.5% | 110.7% | 110.8% | 110.9% | 111%
MK | 231_Carmila 33 kV | % of Rated A | 5.68% | 13.68% | 13.72% | 13.81% | 13.93%
MK | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 211924_1 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
MK | 231_Carmila 33 kV | Loading (A) | 1096% | 6183% | 6201% | 6244% | 6297%
MK | 231_Carmila 33 kV | Loading (MVA) | 65.79% | 1565% | 1570% | 1583% | 1597%
MK | 231_Carmila 33 kV | Loading (MW) | 54.41% | 1.789% | 75.32% | 177.8% | 264.4%
MK | 231_Carmila 33 kV | Power Factor | 82.69% | 0.1133% | 4.795% | 11.23% | 16.55%
MK | 231_Carmila 33 kV | Rating (A) | 19300% | 45200% | 45200% | 45200% | 45200%
MK | 231_Carmila 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 231_Carmila 33 kV | Min Voltage at Constrained Conductor (pu) | 105% | 110.7% | 110.8% | 110.9% | 110.9%
MK | 3045_Sarina No 1 33 kV | % of Rated A | 27.33% | 8.107% | 8.118% | 8.125% | 8.132%
MK | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 12173_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
MK | 3045_Sarina No 1 33 kV | Loading (A) | 8173% | 4118% | 4124% | 4127% | 4131%
MK | 3045_Sarina No 1 33 kV | Loading (MVA) | 506.3% | 1060% | 1062% | 1064% | 1067%
MK | 3045_Sarina No 1 33 kV | Loading (MW) | 171.6% | 43.59% | 49.42% | 27.72% | 8.724%
MK | 3045_Sarina No 1 33 kV | Power Factor | 33.88% | 4.114% | 4.653% | 2.604% | 0.8089%
MK | 3045_Sarina No 1 33 kV | Rating (A) | 29900% | 50800% | 50800% | 50800% | 50800%
MK | 3045_Sarina No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 3045_Sarina No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 108.4% | 112.5% | 112.7% | 112.8% | 112.9%
MK | 3046_Rosella 33 kV | % of Rated A | 0.3353% | 2.55% | 2.836% | 3.171% | 3.555%
MK | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 6962_1 | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a
MK | 3046_Rosella 33 kV | Loading (A) | 137.1% | 966.6% | 1075% | 1202% | 1347%
MK | 3046_Rosella 33 kV | Loading (MVA) | 8.205% | 246.8% | 274.7% | 307.5% | 346.9%
MK | 3046_Rosella 33 kV | Loading (MW) | 3.275% | 136.1% | 181.8% | 228.4% | 283%
MK | 3046_Rosella 33 kV | Power Factor | 39.55% | 55.15% | 66.17% | 74.25% | 81.59%
MK | 3046_Rosella 33 kV | Rating (A) | 40900% | 37900% | 37900% | 37900% | 37900%
MK | 3046_Rosella 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 3046_Rosella 33 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 111.7% | 111.8% | 111.9% | 112.6%
MK | 3047_Sarina No 2 33 kV | % of Rated A | 9.27% | 5.672% | 5.664% | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 211924_1 | TR_LINE 211924_1 | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Loading (A) | 3523% | 1095% | 1093% | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Loading (MVA) | 212.1% | 65.8% | 65.8% | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Loading (MW) | 210.3% | 54.41% | 54.41% | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Power Factor | 99.16% | 82.69% | 82.68% | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Rating (A) | 38000% | 19300% | 19300% | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 0% | 0%
MK | 3047_Sarina No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.2% | 105.3% | 0% | 0%
MK | 3053_Mt Bassett 33 kV | % of Rated A | 4.542% | 27.78% | 28.08% | 28.39% | 28.66%
MK | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1
MK | 3053_Mt Bassett 33 kV | Loading (A) | 1067% | 8307% | 8397% | 8488% | 8570%
MK | 3053_Mt Bassett 33 kV | Loading (MVA) | 64.28% | 518.8% | 524.8% | 530.7% | 536.1%
MK | 3053_Mt Bassett 33 kV | Loading (MW) | 62.77% | 186.8% | 201.5% | 215.8% | 228%
MK | 3053_Mt Bassett 33 kV | Power Factor | 97.61% | 35.98% | 38.37% | 40.65% | 42.51%
MK | 3053_Mt Bassett 33 kV | Rating (A) | 23500% | 29900% | 29900% | 29900% | 29900%
MK | 3053_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 3053_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 105.4% | 109.2% | 109.3% | 109.4% | 109.4%
MK | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.319% | 48.75% | 48.77% | 48.94% | 49.11%
MK | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1
MK | 340_MK3-1 Farleigh 33 kV | Loading (A) | 398.8% | 19941% | 19946% | 20015% | 20084%
MK | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 24.41% | 1202% | 1202% | 1207% | 1211%
MK | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.4485% | 66.52% | 17.63% | 33.5% | 72.18%
MK | 340_MK3-1 Farleigh 33 kV | Power Factor | 1.837% | 5.531% | 1.458% | 2.767% | 5.95%
MK | 340_MK3-1 Farleigh 33 kV | Rating (A) | 17200% | 40900% | 40900% | 40900% | 40900%
MK | 340_MK3-1 Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 340_MK3-1 Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 107.1% | 105.5% | 105.5% | 105.5% | 105.5%
MK | 341_Tennyson St No 2 33 kV | % of Rated A | 11.53% | 17.93% | 19.88% | 0.1277% | 0.1277%
MK | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 253_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11141_1 | TR_LINE 11141_1
MK | 341_Tennyson St No 2 33 kV | Loading (A) | 4036% | 6812% | 7553% | 91.44% | 91.44%
MK | 341_Tennyson St No 2 33 kV | Loading (MVA) | 242.9% | 410.3% | 455.3% | 5.513% | 5.513%
MK | 341_Tennyson St No 2 33 kV | Loading (MW) | 47.96% | 409.9% | 454.9% | 0.0002726% | 0.0002727%
MK | 341_Tennyson St No 2 33 kV | Power Factor | 19.57% | 99.91% | 99.91% | 0.004942% | 0.004943%
MK | 341_Tennyson St No 2 33 kV | Rating (A) | 35000% | 38000% | 38000% | 71600% | 71600%
MK | 341_Tennyson St No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 341_Tennyson St No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.3% | 105.4% | 105.5% | 105.5%
MK | 342_South Mackay 33 kV | % of Rated A | 40.16% | 16.75% | 19.64% | 22.71% | 25.28%
MK | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12106200_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK | 342_South Mackay 33 kV | Loading (A) | 18797% | 3936% | 4614% | 5337% | 5941%
MK | 342_South Mackay 33 kV | Loading (MVA) | 1133% | 237.8% | 279% | 323% | 359.7%
MK | 342_South Mackay 33 kV | Loading (MW) | 82.52% | 237.7% | 278.9% | 322.9% | 359.7%
MK | 342_South Mackay 33 kV | Power Factor | 7.276% | 100% | 99.99% | 99.99% | 99.99%
MK | 342_South Mackay 33 kV | Rating (A) | 46800% | 23500% | 23500% | 23500% | 23500%
MK | 342_South Mackay 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 342_South Mackay 33 kV | Min Voltage at Constrained Conductor (pu) | 105.4% | 105.5% | 105.6% | 105.7% | 105.7%
MK | 343_Pleystowe 33 kV | % of Rated A | 20.38% | 2.353% | 2.358% | 2.362% | 2.365%
MK | 343_Pleystowe 33 kV | Limiting Line Name | TR_LINE 114413_2 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1
MK | 343_Pleystowe 33 kV | Loading (A) | 4485% | 404.8% | 405.5% | 406.3% | 406.9%
MK | 343_Pleystowe 33 kV | Loading (MVA) | 269.9% | 25.14% | 25.24% | 25.33% | 25.4%
MK | 343_Pleystowe 33 kV | Loading (MW) | 268.8% | 0.462% | 0.4637% | 0.4654% | 0.4668%
MK | 343_Pleystowe 33 kV | Power Factor | 99.58% | 1.837% | 1.837% | 1.837% | 1.837%
MK | 343_Pleystowe 33 kV | Rating (A) | 22000% | 17200% | 17200% | 17200% | 17200%
MK | 343_Pleystowe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 343_Pleystowe 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 108.7% | 108.9% | 109.1% | 109.2%
MK | 344_West Mackay 2 33 kV | % of Rated A | 0.6314% | 17.48% | 17.98% | 18.73% | 19.53%
MK | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1
MK | 344_West Mackay 2 33 kV | Loading (A) | 394.6% | 6118% | 6294% | 6555% | 6836%
MK | 344_West Mackay 2 33 kV | Loading (MVA) | 23.75% | 368.1% | 378.8% | 394.6% | 411.6%
MK | 344_West Mackay 2 33 kV | Loading (MW) | 23.34% | 99.6% | 140.4% | 184.1% | 222.2%
MK | 344_West Mackay 2 33 kV | Power Factor | 98.3% | 26.93% | 36.93% | 46.52% | 53.86%
MK | 344_West Mackay 2 33 kV | Rating (A) | 62500% | 35000% | 35000% | 35000% | 35000%
MK | 344_West Mackay 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 344_West Mackay 2 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.3% | 105.3% | 105.3% | 105.3%
MK | 346_Ritchies Rd 33 kV | % of Rated A | 15.21% | 40.39% | 40.11% | 40.15% | 40.19%
MK | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11501_1 | TR_LINE 12106200_1 | TR_LINE 12106200_1 | TR_LINE 12106200_1 | TR_LINE 12106200_1
MK | 346_Ritchies Rd 33 kV | Loading (A) | 3346% | 18901% | 18773% | 18790% | 18809%
MK | 346_Ritchies Rd 33 kV | Loading (MVA) | 201.4% | 1139% | 1132% | 1134% | 1135%
MK | 346_Ritchies Rd 33 kV | Loading (MW) | 200.7% | 21.49% | 12.66% | 20.96% | 44.25%
MK | 346_Ritchies Rd 33 kV | Power Factor | 99.65% | 1.876% | 1.108% | 1.84% | 3.889%
MK | 346_Ritchies Rd 33 kV | Rating (A) | 22000% | 46800% | 46800% | 46800% | 46800%
MK | 346_Ritchies Rd 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 346_Ritchies Rd 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.5% | 105.5% | 105.5% | 105.5%
MK | 347_Mt Bassett 33 kV | % of Rated A | 8.745% | 37.74% | 40.05% | 42.22% | 43.97%
MK | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 4883_1 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 11839_1
MK | 347_Mt Bassett 33 kV | Loading (A) | 2230% | 8303% | 8812% | 9288% | 9673%
MK | 347_Mt Bassett 33 kV | Loading (MVA) | 134.3% | 499.8% | 530.5% | 559.4% | 583.1%
MK | 347_Mt Bassett 33 kV | Loading (MW) | 133.6% | 499.4% | 530.2% | 559.2% | 583%
MK | 347_Mt Bassett 33 kV | Power Factor | 99.52% | 99.92% | 99.94% | 99.96% | 99.99%
MK | 347_Mt Bassett 33 kV | Rating (A) | 25500% | 22000% | 22000% | 22000% | 22000%
MK | 347_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 347_Mt Bassett 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.3% | 105.3% | 105.3% | 105.4%
MK | 348_Farleigh 33 kV | % of Rated A | 14.73% | 0.1527% | 0.9646% | 2.028% | 2.88%
MK | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 13162_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK | 348_Farleigh 33 kV | Loading (A) | 2858% | 95.43% | 602.9% | 1267% | 1800%
MK | 348_Farleigh 33 kV | Loading (MVA) | 173.9% | 5.744% | 36.3% | 76.33% | 108.4%
MK | 348_Farleigh 33 kV | Loading (MW) | 172.3% | 3.69% | 36.12% | 76.31% | 108.4%
MK | 348_Farleigh 33 kV | Power Factor | 99.06% | 64.24% | 99.28% | 99.86% | 99.94%
MK | 348_Farleigh 33 kV | Rating (A) | 19400% | 62500% | 62500% | 62500% | 62500%
MK | 348_Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 348_Farleigh 33 kV | Min Voltage at Constrained Conductor (pu) | 106.5% | 105.3% | 105.3% | 105.4% | 105.4%
MK | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 19.32% | 52.72% | 53.59% | 54.48% | 55.26%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 9735_1 | TR_LINE 11706_1 | TR_LINE 11706_1 | TR_LINE 11706_1 | TR_LINE 11706_1
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 4251% | 8910% | 9057% | 9208% | 9339%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 513.2% | 558.5% | 568.6% | 578.9% | 587.8%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 488.9% | 261.2% | 280.3% | 298.9% | 314.7%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 95.25% | 46.67% | 49.21% | 51.56% | 53.47%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 22000% | 16900% | 16900% | 16900% | 16900%
MK | 349_Pioneer Valley - Pinnacle 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 349_Pioneer Valley - Pinnacle 66 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 109.4% | 109.6% | 109.7% | 109.8%
MK | 351_Alligator Creek 33 kV | % of Rated A | 0.3218% | 15.46% | 18.12% | 20.96% | 23.33%
MK | 351_Alligator Creek 33 kV | Limiting Line Name | TR_LINE 66244_3 | TR_CABLE 22_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK | 351_Alligator Creek 33 kV | Loading (A) | 82.06% | 3942% | 4620% | 5345% | 5950%
MK | 351_Alligator Creek 33 kV | Loading (MVA) | 5.008% | 237.4% | 278.4% | 322.2% | 358.9%
MK | 351_Alligator Creek 33 kV | Loading (MW) | 3.275% | 237% | 278.4% | 322.2% | 358.8%
MK | 351_Alligator Creek 33 kV | Power Factor | 65.4% | 99.81% | 100% | 99.99% | 99.99%
MK | 351_Alligator Creek 33 kV | Rating (A) | 25500% | 25500% | 25500% | 25500% | 25500%
MK | 351_Alligator Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 351_Alligator Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 106.8% | 105.4% | 105.4% | 105.5% | 105.5%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 6.614% | 16% | 17.08% | 18.08% | 18.9%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 10229_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 608.5% | 3104% | 3313% | 3508% | 3667%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 74.1% | 187.1% | 199.8% | 211.8% | 221.5%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 39.68% | 185.7% | 198.7% | 210.8% | 220.6%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 53.55% | 99.28% | 99.41% | 99.51% | 99.58%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 9200% | 19400% | 19400% | 19400% | 19400%
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Min Voltage at Constrained Conductor (pu) | 106.5% | 105.4% | 105.5% | 105.6% | 105.7%
MK | 364_West Mackay No 1 33 kV | % of Rated A | 1.333% | 21.17% | 22.17% | 23.13% | 23.94%
MK | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11500_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1
MK | 364_West Mackay No 1 33 kV | Loading (A) | 386.4% | 4658% | 4878% | 5088% | 5267%
MK | 364_West Mackay No 1 33 kV | Loading (MVA) | 23.25% | 565.4% | 592% | 617.5% | 639.1%
MK | 364_West Mackay No 1 33 kV | Loading (MW) | 23.25% | 557.7% | 584.8% | 610.9% | 632.9%
MK | 364_West Mackay No 1 33 kV | Power Factor | 100% | 98.63% | 98.79% | 98.93% | 99.03%
MK | 364_West Mackay No 1 33 kV | Rating (A) | 29000% | 22000% | 22000% | 22000% | 22000%
MK | 364_West Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 364_West Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 106.2% | 106.2% | 106.2% | 106.1%
MK | 365_Tennyson St No 1 33 kV | % of Rated A | 1.455% | 84.72% | 84.82% | 85% | 85.16%
MK | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_CABLE 7286_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK | 365_Tennyson St No 1 33 kV | Loading (A) | 967.4% | 19824% | 19848% | 19890% | 19926%
MK | 365_Tennyson St No 1 33 kV | Loading (MVA) | 58.21% | 1251% | 1254% | 1258% | 1262%
MK | 365_Tennyson St No 1 33 kV | Loading (MW) | 13.67% | 51.96% | 19.01% | 14.54% | 37.79%
MK | 365_Tennyson St No 1 33 kV | Power Factor | 23.49% | 4.151% | 1.511% | 1.148% | 2.987%
MK | 365_Tennyson St No 1 33 kV | Rating (A) | 66500% | 23400% | 23400% | 23400% | 23400%
MK | 365_Tennyson St No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 365_Tennyson St No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 110.4% | 110.5% | 110.7% | 110.8%
MK | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.06496% | 6.538% | 6.443% | 6.345% | 6.258%
MK | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 16.37% | 601.5% | 592.7% | 583.8% | 575.7%
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 1.977% | 73.7% | 72.65% | 71.58% | 70.61%
MK | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.045e-06% | 37.61% | 35.44% | 33.14% | 30.97%
MK | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 0.000407% | 51.02% | 48.79% | 46.29% | 43.86%
MK | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 25200% | 9200% | 9200% | 9200% | 9200%
MK | 367_Pioneer Valley - Greenmount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 367_Pioneer Valley - Greenmount 66 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 107.2% | 107.2% | 107.3% | 107.3%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 7.45% | 0.2064% | 2.069% | 4.369% | 6.207%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 9963_1 | TR_LINE 11500_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 1453% | 59.85% | 600% | 1267% | 1800%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 175.6% | 3.603% | 36.12% | 76.31% | 108.4%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 175.3% | 3.602% | 36.12% | 76.31% | 108.4%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 99.8% | 99.98% | 100% | 100% | 100%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 19500% | 29000% | 29000% | 29000% | 29000%
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 372_Pioneer Valley-McKinley Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 105.3% | 105.3% | 105.4% | 105.4%
MK | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 18.85% | 2.175% | 2.251% | 2.365% | 2.535%
MK | 387_Mackay-Alfred Street 1 33 kV | Limiting Line Name | TR_CABLE 2967_1 | TR_LINE 11727_1 | TR_LINE 11727_1 | TR_LINE 11727_1 | TR_LINE 11727_1
MK | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 8125% | 1447% | 1497% | 1572% | 1686%
MK | 387_Mackay-Alfred Street 1 33 kV | Loading (MVA) | 488.9% | 87.04% | 90.08% | 94.64% | 101.5%
MK | 387_Mackay-Alfred Street 1 33 kV | Loading (MW) | 20.2% | 15.95% | 6.657% | 17.16% | 27.63%
MK | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 3.864% | 18.32% | 7.39% | 18.13% | 27.23%
MK | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 43100% | 66500% | 66500% | 66500% | 66500%
MK | 387_Mackay-Alfred Street 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 387_Mackay-Alfred Street 1 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.3% | 105.3% | 105.3% | 105.3%
MK | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 5.94% | 0.06535% | 0.06535% | 0.06535% | 0.06534%
MK | 395_Tennyson Street-Alfred Street 33 kV | Limiting Line Name | TR_CABLE 2960_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 3992% | 16.47% | 16.47% | 16.47% | 16.47%
MK | 395_Tennyson Street-Alfred Street 33 kV | Loading (MVA) | 240.3% | 2% | 2% | 2% | 2%
MK | 395_Tennyson Street-Alfred Street 33 kV | Loading (MW) | 110.8% | 8.139e-06% | 8.148e-06% | 8.148e-06% | 8.148e-06%
MK | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 46.11% | 0.0004069% | 0.0004074% | 0.0004074% | 0.0004075%
MK | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 67200% | 25200% | 25200% | 25200% | 25200%
MK | 395_Tennyson Street-Alfred Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 395_Tennyson Street-Alfred Street 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 106.3% | 106.2% | 106.2% | 106.2%
MK | 422_North Mackay No 1 33 kV | % of Rated A | 46.63% | 7.917% | 8.39% | 8.845% | 9.227%
MK | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11650_2 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1
MK | 422_North Mackay No 1 33 kV | Loading (A) | 17111% | 1544% | 1636% | 1725% | 1799%
MK | 422_North Mackay No 1 33 kV | Loading (MVA) | 1041% | 186.9% | 198.1% | 208.8% | 217.8%
MK | 422_North Mackay No 1 33 kV | Loading (MW) | 1040% | 186.7% | 197.9% | 208.7% | 217.7%
MK | 422_North Mackay No 1 33 kV | Power Factor | 99.94% | 99.83% | 99.86% | 99.88% | 99.9%
MK | 422_North Mackay No 1 33 kV | Rating (A) | 36700% | 19500% | 19500% | 19500% | 19500%
MK | 422_North Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 422_North Mackay No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 106.4% | 105.9% | 105.9% | 105.9% | 105.9%
MK | 423_North Mackay No 2 33 kV | % of Rated A | 20.57% | 68.46% | 72.65% | 76.78% | 80.1%
MK | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 6563_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1
MK | 423_North Mackay No 2 33 kV | Loading (A) | 12590% | 42790% | 45408% | 47989% | 50064%
MK | 423_North Mackay No 2 33 kV | Loading (MVA) | 757.7% | 2579% | 2735% | 2889% | 3012%
MK | 423_North Mackay No 2 33 kV | Loading (MW) | 634.9% | 2471% | 2640% | 2805% | 2936%
MK | 423_North Mackay No 2 33 kV | Power Factor | 83.78% | 95.82% | 96.53% | 97.1% | 97.49%
MK | 423_North Mackay No 2 33 kV | Rating (A) | 61200% | 62500% | 62500% | 62500% | 62500%
MK | 423_North Mackay No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 423_North Mackay No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.4% | 105.3% | 105.3% | 105.2%
MK | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 13.68% | 34.94% | 36.41% | 37.83% | 38.99%
MK | 430_Mackay-Alfred Street 2 33 kV | Limiting Line Name | TR_CABLE 8887_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1 | TR_CABLE 7847_1
MK | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 7921% | 26590% | 27707% | 28787% | 29674%
MK | 430_Mackay-Alfred Street 2 33 kV | Loading (MVA) | 476.6% | 1597% | 1664% | 1729% | 1782%
MK | 430_Mackay-Alfred Street 2 33 kV | Loading (MW) | 18.42% | 1353% | 1439% | 1520% | 1585%
MK | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 3.845% | 84.69% | 86.41% | 87.86% | 88.91%
MK | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 57900% | 76100% | 76100% | 76100% | 76100%
MK | 430_Mackay-Alfred Street 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 430_Mackay-Alfred Street 2 33 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.1% | 105.1% | 105.1% | 105.1%
MK | PV 6/4_Glenella No 2 66 kV | % of Rated A | 9.987% | 28.89% | 30.79% | 32.65% | 34.14%
MK | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1
MK | PV 6/4_Glenella No 2 66 kV | Loading (A) | 8080% | 23375% | 24910% | 26417% | 27620%
MK | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 975.5% | 2838% | 3023% | 3206% | 3351%
MK | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 886.5% | 2754% | 2955% | 3151% | 3305%
MK | PV 6/4_Glenella No 2 66 kV | Power Factor | 90.88% | 97.05% | 97.74% | 98.28% | 98.63%
MK | PV 6/4_Glenella No 2 66 kV | Rating (A) | 80900% | 80900% | 80900% | 80900% | 80900%
MK | PV 6/4_Glenella No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | PV 6/4_Glenella No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 106.2% | 106.2% | 106.2% | 106.1%
MK | PV 6/5_Glenella No 1 66 kV | % of Rated A | 17.5% | 28.88% | 30.79% | 32.67% | 34.16%
MK | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1
MK | PV 6/5_Glenella No 1 66 kV | Loading (A) | 14161% | 23366% | 24911% | 26427% | 27637%
MK | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 1723% | 2881% | 3072% | 3259% | 3408%
MK | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 1677% | 2781% | 2986% | 3185% | 3343%
MK | PV 6/5_Glenella No 1 66 kV | Power Factor | 97.33% | 96.53% | 97.2% | 97.74% | 98.1%
MK | PV 6/5_Glenella No 1 66 kV | Rating (A) | 80900% | 80900% | 80900% | 80900% | 80900%
MK | PV 6/5_Glenella No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | PV 6/5_Glenella No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 106.4% | 107.8% | 107.9% | 107.9% | 107.9%
MK | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 2.213% | 2.211% | 2.207% | 2.192% | 2.174%
MK | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1
MK | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 854.1% | 853.5% | 852% | 845.9% | 839.2%
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 102.5% | 102.3% | 102.1% | 101.4% | 100.6%
MK | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 102.4% | 102.2% | 102% | 101.3% | 100.5%
MK | 6328_Broadlea - Moorvale 66 kV | Power Factor | 99.93% | 99.93% | 99.93% | 99.93% | 99.93%
MK | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 38600% | 38600% | 38600% | 38600% | 38600%
MK | 6328_Broadlea - Moorvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 6328_Broadlea - Moorvale 66 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 104.8% | 104.8% | 104.8% | 104.8%
MK | 6329_Broadlea - Coppabella 66 kV | % of Rated A | 24.91% | 24.95% | 24.95% | 24.94% | 24.94%
MK | 6329_Broadlea - Coppabella 66 kV | Limiting Line Name | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1 | TR_LINE 183854_1
MK | 6329_Broadlea - Coppabella 66 kV | Loading (A) | 9614% | 9630% | 9629% | 9629% | 9628%
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MVA) | 1150% | 1150% | 1150% | 1150% | 1150%
MK | 6329_Broadlea - Coppabella 66 kV | Loading (MW) | 1150% | 1150% | 1150% | 1150% | 1150%
MK | 6329_Broadlea - Coppabella 66 kV | Power Factor | 99.98% | 99.98% | 99.98% | 99.98% | 99.98%
MK | 6329_Broadlea - Coppabella 66 kV | Rating (A) | 38600% | 38600% | 38600% | 38600% | 38600%
MK | 6329_Broadlea - Coppabella 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 6329_Broadlea - Coppabella 66 kV | Min Voltage at Constrained Conductor (pu) | 103.3% | 103.1% | 103.1% | 103.1% | 103.1%
MK | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 40.96% | 40.96% | 40.96% | 40.95% | 40.94%
MK | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 28878% | 28878% | 28875% | 28871% | 28866%
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 6858% | 6858% | 6857% | 6857% | 6856%
MK | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 6852% | 6852% | 6852% | 6851% | 6850%
MK | 7366_Moranbah - Broadlea 132 kV | Power Factor | 99.92% | 99.92% | 99.92% | 99.92% | 99.92%
MK | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 70500% | 70500% | 70500% | 70500% | 70500%
MK | 7366_Moranbah - Broadlea 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 7366_Moranbah - Broadlea 132 kV | Min Voltage at Constrained Conductor (pu) | 103.9% | 103.9% | 103.9% | 103.9% | 103.9%
MK | 232_Newlands-Glenden 66 kV | % of Rated A | 2.383% | 2.379% | 2.366% | 2.342% | 2.324%
MK | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1
MK | 232_Newlands-Glenden 66 kV | Loading (A) | 276.4% | 276% | 274.4% | 271.7% | 269.5%
MK | 232_Newlands-Glenden 66 kV | Loading (MVA) | 32.95% | 33.21% | 33.03% | 32.7% | 32.44%
MK | 232_Newlands-Glenden 66 kV | Loading (MW) | 15.88% | 15.39% | 14.98% | 14.23% | 13.61%
MK | 232_Newlands-Glenden 66 kV | Power Factor | 48.19% | 46.33% | 45.36% | 43.51% | 41.95%
MK | 232_Newlands-Glenden 66 kV | Rating (A) | 11600% | 11600% | 11600% | 11600% | 11600%
MK | 232_Newlands-Glenden 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | 232_Newlands-Glenden 66 kV | Min Voltage at Constrained Conductor (pu) | 104.3% | 105.3% | 105.3% | 105.3% | 105.3%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 42.73% | 42.73% | 42.72% | 42.71% | 42.7%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 8033% | 8034% | 8031% | 8029% | 8027%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 957.6% | 957.3% | 957.1% | 956.8% | 956.6%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 951.2% | 950.9% | 950.7% | 950.5% | 950.3%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 99.33% | 99.34% | 99.33% | 99.33% | 99.33%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 18800% | 18800% | 18800% | 18800% | 18800%
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK | NL-WR-1_Newlands-Wirralie 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.3% | 104.2% | 104.2% | 104.2% | 104.2%
NQ | 2021_Collinsville PS-Collinsville 33 kV | % of Rated A | 7.17% | 4.519% | 4.793% | 5.062% | 5.323%
NQ | 2021_Collinsville PS-Collinsville 33 kV | Limiting Line Name | TR_CABLE 4176_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1
NQ | 2021_Collinsville PS-Collinsville 33 kV | Loading (A) | 4969% | 899.3% | 953.9% | 1007% | 1059%
NQ | 2021_Collinsville PS-Collinsville 33 kV | Loading (MVA) | 292% | 107.1% | 113.6% | 120% | 125.6%
NQ | 2021_Collinsville PS-Collinsville 33 kV | Loading (MW) | 284.9% | 102.3% | 109.1% | 115.8% | 121.6%
NQ | 2021_Collinsville PS-Collinsville 33 kV | Power Factor | 97.55% | 95.49% | 96.03% | 96.48% | 96.87%
NQ | 2021_Collinsville PS-Collinsville 33 kV | Rating (A) | 69300% | 19900% | 19900% | 19900% | 19900%
NQ | 2021_Collinsville PS-Collinsville 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 2021_Collinsville PS-Collinsville 33 kV | Min Voltage at Constrained Conductor (pu) | 102.8% | 104.2% | 104.2% | 104.2% | 103.7%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | % of Rated A | 14.06% | 1.657% | 1.82% | 1.987% | 2.158%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Limiting Line Name | TR_CABLE 4177_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Loading (A) | 9745% | 222.1% | 243.9% | 266.3% | 289.1%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MVA) | 572.7% | 26.55% | 29.16% | 31.84% | 34.45%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MW) | 572% | 21.78% | 24.91% | 28.01% | 31.01%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Power Factor | 99.86% | 82.05% | 85.43% | 87.97% | 90%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Rating (A) | 69300% | 13400% | 13400% | 13400% | 13400%
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 2031 Collinsville-PS-Collinsville 33 kV | Min Voltage at Constrained Conductor (pu) | 102.8% | 104.6% | 104.6% | 104.6% | 104.2%
NQ | 6321_Lucinda 66 kV | % of Rated A | 4.219% | 32.23% | 32.23% | 32.22% | 32.23%
NQ | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 135526_1 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2
NQ | 6321_Lucinda 66 kV | Loading (A) | 839.6% | 6413% | 6413% | 6413% | 6413%
NQ | 6321_Lucinda 66 kV | Loading (MVA) | 100.1% | 774.1% | 774.1% | 774.1% | 774.1%
NQ | 6321_Lucinda 66 kV | Loading (MW) | 94.82% | 774.1% | 774.1% | 774.1% | 774.1%
NQ | 6321_Lucinda 66 kV | Power Factor | 94.76% | 100% | 100% | 100% | 100%
NQ | 6321_Lucinda 66 kV | Rating (A) | 19900% | 19900% | 19900% | 19900% | 19900%
NQ | 6321_Lucinda 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6321_Lucinda 66 kV | Min Voltage at Constrained Conductor (pu) | 104.3% | 105.6% | 105.6% | 105.6% | 105.6%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 22.93% | 54.25% | 55.02% | 55.95% | 56.84%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1 | TR_LINE 12744_1
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 1582% | 10470% | 10618% | 10798% | 10971%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 190.1% | 1260% | 1279% | 1301% | 1323%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 3.553% | 274.6% | 345.5% | 418.8% | 481%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 1.868% | 21.78% | 27% | 32.17% | 36.35%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 6900% | 19300% | 19300% | 19300% | 19300%
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | IN-GR_Ingham-Black River/Greenvale 66 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 105.3% | 105.4% | 105.4% | 105.5%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 1.514% | 57.78% | 58.3% | 59.09% | 59.94%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 31685_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 295.3% | 10689% | 10785% | 10931% | 11088%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 35.35% | 1284% | 1297% | 1316% | 1336%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 18.55% | 98.46% | 189.1% | 282.1% | 360.2%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 52.48% | 7.587% | 14.5% | 21.36% | 26.89%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 19500% | 18500% | 18500% | 18500% | 18500%
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | IN-LA-1_Ingham-Lannercost No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 105.1% | 105.2% | 105.3% | 105.3%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 28.52% | 17.4% | 18.48% | 19.55% | 22.22%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 31692_2 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 5676% | 2297% | 2440% | 2580% | 2933%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 679.5% | 274% | 291.2% | 308.2% | 351.4%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 678.4% | 251% | 269.7% | 288% | 334%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 99.83% | 91.58% | 92.61% | 93.46% | 95.05%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 19900% | 13200% | 13200% | 13200% | 13200%
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | IN-VC-1_Ingham-Victoria No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 104.4% | 104.4% | 104.5% | 104.8%
NQ | 118_Cannonvale No 2 66 kV | % of Rated A | 28.64% | 6.359% | 6.351% | 6.343% | 6.396%
NQ | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_CABLE 7280_1 | HV_CABLE 41068222_1 | HV_CABLE 41068222_1 | HV_CABLE 41068222_1 | HV_CABLE 41068222_1
NQ | 118_Cannonvale No 2 66 kV | Loading (A) | 5527% | 1749% | 1747% | 1744% | 1759%
NQ | 118_Cannonvale No 2 66 kV | Loading (MVA) | 661.1% | 68.77% | 68.77% | 68.77% | 69.6%
NQ | 118_Cannonvale No 2 66 kV | Loading (MW) | 33.05% | 68.65% | 68.65% | 68.65% | 69.48%
NQ | 118_Cannonvale No 2 66 kV | Power Factor | 4.999% | 99.83% | 99.82% | 99.82% | 99.83%
NQ | 118_Cannonvale No 2 66 kV | Rating (A) | 19300% | 27500% | 27500% | 27500% | 27500%
NQ | 118_Cannonvale No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 118_Cannonvale No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 103.2% | 103.3% | 103.5% | 103.8%
NQ | 119_Cannonvale No 1 66 kV | % of Rated A | 29.8% | 10.33% | 10.28% | 10.25% | 10.78%
NQ | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13015_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1
NQ | 119_Cannonvale No 1 66 kV | Loading (A) | 5514% | 2572% | 2561% | 2551% | 2683%
NQ | 119_Cannonvale No 1 66 kV | Loading (MVA) | 660.6% | 311.3% | 310.4% | 309.7% | 326.9%
NQ | 119_Cannonvale No 1 66 kV | Loading (MW) | 46.02% | 304.6% | 303.6% | 302.8% | 320.4%
NQ | 119_Cannonvale No 1 66 kV | Power Factor | 6.925% | 97.82% | 97.79% | 97.77% | 98%
NQ | 119_Cannonvale No 1 66 kV | Rating (A) | 18500% | 24900% | 24900% | 24900% | 24900%
NQ | 119_Cannonvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 119_Cannonvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.8% | 105.9% | 106% | 106.2% | 106.6%
NQ | 120_Prosperpine - Calen 66 kV | % of Rated A | 16.35% | 7.327% | 6.931% | 6.564% | 6.458%
NQ | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1
NQ | 120_Prosperpine - Calen 66 kV | Loading (A) | 2158% | 2052% | 1941% | 1838% | 1808%
NQ | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 258% | 252.5% | 239.3% | 227.1% | 220.3%
NQ | 120_Prosperpine - Calen 66 kV | Loading (MW) | 233% | 179.7% | 160.2% | 140.8% | 137.5%
NQ | 120_Prosperpine - Calen 66 kV | Power Factor | 90.28% | 71.19% | 66.94% | 61.99% | 62.39%
NQ | 120_Prosperpine - Calen 66 kV | Rating (A) | 13200% | 28000% | 28000% | 28000% | 28000%
NQ | 120_Prosperpine - Calen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 120_Prosperpine - Calen 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 107.7% | 107.9% | 108.1% | 106.6%
NQ | 426_Mt Rooper 66 kV | % of Rated A | 10.35% | 33.71% | 34.9% | 36.16% | 37.28%
NQ | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ | 426_Mt Rooper 66 kV | Loading (A) | 2578% | 6574% | 6805% | 7052% | 7270%
NQ | 426_Mt Rooper 66 kV | Loading (MVA) | 312.6% | 790.6% | 818.6% | 848.5% | 875%
NQ | 426_Mt Rooper 66 kV | Loading (MW) | 305.8% | 501.5% | 545.9% | 591.3% | 630%
NQ | 426_Mt Rooper 66 kV | Power Factor | 97.82% | 63.43% | 66.69% | 69.69% | 72%
NQ | 426_Mt Rooper 66 kV | Rating (A) | 24900% | 19500% | 19500% | 19500% | 19500%
NQ | 426_Mt Rooper 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 426_Mt Rooper 66 kV | Min Voltage at Constrained Conductor (pu) | 106.1% | 105.2% | 105.2% | 105.3% | 105.3%
NQ | CANN_JUPO (Ex119&118) | % of Rated A | 7.774% | 10.53% | 11.19% | 12.23% | 13.11%
NQ | CANN_JUPO (Ex119&118) | Limiting Line Name | TR_CABLE 17_1 | TR_LINE 175214_1 | TR_LINE 175208_1 | TR_LINE 175208_1 | TR_LINE 175208_1
NQ | CANN_JUPO (Ex119&118) | Loading (A) | 2177% | 2032% | 2159% | 2360% | 2531%
NQ | CANN_JUPO (Ex119&118) | Loading (MVA) | 264% | 243.6% | 257.4% | 281.4% | 301.9%
NQ | CANN_JUPO (Ex119&118) | Loading (MW) | 200.1% | 197.1% | 234.3% | 261.9% | 285%
NQ | CANN_JUPO (Ex119&118) | Power Factor | 75.77% | 80.91% | 90.44% | 92.41% | 93.7%
NQ | CANN_JUPO (Ex119&118) | Rating (A) | 28000% | 19300% | 19300% | 19300% | 19300%
NQ | CANN_JUPO (Ex119&118) | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CANN_JUPO (Ex119&118) | Min Voltage at Constrained Conductor (pu) | 106.1% | 104.8% | 104.3% | 104.3% | 104.3%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 19.82% | 64.79% | 64.75% | 64.71% | 68.12%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1 | TR_LINE 9381_1
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 3865% | 12893% | 12885% | 12877% | 13556%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 462.7% | 1523% | 1523% | 1523% | 1605%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 38.62% | 1523% | 1523% | 1523% | 1605%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 8.343% | 100% | 100% | 100% | 100%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 19500% | 19900% | 19900% | 19900% | 19900%
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ME-BN-1_Merinda - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.7% | 102.5% | 102.5% | 102.6% | 102.6%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 7.846% | 9.833% | 10.5% | 11.13% | 11.86%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175214_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 1514% | 1741% | 1858% | 1970% | 2100%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 181.1% | 207.6% | 221.8% | 235.4% | 251.5%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 122.3% | 207.6% | 221.7% | 235.3% | 251.5%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 67.51% | 99.98% | 99.98% | 99.98% | 99.98%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 19300% | 17700% | 17700% | 17700% | 17700%
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ME-PR-1_Merinda - Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 104.4% | 104.4% | 104.5% | 104.8%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 64.71% | 19.65% | 20.97% | 22.24% | 23.75%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 9381_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 12877% | 3478% | 3712% | 3936% | 4204%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 1523% | 414.9% | 443.1% | 470.2% | 503.7%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 1523% | 414.8% | 443% | 470.1% | 503.6%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 100% | 99.98% | 99.98% | 99.98% | 99.98%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 19900% | 17700% | 17700% | 17700% | 17700%
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PR-BN-1_Proserpine - Bowen No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 102.6% | 104.4% | 104.4% | 104.5% | 104.8%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 9.096% | 15.32% | 15.3% | 15.26% | 15.24%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 1610% | 13101% | 13079% | 13050% | 13030%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 192.5% | 5258% | 5233% | 5222% | 5409%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 192.5% | 4289% | 4275% | 4260% | 4293%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 99.99% | 81.57% | 81.69% | 81.58% | 79.36%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 17700% | 85500% | 85500% | 85500% | 85500%
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PROS-KECR-1_Proserpine No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 105.3% | 105% | 105% | 108.9%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 18.17% | 0.9263% | 1.305% | 1.993% | 2.644%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 3217% | 151% | 212.7% | 324.8% | 431%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 384.7% | 18.89% | 24.65% | 37.63% | 49.93%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 384.7% | 5.545% | 19.19% | 34.32% | 47.51%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 99.99% | 29.35% | 77.87% | 91.21% | 95.14%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 17700% | 16300% | 16300% | 16300% | 16300%
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PROS-KECR-2_Proserpine No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 109.4% | 101.3% | 101.3% | 101.4%
NQ | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 15.28% | 17.26% | 17.33% | 17.56% | 17.85%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 3024_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 13069% | 1433% | 1439% | 1458% | 1482%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 5432% | 178.5% | 178.9% | 181.3% | 184.3%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 4301% | 4.318% | 17.94% | 32.98% | 46.06%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 79.18% | 2.412% | 10.02% | 18.18% | 24.98%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 85500% | 8300% | 8300% | 8300% | 8300%
NQ | 7018_Mica Creek C - Chumvale 220 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 7018_Mica Creek C - Chumvale 220 kV | Min Voltage at Constrained Conductor (pu) | 109.1% | 109% | 108.8% | 108.8% | 108.8%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 0.9423% | 3.814% | 4.372% | 4.96% | 5.47%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 34857_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 153.6% | 1464% | 1679% | 1905% | 2100%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 18.5% | 352.5% | 403.7% | 458% | 505.1%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 7.928% | 289.3% | 348.2% | 410.4% | 462.7%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 42.87% | 82.05% | 86.25% | 89.6% | 91.61%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 16300% | 38400% | 38400% | 38400% | 38400%
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CH-CC-1_Chumvale-Cloncurry 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.3% | 105.2% | 105.2% | 105.2%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 15.56% | 5.102% | 5.861% | 6.69% | 7.406%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 1292% | 1423% | 1635% | 1867% | 2066%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 161.8% | 342.7% | 393.2% | 448.8% | 496.9%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.9114% | 289.3% | 348.2% | 410.4% | 462.8%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.5592% | 84.41% | 88.56% | 91.43% | 93.13%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 8300% | 27900% | 27900% | 27900% | 27900%
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Min Voltage at Constrained Conductor (pu) | 109.5% | 105.3% | 105.2% | 105.2% | 105.2%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 1.325% | 75.5% | 75.4% | 75.35% | 75.31%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 174405_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 509% | 39410% | 39360% | 39335% | 39312%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 122.5% | 9496% | 9474% | 9468% | 9463%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 113.8% | 5203% | 5190% | 5174% | 5161%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 92.86% | 54.79% | 54.77% | 54.64% | 54.53%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 38400% | 52200% | 52200% | 52200% | 52200%
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.4% | 105.3% | 105.3% | 105.3%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 3.225% | 75.48% | 75.39% | 75.34% | 75.3%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174422_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 899.7% | 39403% | 39353% | 39327% | 39305%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 216.6% | 9494% | 9473% | 9467% | 9461%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 112.6% | 5203% | 5190% | 5174% | 5161%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 51.97% | 54.8% | 54.78% | 54.65% | 54.54%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 27900% | 52200% | 52200% | 52200% | 52200%
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.4% | 105.3% | 105.3% | 105.3%
NQ | MICC-MICB No 1 132 kV | % of Rated A | 36.89% | 25.72% | 27.22% | 28.66% | 29.8%
NQ | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ | MICC-MICB No 1 132 kV | Loading (A) | 19255% | 18748% | 19847% | 20891% | 21724%
NQ | MICC-MICB No 1 132 kV | Loading (MVA) | 4636% | 2277% | 2411% | 2538% | 2639%
NQ | MICC-MICB No 1 132 kV | Loading (MW) | 2598% | 2276% | 2409% | 2535% | 2636%
NQ | MICC-MICB No 1 132 kV | Power Factor | 56.04% | 99.94% | 99.91% | 99.89% | 99.87%
NQ | MICC-MICB No 1 132 kV | Rating (A) | 52200% | 72900% | 72900% | 72900% | 72900%
NQ | MICC-MICB No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICC-MICB No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 106.2% | 106.3% | 106.3% | 106.3%
NQ | MICC-MICB No 2 132 kV | % of Rated A | 37.02% | 25.72% | 27.22% | 28.66% | 29.8%
NQ | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ | MICC-MICB No 2 132 kV | Loading (A) | 19322% | 18748% | 19846% | 20891% | 21723%
NQ | MICC-MICB No 2 132 kV | Loading (MVA) | 4652% | 2277% | 2411% | 2538% | 2639%
NQ | MICC-MICB No 2 132 kV | Loading (MW) | 2607% | 2276% | 2409% | 2535% | 2636%
NQ | MICC-MICB No 2 132 kV | Power Factor | 56.04% | 99.94% | 99.91% | 99.89% | 99.87%
NQ | MICC-MICB No 2 132 kV | Rating (A) | 52200% | 72900% | 72900% | 72900% | 72900%
NQ | MICC-MICB No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MICC-MICB No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 106.2% | 106.3% | 106.3% | 106.3%
NQ | 6127_Bohle-Black River 1 66 kV | % of Rated A | 11.96% | 2.793% | 3.408% | 3.798% | 4.927%
NQ | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 68120_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96490_1
NQ | 6127_Bohle-Black River 1 66 kV | Loading (A) | 8718% | 3050% | 3721% | 4147% | 5381%
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 1058% | 367.5% | 448.4% | 499.7% | 644.7%
NQ | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 1058% | 367.4% | 448% | 499.4% | 624.9%
NQ | 6127_Bohle-Black River 1 66 kV | Power Factor | 99.97% | 99.96% | 99.91% | 99.94% | 96.93%
NQ | 6127_Bohle-Black River 1 66 kV | Rating (A) | 72900% | 109200% | 109200% | 109200% | 109200%
NQ | 6127_Bohle-Black River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6127_Bohle-Black River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 106.2% | 105.4% | 105.4% | 105.4% | 104.8%
NQ | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 12.09% | 5.743% | 5.726% | 5.708% | 5.899%
NQ | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 162727_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 32515_1
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 8815% | 1482% | 1477% | 1473% | 1522%
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 1070% | 178.5% | 178.1% | 177.6% | 182.8%
NQ | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 1069% | 114.4% | 113.4% | 112.5% | 123.4%
NQ | 6266_Bohle-Black River No 2 66 kV | Power Factor | 99.95% | 64.07% | 63.71% | 63.32% | 67.53%
NQ | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 72900% | 25800% | 25800% | 25800% | 25800%
NQ | 6266_Bohle-Black River No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6266_Bohle-Black River No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 106.2% | 105.4% | 105.4% | 105.5% | 105.1%
NQ | 6299_Townsville Port 66 kV | % of Rated A | 5.066% | 23.13% | 24.68% | 25.64% | 26.92%
NQ | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96490_1 | TR_LINE 98272_1 | TR_LINE 98272_1 | TR_LINE 31738_1 | TR_LINE 31738_1
NQ | 6299_Townsville Port 66 kV | Loading (A) | 5532% | 7518% | 8020% | 8334% | 8748%
NQ | 6299_Townsville Port 66 kV | Loading (MVA) | 665.6% | 901.7% | 962% | 998.8% | 1048%
NQ | 6299_Townsville Port 66 kV | Loading (MW) | 252.4% | 901.7% | 961.8% | 993.1% | 1044%
NQ | 6299_Townsville Port 66 kV | Power Factor | 37.92% | 99.99% | 99.98% | 99.43% | 99.58%
NQ | 6299_Townsville Port 66 kV | Rating (A) | 109200% | 32500% | 32500% | 32500% | 32500%
NQ | 6299_Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6299_Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 104.9% | 104.9% | 104.8% | 104.8%
NQ | 6312_Merinda - Home Hill 66 kV | % of Rated A | 5.754% | 78.56% | 78.86% | 79.17% | 79.43%
NQ | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 32515_1 | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ | 6312_Merinda - Home Hill 66 kV | Loading (A) | 1485% | 11155% | 11197% | 11242% | 11279%
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 178.1% | 1896% | 1911% | 1926% | 1939%
NQ | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 115.2% | 38.88% | 39.18% | 39.5% | 39.75%
NQ | 6312_Merinda - Home Hill 66 kV | Power Factor | 64.69% | 0.7668% | 0.7671% | 0.7671% | 0.7668%
NQ | 6312_Merinda - Home Hill 66 kV | Rating (A) | 25800% | 14200% | 14200% | 14200% | 14200%
NQ | 6312_Merinda - Home Hill 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6312_Merinda - Home Hill 66 kV | Min Voltage at Constrained Conductor (pu) | 105% | 148.7% | 149.3% | 149.9% | 150.4%
NQ | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 18.17% | 46.18% | 46.35% | 46.53% | 46.68%
NQ | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 5904% | 14408% | 14461% | 14517% | 14563%
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 708.4% | 2063% | 2075% | 2088% | 2098%
NQ | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 640.3% | 97.79% | 114.6% | 132.2% | 146.8%
NQ | 6325_Oonoonba-Stuart 66 kV | Power Factor | 90.39% | 4.736% | 5.516% | 6.327% | 6.988%
NQ | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 32500% | 31200% | 31200% | 31200% | 31200%
NQ | 6325_Oonoonba-Stuart 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6325_Oonoonba-Stuart 66 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 125.2% | 125.5% | 125.8% | 126%
NQ | 6382 JACR-HUGH 66kV | % of Rated A | 49.31% | 48.25% | 48.08% | 47.89% | 47.76%
NQ | 6382 JACR-HUGH 66kV | Limiting Line Name | KEP2 - HUGH 66kV line | TR_LINE 178521_1 | TR_LINE 178521_1 | TR_LINE 178521_1 | TR_LINE 178521_1
NQ | 6382 JACR-HUGH 66kV | Loading (A) | 7002% | 16068% | 16011% | 15946% | 15904%
NQ | 6382 JACR-HUGH 66kV | Loading (MVA) | 922.8% | 3873% | 3859% | 3844% | 3840%
NQ | 6382 JACR-HUGH 66kV | Loading (MW) | 107.9% | 2192% | 2141% | 2087% | 2063%
NQ | 6382 JACR-HUGH 66kV | Power Factor | 10.65% | 56.6% | 55.48% | 54.3% | 53.71%
NQ | 6382 JACR-HUGH 66kV | Rating (A) | 14200% | 33300% | 33300% | 33300% | 33300%
NQ | 6382 JACR-HUGH 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6382 JACR-HUGH 66kV | Min Voltage at Constrained Conductor (pu) | 115.3% | 105.4% | 105.4% | 105.4% | 105.6%
NQ | 6383 CARI-CPRE 66kV | % of Rated A | 43.8% | 41.19% | 41.34% | 41.5% | 41.63%
NQ | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ | 6383 CARI-CPRE 66kV | Loading (A) | 13665% | 7125% | 7152% | 7180% | 7202%
NQ | 6383 CARI-CPRE 66kV | Loading (MVA) | 1859% | 2099% | 2112% | 2125% | 2136%
NQ | 6383 CARI-CPRE 66kV | Loading (MW) | 67.69% | 105.9% | 122.7% | 140.4% | 155%
NQ | 6383 CARI-CPRE 66kV | Power Factor | 3.634% | 5.002% | 5.769% | 6.565% | 7.214%
NQ | 6383 CARI-CPRE 66kV | Rating (A) | 31200% | 17300% | 17300% | 17300% | 17300%
NQ | 6383 CARI-CPRE 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 6383 CARI-CPRE 66kV | Min Voltage at Constrained Conductor (pu) | 119% | 128.9% | 129.2% | 129.5% | 129.7%
NQ | 7182 Ross - Milchester | % of Rated A | 40.07% | 20.33% | 20.71% | 19.28% | 19.61%
NQ | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 178521_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ | 7182 Ross - Milchester | Loading (A) | 13343% | 6768% | 6897% | 6420% | 6530%
NQ | 7182 Ross - Milchester | Loading (MVA) | 3227% | 817.7% | 833.3% | 775.7% | 789%
NQ | 7182 Ross - Milchester | Loading (MW) | 1455% | 817.5% | 833.3% | 775.6% | 789%
NQ | 7182 Ross - Milchester | Power Factor | 45.11% | 99.97% | 99.99% | 99.98% | 100%
NQ | 7182 Ross - Milchester | Rating (A) | 33300% | 33300% | 33300% | 33300% | 33300%
NQ | 7182 Ross - Milchester | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 7182 Ross - Milchester | Min Voltage at Constrained Conductor (pu) | 105.8% | 105.7% | 105.7% | 105.7% | 105.7%
NQ | 7460 CPRE-JACR 132kV | % of Rated A | 39.06% | 16.9% | 17.68% | 17.33% | 17.92%
NQ | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ | 7460 CPRE-JACR 132kV | Loading (A) | 6758% | 7775% | 8133% | 7973% | 8245%
NQ | 7460 CPRE-JACR 132kV | Loading (MVA) | 1892% | 936.4% | 979.5% | 960.2% | 993.1%
NQ | 7460 CPRE-JACR 132kV | Loading (MW) | 75% | 858.2% | 909.5% | 886.8% | 926.1%
NQ | 7460 CPRE-JACR 132kV | Power Factor | 3.921% | 91.64% | 92.84% | 92.34% | 93.24%
NQ | 7460 CPRE-JACR 132kV | Rating (A) | 17300% | 46000% | 46000% | 46000% | 46000%
NQ | 7460 CPRE-JACR 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | 7460 CPRE-JACR 132kV | Min Voltage at Constrained Conductor (pu) | 122.5% | 105.3% | 105.3% | 105.4% | 105.4%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 8.615% | 13.85% | 14.03% | 14.5% | 14.9%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 2869% | 3586% | 3633% | 3755% | 3860%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 346.9% | 430.9% | 438.2% | 453.2% | 466.1%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 220.4% | 397.8% | 334.1% | 352% | 367%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 63.54% | 92.29% | 76.23% | 77.64% | 78.71%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 33300% | 25900% | 25900% | 25900% | 25900%
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Min Voltage at Constrained Conductor (pu) | 105.8% | 105.1% | 105.5% | 105.6% | 105.6%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 4.352% | 16.01% | 16.38% | 16.8% | 17.2%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 34618_1 | TR_LINE 32456_1 | TR_LINE 32456_1 | TR_LINE 32456_1 | TR_LINE 32456_1
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 2002% | 3185% | 3259% | 3343% | 3422%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 242% | 382.1% | 391.2% | 401.4% | 411%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 223.4% | 303.2% | 315.5% | 329% | 341.2%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 92.33% | 79.34% | 80.64% | 81.95% | 83%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 46000% | 19900% | 19900% | 19900% | 19900%
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 104.9% | 105% | 105% | 105.1%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 8.771% | 23.85% | 23.87% | 24.15% | 24.75%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 214252_1 | TR_LINE 214252_1
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 2272% | 1645% | 1647% | 4565% | 4678%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 272.6% | 205.5% | 205.9% | 556.1% | 570.1%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 231% | 2.179% | 0.7293% | 469.6% | 486.5%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 84.72% | 1.059% | 0.3529% | 84.31% | 85.2%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 25900% | 6900% | 6900% | 18900% | 18900%
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AY-EA-1_Ayr - East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105% | 109.3% | 109.4% | 106.6% | 106.6%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 8.69% | 51.96% | 54.91% | 55.85% | 58.55%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 33601_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 2242% | 23228% | 24545% | 24965% | 26173%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 269% | 2811% | 2971% | 3021% | 3168%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 145.4% | 2800% | 2962% | 3015% | 3163%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 54.05% | 99.57% | 99.69% | 99.75% | 99.82%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 25800% | 44700% | 44700% | 44700% | 44700%
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105% | 105.9% | 105.9% | 105.9% | 105.9%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 17.17% | 146.4% | 145.5% | 144.7% | 143.9%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 214252_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 3245% | 37761% | 37529% | 37320% | 37125%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 394.3% | 4494% | 4467% | 4443% | 4420%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 392.9% | 4308% | 4268% | 4230% | 4197%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 99.59% | 95.86% | 95.55% | 95.22% | 94.94%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 18900% | 25800% | 25800% | 25800% | 25800%
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | BC-IN-1_Black River - Ingham No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 106.3% | 104.1% | 104.1% | 104.1% | 104.1%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 2.962% | 14.07% | 14.74% | 15.39% | 15.9%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Limiting Line Name | TR_CABLE 4808_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 2352% | 4390% | 4598% | 4803% | 4962%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MVA) | 284.3% | 520.9% | 545.6% | 569.9% | 588.8%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MW) | 56.31% | 471.9% | 499.7% | 526.9% | 547.9%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 19.53% | 90.6% | 91.59% | 92.44% | 93.05%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 79400% | 31200% | 31200% | 31200% | 31200%
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 103.8% | 103.8% | 103.8% | 103.8%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 2.943% | 24.46% | 25.67% | 26.87% | 27.79%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Limiting Line Name | TR_CABLE 16086_1 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 2337% | 4134% | 4339% | 4540% | 4697%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MVA) | 282.5% | 494.7% | 519.3% | 543.6% | 562.4%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MW) | 56.37% | 467.1% | 494% | 520.2% | 540.6%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 19.65% | 94.41% | 95.11% | 95.69% | 96.11%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 79400% | 16900% | 16900% | 16900% | 16900%
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 104.7% | 104.7% | 104.7% | 104.7%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 22.53% | 143.3% | 143.8% | 144.4% | 144.9%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 10070% | 20489% | 20567% | 20650% | 20718%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 1215% | 2804% | 2821% | 2839% | 2853%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 1125% | 586% | 566.3% | 545.7% | 528.6%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 92.52% | 20.89% | 20.07% | 19.21% | 18.52%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 44700% | 14300% | 14300% | 14300% | 14300%
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | BO-DG-1_Bohle-Dan Gleeson 66 kV | Min Voltage at Constrained Conductor (pu) | 105.5% | 119.7% | 120% | 120.2% | 120.5%
NQ | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 52.28% | 3.974% | 4.117% | 4.264% | 4.549%
NQ | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 102297_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 13489% | 774.8% | 802.7% | 831.5% | 887%
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 1602% | 91.74% | 95.04% | 98.45% | 105.4%
NQ | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 1389% | 75.15% | 79.17% | 83.25% | 91.16%
NQ | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 86.67% | 81.91% | 83.3% | 84.56% | 86.53%
NQ | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 25800% | 19500% | 19500% | 19500% | 19500%
NQ | CHTO_Clare South - Charters Towers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CHTO_Clare South - Charters Towers 66 kV | Min Voltage at Constrained Conductor (pu) | 103.9% | 103.6% | 103.6% | 103.6% | 103.9%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 8.737% | 89.85% | 90.19% | 90.56% | 90.86%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 102266_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 2726% | 16533% | 16595% | 16662% | 16717%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 323.8% | 2053% | 2063% | 2074% | 2082%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 224.7% | 470.6% | 448.2% | 424.7% | 405.4%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 69.39% | 22.77% | 21.57% | 20.33% | 19.31%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 31200% | 18400% | 18400% | 18400% | 18400%
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 103.9% | 108.6% | 108.7% | 108.8% | 108.9%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 14.58% | 92.69% | 93.01% | 93.36% | 93.64%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_2 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 2464% | 25768% | 25857% | 25955% | 26032%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 294.5% | 3298% | 3326% | 3355% | 3379%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 228.6% | 1078% | 1054% | 1029% | 1008%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 77.6% | 32.69% | 31.68% | 30.66% | 29.84%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 16900% | 27800% | 27800% | 27800% | 27800%
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 104.6% | 112% | 112.5% | 113.1% | 113.5%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 12.91% | 16.04% | 16.33% | 16.67% | 16.94%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 32874_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 1846% | 7251% | 7383% | 7533% | 7656%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 247.3% | 878.6% | 894.6% | 912.7% | 927.7%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 199.9% | 213.2% | 272.3% | 328.3% | 368.5%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 80.81% | 24.25% | 30.42% | 35.96% | 39.71%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 14300% | 45200% | 45200% | 45200% | 45200%
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CR-HU-1_Cape River-Hughenden No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 117.2% | 106% | 106% | 106% | 106%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 3.807% | 14.27% | 14.16% | 13.14% | 13.45%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 102260_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 172527_2
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 742.3% | 7864% | 7800% | 7239% | 7409%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 88.19% | 948.1% | 940.4% | 872.8% | 889.4%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 70.46% | 947.9% | 940.2% | 872.6% | 781.6%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 79.9% | 99.97% | 99.99% | 99.98% | 87.89%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 19500% | 55100% | 55100% | 55100% | 55100%
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CS-ML-1_Clare South - Millaroo 66 kV | Min Voltage at Constrained Conductor (pu) | 103.9% | 105.5% | 105.5% | 105.5% | 105%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 40.78% | 26.92% | 28.24% | 29.41% | 31.1%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 31871_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 7503% | 6758% | 7088% | 7383% | 7806%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 947.9% | 815.9% | 855.7% | 891.2% | 936.5%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 10.46% | 777.6% | 820% | 857.7% | 906.5%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 1.034% | 95.31% | 95.83% | 96.24% | 96.79%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 18400% | 25100% | 25100% | 25100% | 25100%
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CT-CR-1_Charters Towers-CARI No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 110.5% | 105.6% | 105.6% | 105.6% | 104.9%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 13.66% | 21.02% | 22.08% | 23.15% | 23.99%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 3799% | 4413% | 4636% | 4861% | 5038%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 479.9% | 531.5% | 558.6% | 585.9% | 607.5%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 264% | 463.4% | 493.9% | 524.3% | 548.2%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 55% | 87.19% | 88.41% | 89.47% | 90.24%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 27800% | 21000% | 21000% | 21000% | 21000%
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | CT-MR-1_Millchester-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 110.5% | 105.4% | 105.4% | 105.4% | 105.5%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 14.53% | 42.17% | 44.56% | 45.32% | 47.51%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 128084_1
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 6566% | 23234% | 24553% | 24971% | 26180%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 793% | 2805% | 2964% | 3015% | 3161%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 78.06% | 2796% | 2958% | 3010% | 3157%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 9.838% | 99.68% | 99.78% | 99.83% | 99.88%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 45200% | 55100% | 55100% | 55100% | 55100%
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 105.6% | 105.6% | 105.6% | 105.6%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 9.652% | 13.36% | 12.77% | 12.43% | 13.95%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 172527_2 | TR_LINE 77120_1 | TR_LINE 77120_1 | TR_LINE 77120_1 | TR_LINE 77120_1
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 5318% | 4609% | 4407% | 4289% | 4813%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 640.4% | 555.6% | 531.3% | 517.9% | 581.1%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 635.4% | 555.2% | 530.4% | 517.8% | 581.1%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 99.22% | 99.94% | 99.84% | 99.99% | 100%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 55100% | 34500% | 34500% | 34500% | 34500%
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 105.4% | 105.4% | 105.6% | 105.6%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 9.639% | 17.83% | 19.44% | 18.75% | 17.83%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 2419% | 3014% | 3285% | 3169% | 3013%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 291.4% | 363.3% | 396% | 382% | 360.7%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 245.8% | 354.3% | 388% | 373.7% | 351.9%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 84.34% | 97.52% | 97.99% | 97.8% | 97.56%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 25100% | 16900% | 16900% | 16900% | 16900%
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.4% | 105.4% | 105.4% | 105.5% | 104.7%
NQ | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 11.34% | 35.07% | 36.9% | 37.2% | 38.56%
NQ | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 183529_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 2382% | 9049% | 9519% | 9598% | 9948%
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 285.8% | 1092% | 1149% | 1159% | 1201%
NQ | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 139.6% | 1048% | 1104% | 1113% | 1154%
NQ | EAAY_Clare South - East Ayr 66 kV | Power Factor | 48.84% | 95.93% | 96.04% | 96.02% | 96.06%
NQ | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 21000% | 25800% | 25800% | 25800% | 25800%
NQ | EAAY_Clare South - East Ayr 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | EAAY_Clare South - East Ayr 66 kV | Min Voltage at Constrained Conductor (pu) | 105% | 105.6% | 105.6% | 105.6% | 105.6%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 22.61% | 9.683% | 10.11% | 10.54% | 11.63%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 32140_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 12460% | 1830% | 1911% | 1992% | 2198%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 1510% | 219.7% | 229.5% | 239.4% | 264.1%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 1503% | 188% | 199.5% | 210.8% | 238.8%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 99.5% | 85.59% | 86.91% | 88.05% | 90.42%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 55100% | 18900% | 18900% | 18900% | 18900%
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-BO-1_Garbutt-Bohle No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 106% | 105% | 105.1% | 105.1% | 105.1%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 10.51% | 14.72% | 15.24% | 15.34% | 15.89%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 98259_1 | TR_LINE 98259_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 3627% | 5079% | 5259% | 5292% | 5483%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 438.2% | 611.4% | 633.1% | 636.8% | 659.9%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 327.8% | 611.3% | 632.7% | 627.8% | 652.7%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 74.8% | 99.98% | 99.93% | 98.57% | 98.91%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 34500% | 34500% | 34500% | 34500% | 34500%
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 105.3% | 105.3% | 105.3% | 105.3%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 7.563% | 15.89% | 15.93% | 15.97% | 16.01%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 1278% | 4528% | 4539% | 4552% | 4563%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 154.5% | 771.3% | 776.1% | 781.4% | 785.8%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 128% | 121.7% | 112.2% | 102.2% | 93.92%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 82.84% | 15.78% | 14.46% | 13.08% | 11.95%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 16900% | 28500% | 28500% | 28500% | 28500%
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 149% | 149.6% | 150.2% | 150.6%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 25.64% | 14.48% | 14.55% | 14.62% | 14.68%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 6616% | 3795% | 3812% | 3831% | 3846%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 796.8% | 645.2% | 650.5% | 656.3% | 661%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 761.9% | 33.41% | 39.69% | 46.47% | 52.18%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 95.61% | 5.177% | 6.099% | 7.077% | 7.892%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 25800% | 26200% | 26200% | 26200% | 26200%
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 148.7% | 149.3% | 149.9% | 150.4%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 7.432% | 25.5% | 26.66% | 27.7% | 28.5%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 170050_1 | TR_LINE 78407_1 | TR_LINE 78407_1 | TR_LINE 78407_1 | TR_LINE 78407_1
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 1405% | 3366% | 3519% | 3657% | 3762%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 168.6% | 414.6% | 433.9% | 451.3% | 464.6%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 149.7% | 413.4% | 432.8% | 450.4% | 463.7%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 88.82% | 99.72% | 99.76% | 99.79% | 99.82%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 18900% | 13200% | 13200% | 13200% | 13200%
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | GI-AY-1_Giru - Ayr 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105% | 107.7% | 107.8% | 107.9% | 108%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 10.84% | 11.68% | 11.7% | 11.75% | 12.12%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 3740% | 1974% | 1977% | 1985% | 2048%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 450.5% | 237.6% | 238.1% | 239.5% | 247.2%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 336.7% | 81.79% | 85.71% | 239.5% | 247.2%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 74.73% | 34.42% | 36% | 99.99% | 99.99%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 34500% | 16900% | 16900% | 16900% | 16900%
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | HP-OO_Hermit park - Oonoonba 66 kV | Min Voltage at Constrained Conductor (pu) | 105.4% | 105.3% | 105.4% | 105.5% | 105.6%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 12.73% | 6.139% | 6.343% | 6.535% | 7.052%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 3627% | 1222% | 1262% | 1300% | 1403%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 487% | 146.2% | 151.1% | 155.8% | 168.6%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 127.9% | 145.2% | 150.1% | 154.8% | 167.8%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 26.26% | 99.3% | 99.36% | 99.4% | 99.51%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 28500% | 19900% | 19900% | 19900% | 19900%
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | HU-RI-1_Hughenden-Richmond No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 117.4% | 104.7% | 104.7% | 104.8% | 105.1%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 11.44% | 14.62% | 14.49% | 14.37% | 14.3%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 2997% | 3773% | 3737% | 3707% | 3691%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 401.6% | 454.5% | 450.1% | 446.5% | 444.6%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 30.12% | 103% | 80.65% | 54.5% | 33.83%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 7.496% | 22.67% | 17.92% | 12.21% | 7.61%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 26200% | 25800% | 25800% | 25800% | 25800%
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | HU-WI-1 Hughenden-Winton No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 117.2% | 105.4% | 105.4% | 105.4% | 105.4%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 8.123% | 14.83% | 14.69% | 14.57% | 14.51%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 1373% | 3825% | 3790% | 3760% | 3744%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 165% | 460.8% | 456.5% | 453% | 451%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 110.6% | 103.1% | 80.76% | 54.59% | 33.93%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 67.03% | 22.38% | 17.69% | 12.05% | 7.522%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 16900% | 25800% | 25800% | 25800% | 25800%
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.2% | 105.4% | 105.4% | 105.4% | 105.4%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 5.893% | 22.7% | 23.84% | 25.01% | 25.94%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 31747_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 1173% | 4767% | 5006% | 5252% | 5448%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 140.7% | 565.7% | 594% | 623.2% | 646.5%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 139.6% | 503% | 535.2% | 568% | 594.1%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 99.22% | 88.92% | 90.1% | 91.13% | 91.89%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 19900% | 21000% | 21000% | 21000% | 21000%
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | KA-AY-01_Ayr - Kalamia No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105% | 103.8% | 103.8% | 103.8% | 103.8%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 2.175% | 19.01% | 19.89% | 20.75% | 21.41%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 121605_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 561.1% | 3783% | 3958% | 4129% | 4261%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 67.51% | 453% | 474.1% | 494.8% | 510.7%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 63.17% | 399.4% | 423.3% | 446.6% | 464.6%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 93.57% | 88.16% | 89.29% | 90.26% | 90.97%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 25800% | 19900% | 19900% | 19900% | 19900%
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 104.8% | 104.8% | 104.8% | 104.8%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 14.6% | 107.4% | 107.7% | 108% | 108.2%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 3766% | 16654% | 16694% | 16738% | 16774%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 453.3% | 2084% | 2090% | 2098% | 2103%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 63.85% | 324.1% | 299.7% | 274.2% | 253.2%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 14.09% | 15.55% | 14.33% | 13.06% | 12.03%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 25800% | 15500% | 15500% | 15500% | 15500%
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 109.4% | 109.5% | 109.6% | 109.7%
NQ | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 12.03% | 36.38% | 36.36% | 36.34% | 36.62%
NQ | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 2526% | 6840% | 6835% | 6832% | 6885%
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 300.1% | 833.5% | 833.4% | 833.5% | 867.1%
NQ | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 146.1% | 832.9% | 832.9% | 832.9% | 866.6%
NQ | MOPA_Clare South - Mona Park 66 kV | Power Factor | 48.67% | 99.77% | 99.77% | 99.76% | 99.76%
NQ | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 21000% | 18800% | 18800% | 18800% | 18800%
NQ | MOPA_Clare South - Mona Park 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MOPA_Clare South - Mona Park 66 kV | Min Voltage at Constrained Conductor (pu) | 103.9% | 104.2% | 104.3% | 104.4% | 107.8%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 9.187% | 22.28% | 23.21% | 22.24% | 24.05%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32534_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 32958_1
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 1828% | 5748% | 5988% | 5738% | 6205%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 218.4% | 692.1% | 721% | 690.9% | 745.2%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 49.05% | 691.2% | 720.4% | 690.1% | 622.6%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 22.45% | 99.86% | 99.92% | 99.89% | 83.54%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 19900% | 25800% | 25800% | 25800% | 25800%
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MP-AY-1 Mona Park - Ayr No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 104.5% | 105.3% | 105.3% | 105.3% | 105.1%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 63.04% | 7.384% | 7.406% | 7.43% | 7.45%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 165123_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 9771% | 2621% | 2629% | 2638% | 2645%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 1238% | 457.5% | 460.8% | 464.2% | 467.1%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 286.4% | 67.02% | 63.4% | 59.33% | 55.92%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 23.13% | 14.65% | 13.76% | 12.78% | 11.97%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 15500% | 35500% | 35500% | 35500% | 35500%
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MR-CR-1_Millchester-Cape River 1 66 kV | Min Voltage at Constrained Conductor (pu) | 110.8% | 152.7% | 153.3% | 154% | 154.5%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 35.51% | 10.46% | 10.99% | 11.52% | 11.95%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 195947_1 | TR_LINE 195947_1 | TR_LINE 195947_1 | TR_LINE 195947_1
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 6676% | 1380% | 1451% | 1521% | 1577%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 832.4% | 166% | 174.4% | 182.9% | 189.7%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 832% | 159.4% | 168.3% | 177.1% | 184.2%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 99.77% | 95.97% | 96.39% | 96.75% | 97%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 18800% | 13200% | 13200% | 13200% | 13200%
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Min Voltage at Constrained Conductor (pu) | 106.8% | 105.2% | 105.2% | 105.2% | 105.2%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 11.14% | 12.38% | 12.97% | 13.5% | 13.89%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 2873% | 6822% | 7147% | 7438% | 7655%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 345.8% | 817.9% | 856.9% | 891.8% | 917.9%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 339.3% | 777.7% | 820.1% | 857.8% | 885.9%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 98.12% | 94.69% | 95.29% | 95.76% | 96.08%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 25800% | 55100% | 55100% | 55100% | 55100%
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 104.9% | 104.9% | 104.9% | 104.9%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 5.901% | 11.93% | 12.38% | 12.18% | 12.54%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 2095% | 8104% | 8406% | 8267% | 8517%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 287.7% | 971.4% | 1008% | 991% | 1021%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 69.9% | 889.9% | 932.4% | 913.2% | 948.4%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 24.3% | 91.61% | 92.54% | 92.14% | 92.9%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 35500% | 67900% | 67900% | 67900% | 67900%
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 120.1% | 104.9% | 104.9% | 104.9% | 104.9%
NQ | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 3% | 20.47% | 20.96% | 20.79% | 21.06%
NQ | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 162083_1 | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 294% | 5138% | 5260% | 5218% | 5286%
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 35.31% | 618.8% | 633.4% | 628.3% | 636.5%
NQ | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 26.47% | 240.9% | 260.5% | 252.5% | 261.7%
NQ | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 74.94% | 38.93% | 41.14% | 40.18% | 41.11%
NQ | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 9800% | 25100% | 25100% | 25100% | 25100%
NQ | ST-GI-1_Stuart-Giru 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-GI-1_Stuart-Giru 66 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 105.3% | 105.3% | 105.3% | 105.3%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 7.579% | 16.98% | 17.4% | 17.67% | 16.41%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 4176% | 15635% | 16021% | 16278% | 15112%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 501% | 1875% | 1921% | 1952% | 1812%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 486.1% | 764.3% | 876.6% | 936.7% | 504.1%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 96.77% | 40.77% | 45.63% | 47.99% | 27.81%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 55100% | 92100% | 92100% | 92100% | 92100%
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-RM-1_Stuart-Rasmussen 66 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 104.9% | 104.9% | 104.9% | 104.9%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 7.343% | 8.13% | 8.874% | 9.32% | 8.035%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32425_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 4986% | 7488% | 8173% | 8584% | 7401%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 598.2% | 899.5% | 981.8% | 1031% | 888.5%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 521.5% | 630.6% | 745.4% | 806.8% | 873.7%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 87.17% | 70.1% | 75.92% | 78.24% | 98.34%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 67900% | 92100% | 92100% | 92100% | 92100%
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-RP-1_Stuart-Ross Plains 66 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 105.1% | 105.1% | 105.1% | 105%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 6.814% | 134.3% | 134% | 133.6% | 133.4%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 1710% | 17733% | 17694% | 17635% | 17610%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 205.7% | 2142% | 2140% | 2137% | 2136%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 82.44% | 1287% | 1258% | 1226% | 1202%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 40.07% | 58.96% | 57.64% | 56.23% | 55.12%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 25100% | 13200% | 13200% | 13200% | 13200%
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-TOPO-1_Stuart-Townsville Port 66 kV | Min Voltage at Constrained Conductor (pu) | 105.2% | 105.7% | 105.8% | 106% | 106.1%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 13.87% | 11.71% | 12.76% | 12.31% | 11.99%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 12778% | 3020% | 3291% | 3176% | 3093%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 1531% | 363.5% | 396.2% | 382.3% | 372.2%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 469.4% | 354.2% | 387.9% | 373.5% | 363.2%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 30.66% | 97.43% | 97.9% | 97.72% | 97.57%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 92100% | 25800% | 25800% | 25800% | 25800%
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Min Voltage at Constrained Conductor (pu) | 104.8% | 105.3% | 105.3% | 105.3% | 105.3%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 4.292% | 95.86% | 95.7% | 95.41% | 95.32%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157898_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 3953% | 17159% | 17129% | 17079% | 17062%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 474.2% | 2164% | 2170% | 2174% | 2179%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 426% | 966.7% | 943.4% | 917.8% | 898.4%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 89.85% | 44.25% | 43.06% | 41.81% | 40.82%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 92100% | 17900% | 17900% | 17900% | 17900%
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 110.3% | 110.8% | 111.3% | 111.7%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 43.36% | 6.715% | 6.715% | 6.715% | 6.715%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 5724% | 4365% | 4365% | 4365% | 4365%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 696.3% | 1054% | 1054% | 1054% | 1054%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 170.7% | 811.9% | 811.9% | 811.9% | 811.9%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 24.32% | 77.03% | 77.02% | 77.02% | 77.02%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 13200% | 65000% | 65000% | 65000% | 65000%
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | ST-WO-1_Stuart-Woodstock South 1 66 kV | Min Voltage at Constrained Conductor (pu) | 106.4% | 105.6% | 105.6% | 105.6% | 105.6%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 4.99% | 8.042% | 8.036% | 8.046% | 8.064%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 56322_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 1287% | 747.9% | 747.3% | 748.3% | 749.9%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 154.9% | 42.96% | 42.95% | 43.03% | 43.14%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 128.1% | 2.96% | 1.101% | 0.7735% | 2.319%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 82.65% | 6.888% | 2.562% | 1.795% | 5.372%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 25800% | 9300% | 9300% | 9300% | 9300%
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | TP-NS-1_Townsville Port-NESM No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 105.3% | 100.5% | 100.6% | 100.6% | 100.7%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 30.23% | 2.531% | 3.287% | 4.118% | 4.829%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 32389_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 5713% | 898.5% | 1167% | 1462% | 1714%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 697.2% | 52.62% | 68.36% | 85.63% | 100.4%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 197.5% | 43.96% | 62.12% | 80.93% | 96.6%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 27.89% | 83.51% | 90.86% | 94.48% | 96.16%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 18900% | 35500% | 35500% | 35500% | 35500%
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ | WO-CT-1_Woodstock-CHTO No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 106.8% | 102.5% | 102.5% | 102.5% | 102.5%
SW | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 6.715% | 8.668% | 8.76% | 8.866% | 8.961%
SW | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 63522_1 | TR_LINE 63522_1 | TR_LINE 63522_1 | TR_LINE 63522_1
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 4365% | 806.1% | 814.7% | 824.5% | 833.4%
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 1054% | 46.16% | 46.68% | 47.29% | 47.82%
SW | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 811.9% | 10.49% | 12.36% | 14.23% | 15.78%
SW | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 77.02% | 22.58% | 26.31% | 29.94% | 32.84%
SW | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 65000% | 9300% | 9300% | 9300% | 9300%
SW | 7235_Bulli Creek - Waggamba 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7235_Bulli Creek - Waggamba 132 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 100.2% | 100.3% | 100.3% | 100.4%
SW | 3196_Tara 33 kV | % of Rated A | 8.028% | 52.55% | 52.55% | 52.54% | 52.54%
SW | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1
SW | 3196_Tara 33 kV | Loading (A) | 746.6% | 4887% | 4887% | 4886% | 4886%
SW | 3196_Tara 33 kV | Loading (MVA) | 42.74% | 276.3% | 276.3% | 276.3% | 276.2%
SW | 3196_Tara 33 kV | Loading (MW) | 5.002% | 273.8% | 273.8% | 273.8% | 273.8%
SW | 3196_Tara 33 kV | Power Factor | 11.7% | 99.11% | 99.11% | 99.11% | 99.11%
SW | 3196_Tara 33 kV | Rating (A) | 9300% | 9300% | 9300% | 9300% | 9300%
SW | 3196_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3196_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 100.2% | 98.86% | 98.87% | 98.87% | 98.88%
SW | 3203_Miles 33 kV | % of Rated A | 2.653% | 14.68% | 14.86% | 15.03% | 15.19%
SW | 3203_Miles 33 kV | Limiting Line Name | HV_CABLE 219934_1 | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 28408_1
SW | 3203_Miles 33 kV | Loading (A) | 941.9% | 1292% | 1308% | 1323% | 1336%
SW | 3203_Miles 33 kV | Loading (MVA) | 55.11% | 74.52% | 75.44% | 76.33% | 77.11%
SW | 3203_Miles 33 kV | Loading (MW) | 50.52% | 74.37% | 75.3% | 76.19% | 76.97%
SW | 3203_Miles 33 kV | Power Factor | 91.68% | 99.8% | 99.8% | 99.81% | 99.82%
SW | 3203_Miles 33 kV | Rating (A) | 35500% | 8800% | 8800% | 8800% | 8800%
SW | 3203_Miles 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3203_Miles 33 kV | Min Voltage at Constrained Conductor (pu) | 102.4% | 100.9% | 100.9% | 100.9% | 101%
SW | F060T_Tara 33 kV | % of Rated A | 8.553% | 3.891% | 3.89% | 3.89% | 3.89%
SW | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 63522_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1
SW | F060T_Tara 33 kV | Loading (A) | 795.5% | 361.8% | 361.8% | 361.8% | 361.8%
SW | F060T_Tara 33 kV | Loading (MVA) | 45.38% | 20.81% | 20.81% | 20.81% | 20.81%
SW | F060T_Tara 33 kV | Loading (MW) | 8.446% | 20.36% | 20.36% | 20.36% | 20.36%
SW | F060T_Tara 33 kV | Power Factor | 18.46% | 97.82% | 97.82% | 97.82% | 97.82%
SW | F060T_Tara 33 kV | Rating (A) | 9300% | 9300% | 9300% | 9300% | 9300%
SW | F060T_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F060T_Tara 33 kV | Min Voltage at Constrained Conductor (pu) | 99.82% | 100.6% | 100.6% | 100.6% | 100.6%
SW | F067C_Kogan 33 kV | % of Rated A | 52.42% | 7.168% | 7.006% | 6.877% | 6.874%
SW | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 28354_1 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 22686_1 | TR_LINE 22686_1
SW | F067C_Kogan 33 kV | Loading (A) | 4875% | 1025% | 1002% | 639.6% | 639.2%
SW | F067C_Kogan 33 kV | Loading (MVA) | 276.2% | 58.06% | 56.77% | 35.9% | 35.9%
SW | F067C_Kogan 33 kV | Loading (MW) | 273.7% | 57.8% | 56.5% | 30.33% | 30.33%
SW | F067C_Kogan 33 kV | Power Factor | 99.11% | 99.55% | 99.52% | 84.28% | 84.28%
SW | F067C_Kogan 33 kV | Rating (A) | 9300% | 14300% | 14300% | 9300% | 9300%
SW | F067C_Kogan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F067C_Kogan 33 kV | Min Voltage at Constrained Conductor (pu) | 99.09% | 99.07% | 99.12% | 98.2% | 98.25%
SW | F069C_Brigalow 33 kV | % of Rated A | 14.41% | 6.109% | 6.816% | 7.529% | 8.099%
SW | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 28408_1 | TR_LINE 25573_1 | TR_LINE 25573_1 | TR_LINE 25573_1 | TR_LINE 25573_1
SW | F069C_Brigalow 33 kV | Loading (A) | 1268% | 1191% | 1329% | 1468% | 1579%
SW | F069C_Brigalow 33 kV | Loading (MVA) | 73.31% | 68.16% | 76.06% | 84.02% | 90.38%
SW | F069C_Brigalow 33 kV | Loading (MW) | 73.15% | 68.13% | 76.03% | 84% | 90.36%
SW | F069C_Brigalow 33 kV | Power Factor | 99.78% | 99.95% | 99.97% | 99.98% | 99.98%
SW | F069C_Brigalow 33 kV | Rating (A) | 8800% | 19500% | 19500% | 19500% | 19500%
SW | F069C_Brigalow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F069C_Brigalow 33 kV | Min Voltage at Constrained Conductor (pu) | 101.2% | 100.1% | 100.1% | 100.1% | 100.1%
SW | F073C_Fairymeadow 33 kV | % of Rated A | 3.88% | 7.404% | 7.168% | 7.162% | 7.157%
SW | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_LINE 155280_1 | TR_LINE 24905_1 | TR_LINE 24905_1 | TR_LINE 24905_1
SW | F073C_Fairymeadow 33 kV | Loading (A) | 360.8% | 1281% | 1240% | 1239% | 1238%
SW | F073C_Fairymeadow 33 kV | Loading (MVA) | 20.8% | 72.64% | 70.34% | 70.34% | 70.34%
SW | F073C_Fairymeadow 33 kV | Loading (MW) | 20.35% | 69.72% | 58.84% | 58.84% | 58.84%
SW | F073C_Fairymeadow 33 kV | Power Factor | 97.87% | 95.84% | 83.64% | 83.64% | 83.64%
SW | F073C_Fairymeadow 33 kV | Rating (A) | 9300% | 17300% | 17300% | 17300% | 17300%
SW | F073C_Fairymeadow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F073C_Fairymeadow 33 kV | Min Voltage at Constrained Conductor (pu) | 100.8% | 99.22% | 99.25% | 99.32% | 99.39%
SW | F074C_Miles-Condamine 33 kV | % of Rated A | 7.305% | 29.16% | 29.17% | 29.18% | 29.18%
SW | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26905_1 | TR_LINE 26905_1
SW | F074C_Miles-Condamine 33 kV | Loading (A) | 1045% | 8079% | 8080% | 8082% | 8083%
SW | F074C_Miles-Condamine 33 kV | Loading (MVA) | 59.51% | 461.7% | 461.7% | 461.7% | 461.7%
SW | F074C_Miles-Condamine 33 kV | Loading (MW) | 59.2% | 409.3% | 409.3% | 409.3% | 409.3%
SW | F074C_Miles-Condamine 33 kV | Power Factor | 99.49% | 88.65% | 88.65% | 88.65% | 88.64%
SW | F074C_Miles-Condamine 33 kV | Rating (A) | 14300% | 27700% | 27700% | 27700% | 27700%
SW | F074C_Miles-Condamine 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F074C_Miles-Condamine 33 kV | Min Voltage at Constrained Conductor (pu) | 99.64% | 99.98% | 99.96% | 99.95% | 99.94%
SW | F075S_St George Town 33 kV | % of Rated A | 6.057% | 12.24% | 12.24% | 12.24% | 12.24%
SW | F075S_St George Town 33 kV | Limiting Line Name | TR_CABLE 16563_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1 | TR_LINE 12085532_1
SW | F075S_St George Town 33 kV | Loading (A) | 993.3% | 746.9% | 746.9% | 746.9% | 746.8%
SW | F075S_St George Town 33 kV | Loading (MVA) | 57.07% | 42.9% | 42.89% | 42.89% | 42.89%
SW | F075S_St George Town 33 kV | Loading (MW) | 56.97% | 21.01% | 21.01% | 21.01% | 21.01%
SW | F075S_St George Town 33 kV | Power Factor | 99.8% | 48.97% | 48.97% | 48.98% | 48.98%
SW | F075S_St George Town 33 kV | Rating (A) | 16400% | 6100% | 6100% | 6100% | 6100%
SW | F075S_St George Town 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F075S_St George Town 33 kV | Min Voltage at Constrained Conductor (pu) | 100.5% | 100.5% | 100.5% | 100.5% | 100.5%
SW | F077C_Wandoan 33 kV | % of Rated A | 12.49% | 12.81% | 14.5% | 16.23% | 17.71%
SW | F077C_Wandoan 33 kV | Limiting Line Name | TR_CABLE 126_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1
SW | F077C_Wandoan 33 kV | Loading (A) | 1249% | 4277% | 4843% | 5422% | 5914%
SW | F077C_Wandoan 33 kV | Loading (MVA) | 70.81% | 246.5% | 279.3% | 312.8% | 341.2%
SW | F077C_Wandoan 33 kV | Loading (MW) | 58.83% | 246.5% | 279.3% | 312.7% | 341.2%
SW | F077C_Wandoan 33 kV | Power Factor | 83.07% | 99.99% | 99.99% | 99.99% | 99.99%
SW | F077C_Wandoan 33 kV | Rating (A) | 10000% | 33400% | 33400% | 33400% | 33400%
SW | F077C_Wandoan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F077C_Wandoan 33 kV | Min Voltage at Constrained Conductor (pu) | 99.17% | 100.8% | 100.9% | 100.9% | 100.9%
SW | F077S_Main Camp 33 kV | % of Rated A | 80.25% | 12.85% | 12.85% | 12.85% | 12.85%
SW | F077S_Main Camp 33 kV | Limiting Line Name | TR_CABLE 16560_1 | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1
SW | F077S_Main Camp 33 kV | Loading (A) | 8025% | 937.8% | 937.9% | 938.1% | 938.2%
SW | F077S_Main Camp 33 kV | Loading (MVA) | 461.1% | 51.67% | 51.67% | 51.67% | 51.67%
SW | F077S_Main Camp 33 kV | Loading (MW) | 409.2% | 45.76% | 45.76% | 45.76% | 45.76%
SW | F077S_Main Camp 33 kV | Power Factor | 88.75% | 88.51% | 88.5% | 88.5% | 88.5%
SW | F077S_Main Camp 33 kV | Rating (A) | 10000% | 7300% | 7300% | 7300% | 7300%
SW | F077S_Main Camp 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F077S_Main Camp 33 kV | Min Voltage at Constrained Conductor (pu) | 100.5% | 96.4% | 96.38% | 96.37% | 96.35%
SW | F079S_St George Meatworks 33 kV | % of Rated A | 22.84% | 0.9402% | 2.007% | 3.109% | 3.991%
SW | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_CABLE 16561_1 | TR_LINE 44567_3 | TR_LINE 116092_1 | TR_LINE 116092_1 | TR_LINE 116092_1
SW | F079S_St George Meatworks 33 kV | Loading (A) | 2284% | 240.7% | 513.7% | 796% | 1022%
SW | F079S_St George Meatworks 33 kV | Loading (MVA) | 131.2% | 13.84% | 29.55% | 45.81% | 58.83%
SW | F079S_St George Meatworks 33 kV | Loading (MW) | 124.8% | 13.84% | 29.55% | 45.81% | 58.83%
SW | F079S_St George Meatworks 33 kV | Power Factor | 95.1% | 100% | 100% | 100% | 100%
SW | F079S_St George Meatworks 33 kV | Rating (A) | 10000% | 25600% | 25600% | 25600% | 25600%
SW | F079S_St George Meatworks 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F079S_St George Meatworks 33 kV | Min Voltage at Constrained Conductor (pu) | 100.5% | 100.6% | 100.6% | 100.7% | 100.7%
SW | F083C_Chinchilla 33 kV | % of Rated A | 11% | 3.543% | 4.739% | 5.98% | 6.994%
SW | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 27121_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1
SW | F083C_Chinchilla 33 kV | Loading (A) | 3674% | 411% | 549.7% | 693.7% | 811.3%
SW | F083C_Chinchilla 33 kV | Loading (MVA) | 211.7% | 23.63% | 31.62% | 39.92% | 46.7%
SW | F083C_Chinchilla 33 kV | Loading (MW) | 211.2% | 23.54% | 31.56% | 39.88% | 46.67%
SW | F083C_Chinchilla 33 kV | Power Factor | 99.76% | 99.61% | 99.79% | 99.88% | 99.92%
SW | F083C_Chinchilla 33 kV | Rating (A) | 33400% | 11600% | 11600% | 11600% | 11600%
SW | F083C_Chinchilla 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F083C_Chinchilla 33 kV | Min Voltage at Constrained Conductor (pu) | 100.8% | 100.6% | 100.6% | 100.7% | 100.7%
SW | F106R_Roma East 33 kV | % of Rated A | 0.4765% | 47.9% | 47.58% | 47.25% | 46.99%
SW | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1 | TR_LINE 158494_1
SW | F106R_Roma East 33 kV | Loading (A) | 122% | 8286% | 8231% | 8175% | 8130%
SW | F106R_Roma East 33 kV | Loading (MVA) | 7.012% | 2013% | 2000% | 1986% | 1976%
SW | F106R_Roma East 33 kV | Loading (MW) | 6.736% | 1820% | 1805% | 1790% | 1778%
SW | F106R_Roma East 33 kV | Power Factor | 96.07% | 90.41% | 90.26% | 90.11% | 89.99%
SW | F106R_Roma East 33 kV | Rating (A) | 25600% | 17300% | 17300% | 17300% | 17300%
SW | F106R_Roma East 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F106R_Roma East 33 kV | Min Voltage at Constrained Conductor (pu) | 100.6% | 105.6% | 105.7% | 105.7% | 105.7%
SW | F127R_Roma West 33 kV | % of Rated A | 2.242% | 47.91% | 47.6% | 47.27% | 47.01%
SW | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 125467_1 | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1) | TR_LINE 158493_1(1)
SW | F127R_Roma West 33 kV | Loading (A) | 260% | 8289% | 8234% | 8178% | 8133%
SW | F127R_Roma West 33 kV | Loading (MVA) | 14.95% | 2013% | 2000% | 1987% | 1976%
SW | F127R_Roma West 33 kV | Loading (MW) | 14.8% | 1820% | 1806% | 1791% | 1779%
SW | F127R_Roma West 33 kV | Power Factor | 98.97% | 90.42% | 90.27% | 90.12% | 89.99%
SW | F127R_Roma West 33 kV | Rating (A) | 11600% | 17300% | 17300% | 17300% | 17300%
SW | F127R_Roma West 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F127R_Roma West 33 kV | Min Voltage at Constrained Conductor (pu) | 100.6% | 105.6% | 105.7% | 105.7% | 105.7%
SW | F217R_St George 66 kV | % of Rated A | 18.54% | 22.49% | 22.36% | 22.22% | 22.11%
SW | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b
SW | F217R_St George 66 kV | Loading (A) | 8286% | 8793% | 8741% | 8689% | 8647%
SW | F217R_St George 66 kV | Loading (MVA) | 963.9% | 2134% | 2122% | 2109% | 2099%
SW | F217R_St George 66 kV | Loading (MW) | 890.9% | 1841% | 1826% | 1811% | 1799%
SW | F217R_St George 66 kV | Power Factor | 92.43% | 86.29% | 86.08% | 85.87% | 85.7%
SW | F217R_St George 66 kV | Rating (A) | 44700% | 39100% | 39100% | 39100% | 39100%
SW | F217R_St George 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F217R_St George 66 kV | Min Voltage at Constrained Conductor (pu) | 101.8% | 106.1% | 106.2% | 106.2% | 106.2%
SW | F7164 | % of Rated A | 47.45% | 22.46% | 22.33% | 22.2% | 22.09%
SW | F7164 | Limiting Line Name | TR_LINE 158494_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1 | TR_LINE 158493_1
SW | F7164 | Loading (A) | 8209% | 8783% | 8731% | 8679% | 8637%
SW | F7164 | Loading (MVA) | 1994% | 2131% | 2119% | 2107% | 2096%
SW | F7164 | Loading (MW) | 1800% | 1839% | 1824% | 1809% | 1796%
SW | F7164 | Power Factor | 90.3% | 86.28% | 86.08% | 85.86% | 85.69%
SW | F7164 | Rating (A) | 17300% | 39100% | 39100% | 39100% | 39100%
SW | F7164 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7164 | Min Voltage at Constrained Conductor (pu) | 105.6% | 106.1% | 106.2% | 106.2% | 106.2%
SW | F7174 | % of Rated A | 47.47% | 66.25% | 66.22% | 66.19% | 66.17%
SW | F7174 | Limiting Line Name | TR_LINE 158493_1(1) | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2
SW | F7174 | Loading (A) | 8212% | 6161% | 6159% | 6156% | 6154%
SW | F7174 | Loading (MVA) | 1995% | 358.8% | 358.8% | 358.8% | 358.8%
SW | F7174 | Loading (MW) | 1801% | 356.9% | 356.9% | 356.9% | 356.9%
SW | F7174 | Power Factor | 90.31% | 99.49% | 99.49% | 99.49% | 99.49%
SW | F7174 | Rating (A) | 17300% | 9300% | 9300% | 9300% | 9300%
SW | F7174 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7174 | Min Voltage at Constrained Conductor (pu) | 105.6% | 101.9% | 101.9% | 102% | 102%
SW | F7490 | % of Rated A | 22.3% | 7.798% | 8.457% | 9.104% | 9.631%
SW | F7490 | Limiting Line Name | TR_LINE 158494_b | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1 | TR_LINE 121841_1
SW | F7490 | Loading (A) | 8719% | 3564% | 3865% | 4160% | 4401%
SW | F7490 | Loading (MVA) | 2116% | 208.5% | 226.2% | 243.6% | 257.8%
SW | F7490 | Loading (MW) | 1822% | 208.1% | 225.7% | 243.1% | 257.2%
SW | F7490 | Power Factor | 86.11% | 99.82% | 99.79% | 99.77% | 99.74%
SW | F7490 | Rating (A) | 39100% | 45700% | 45700% | 45700% | 45700%
SW | F7490 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7490 | Min Voltage at Constrained Conductor (pu) | 106.1% | 102.3% | 102.4% | 102.4% | 102.5%
SW | F7491 | % of Rated A | 22.27% | 3.665% | 3.666% | 3.668% | 3.669%
SW | F7491 | Limiting Line Name | TR_LINE 158493_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1 | TR_LINE 163206_1
SW | F7491 | Loading (A) | 8709% | 388.5% | 388.6% | 388.8% | 388.9%
SW | F7491 | Loading (MVA) | 2113% | 22.26% | 22.28% | 22.3% | 22.31%
SW | F7491 | Loading (MW) | 1819% | 0.8238% | 0.8239% | 0.8241% | 0.8242%
SW | F7491 | Power Factor | 86.1% | 3.701% | 3.699% | 3.696% | 3.694%
SW | F7491 | Rating (A) | 39100% | 10600% | 10600% | 10600% | 10600%
SW | F7491 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F7491 | Min Voltage at Constrained Conductor (pu) | 106.1% | 100.3% | 100.3% | 100.3% | 100.4%
SW | 3153_Cecil Plains Road 33 kV | % of Rated A | 66.08% | 5.719% | 6.183% | 6.657% | 7.029%
SW | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_LINE 24115_1 | TR_LINE 24115_1 | TR_LINE 24115_1 | TR_LINE 24115_1
SW | 3153_Cecil Plains Road 33 kV | Loading (A) | 6146% | 726.3% | 785.2% | 845.4% | 892.7%
SW | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 358.7% | 42.67% | 46.14% | 49.69% | 52.47%
SW | 3153_Cecil Plains Road 33 kV | Loading (MW) | 356.9% | 42.26% | 45.78% | 49.38% | 52.2%
SW | 3153_Cecil Plains Road 33 kV | Power Factor | 99.49% | 98.88% | 99.06% | 99.21% | 99.3%
SW | 3153_Cecil Plains Road 33 kV | Rating (A) | 9300% | 12700% | 12700% | 12700% | 12700%
SW | 3153_Cecil Plains Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3153_Cecil Plains Road 33 kV | Min Voltage at Constrained Conductor (pu) | 102.1% | 102.8% | 102.8% | 102.8% | 102.8%
SW | 3154_Central Dalby 1 33 kV | % of Rated A | 2.305% | 11.85% | 13.34% | 11.83% | 12.89%
SW | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_CABLE 4402_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1
SW | 3154_Central Dalby 1 33 kV | Loading (A) | 1037% | 10402% | 11713% | 10383% | 11317%
SW | 3154_Central Dalby 1 33 kV | Loading (MVA) | 60.59% | 2083% | 2345% | 2078% | 2265%
SW | 3154_Central Dalby 1 33 kV | Loading (MW) | 59.79% | 2069% | 2337% | 2058% | 2250%
SW | 3154_Central Dalby 1 33 kV | Power Factor | 98.69% | 99.25% | 99.59% | 98.92% | 99.24%
SW | 3154_Central Dalby 1 33 kV | Rating (A) | 45000% | 87800% | 87800% | 87800% | 87800%
SW | 3154_Central Dalby 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3154_Central Dalby 1 33 kV | Min Voltage at Constrained Conductor (pu) | 102.2% | 105.1% | 105.1% | 105.1% | 105%
SW | 3178_Wilkie Creek 33 kV | % of Rated A | 4.129% | 11.85% | 13.34% | 11.83% | 12.89%
SW | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_CABLE 3771_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1
SW | 3178_Wilkie Creek 33 kV | Loading (A) | 384% | 10403% | 11714% | 10384% | 11319%
SW | 3178_Wilkie Creek 33 kV | Loading (MVA) | 21.93% | 2083% | 2346% | 2079% | 2266%
SW | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.8213% | 2069% | 2337% | 2058% | 2250%
SW | 3178_Wilkie Creek 33 kV | Power Factor | 3.745% | 99.24% | 99.58% | 98.9% | 99.22%
SW | 3178_Wilkie Creek 33 kV | Rating (A) | 9300% | 87800% | 87800% | 87800% | 87800%
SW | 3178_Wilkie Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3178_Wilkie Creek 33 kV | Min Voltage at Constrained Conductor (pu) | 99.92% | 105.1% | 105.1% | 105.1% | 105%
SW | 3900_Peranga 33 kV | % of Rated A | 7.341% | 18.64% | 19.16% | 19.74% | 20.01%
SW | 3900_Peranga 33 kV | Limiting Line Name | TR_CABLE 9120_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1
SW | 3900_Peranga 33 kV | Loading (A) | 734.1% | 19185% | 19720% | 20309% | 20585%
SW | 3900_Peranga 33 kV | Loading (MVA) | 43.03% | 3841% | 3947% | 4066% | 4121%
SW | 3900_Peranga 33 kV | Loading (MW) | 37.57% | 1992% | 2224% | 2456% | 2564%
SW | 3900_Peranga 33 kV | Power Factor | 87.29% | 51.83% | 56.31% | 60.4% | 62.2%
SW | 3900_Peranga 33 kV | Rating (A) | 10000% | 102900% | 102900% | 102900% | 102900%
SW | 3900_Peranga 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 3900_Peranga 33 kV | Min Voltage at Constrained Conductor (pu) | 102.5% | 105.1% | 105% | 105% | 105%
SW | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 5.857% | 18.65% | 19.17% | 19.74% | 20.01%
SW | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 5142% | 19187% | 19721% | 20311% | 20587%
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 1030% | 3841% | 3948% | 4066% | 4121%
SW | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 1013% | 1992% | 2224% | 2456% | 2563%
SW | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 98.34% | 51.83% | 56.31% | 60.4% | 62.2%
SW | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 87800% | 102900% | 102900% | 102900% | 102900%
SW | 7233_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7233_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 105.1% | 105% | 105% | 105%
SW | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 6.064% | 4.569% | 4.57% | 4.571% | 4.572%
SW | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 5324% | 1266% | 1266% | 1266% | 1267%
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 1066% | 254.5% | 254.6% | 254.8% | 255%
SW | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 1050% | 13.89% | 12.03% | 10.16% | 8.612%
SW | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 98.43% | 5.457% | 4.724% | 3.985% | 3.378%
SW | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 87800% | 27700% | 27700% | 27700% | 27700%
SW | 7234_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7234_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 105.5% | 105.6% | 105.6% | 105.7%
SW | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 9.349% | 19.2% | 19.64% | 20.08% | 20.45%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33947_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 178160_1
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 9620% | 4590% | 4693% | 4799% | 4887%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 1927% | 979.4% | 1003% | 1027% | 1047%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 871.8% | 509.9% | 553.1% | 595.3% | 629.1%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 45.24% | 52.06% | 55.15% | 57.94% | 60.06%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 102900% | 23900% | 23900% | 23900% | 23900%
SW | 728_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 728_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 112% | 112.2% | 112.4% | 112.5%
SW | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 9.35% | 4.845% | 4.845% | 4.845% | 4.846%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33960_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1 | TR_LINE 12102800_1
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 9621% | 1080% | 1081% | 1080% | 1081%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 1927% | 62.97% | 62.97% | 62.97% | 62.97%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 872.5% | 52.13% | 52.13% | 52.13% | 52.13%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 45.27% | 82.77% | 82.77% | 82.77% | 82.77%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 102900% | 22300% | 22300% | 22300% | 22300%
SW | 730_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 730_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 102% | 102% | 102% | 102%
SW | 7314_Dalby East 110 kV | % of Rated A | 4.553% | 7.086% | 7.684% | 8.272% | 8.751%
SW | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1 | TR_LINE 92498_1
SW | 7314_Dalby East 110 kV | Loading (A) | 1261% | 3777% | 4095% | 4409% | 4664%
SW | 7314_Dalby East 110 kV | Loading (MVA) | 252.8% | 220.8% | 239.6% | 258.1% | 273.1%
SW | 7314_Dalby East 110 kV | Loading (MW) | 15.92% | 220.6% | 239.4% | 257.9% | 273%
SW | 7314_Dalby East 110 kV | Power Factor | 6.3% | 99.89% | 99.91% | 99.93% | 99.94%
SW | 7314_Dalby East 110 kV | Rating (A) | 27700% | 53300% | 53300% | 53300% | 53300%
SW | 7314_Dalby East 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7314_Dalby East 110 kV | Min Voltage at Constrained Conductor (pu) | 105.2% | 102.2% | 102.2% | 102.2% | 102.3%
SW | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 8.063% | 11.18% | 9.922% | 8.843% | 9.523%
SW | 7448_South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13760_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 81367_1 | TR_LINE 81367_1
SW | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 3386% | 4194% | 3721% | 3316% | 3571%
SW | 7448_South Toowoomba-TWCE 110 kV | Loading (MVA) | 680% | 244.6% | 217.1% | 194.5% | 209.5%
SW | 7448_South Toowoomba-TWCE 110 kV | Loading (MW) | 286.5% | 243.4% | 215.7% | 194.5% | 209.5%
SW | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 42.13% | 99.5% | 99.34% | 99.99% | 100%
SW | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 42000% | 37500% | 37500% | 37500% | 37500%
SW | 7448_South Toowoomba-TWCE 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7448_South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor (pu) | 105.4% | 102% | 102% | 102.6% | 102.6%
SW | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 7.557% | 14.99% | 15% | 15.04% | 15.1%
SW | 7449 South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13761_1 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2 | TR_LINE 160964_2
SW | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 3174% | 5020% | 5024% | 5040% | 5060%
SW | 7449 South Toowoomba-TWCE 110 kV | Loading (MVA) | 637.3% | 293% | 293.6% | 294.8% | 296.1%
SW | 7449 South Toowoomba-TWCE 110 kV | Loading (MW) | 149.4% | 292.9% | 293.5% | 294.7% | 296%
SW | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 23.45% | 99.95% | 99.96% | 99.96% | 99.96%
SW | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 42000% | 33500% | 33500% | 33500% | 33500%
SW | 7449 South Toowoomba-TWCE 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 7449 South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor (pu) | 105.4% | 102.1% | 102.2% | 102.3% | 102.3%
SW | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 18.42% | 6.686% | 7.241% | 7.784% | 8.234%
SW | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 178160_1 | TR_LINE 23047_1 | TR_LINE 23047_1 | TR_LINE 23047_1 | TR_LINE 23047_1
SW | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 4402% | 621.8% | 673.4% | 723.9% | 765.8%
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 908.4% | 36.4% | 39.46% | 42.47% | 44.96%
SW | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 461.2% | 36.39% | 39.45% | 42.45% | 44.94%
SW | 790_Warwick-Stanthorpe 110 kV | Power Factor | 50.77% | 99.98% | 99.97% | 99.96% | 99.96%
SW | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 23900% | 9300% | 9300% | 9300% | 9300%
SW | 790_Warwick-Stanthorpe 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | 790_Warwick-Stanthorpe 110 kV | Min Voltage at Constrained Conductor (pu) | 108.3% | 102.4% | 102.5% | 102.6% | 102.7%
SW | EB10_Acland 33 kV | % of Rated A | 12.27% | 7.516% | 8.254% | 9.099% | 9.796%
SW | EB10_Acland 33 kV | Limiting Line Name | TR_CABLE 104_1 | TR_LINE 84666_1 | TR_LINE 76815_4 | TR_LINE 76815_4 | TR_LINE 76815_4
SW | EB10_Acland 33 kV | Loading (A) | 1141% | 1075% | 1180% | 1301% | 1401%
SW | EB10_Acland 33 kV | Loading (MVA) | 66.85% | 62.76% | 68.78% | 75.88% | 81.75%
SW | EB10_Acland 33 kV | Loading (MW) | 56.29% | 59.71% | 65.84% | 73.27% | 79.37%
SW | EB10_Acland 33 kV | Power Factor | 83.95% | 95.14% | 95.72% | 96.56% | 97.09%
SW | EB10_Acland 33 kV | Rating (A) | 9300% | 14300% | 14300% | 14300% | 14300%
SW | EB10_Acland 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | EB10_Acland 33 kV | Min Voltage at Constrained Conductor (pu) | 102.5% | 102.2% | 102% | 102% | 102.1%
SW | F008D_Central Dalby 2 33 kV | % of Rated A | 2.206% | 39.32% | 39.22% | 39.1% | 39.01%
SW | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_CABLE 5204_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1
SW | F008D_Central Dalby 2 33 kV | Loading (A) | 1103% | 6487% | 6471% | 6451% | 6436%
SW | F008D_Central Dalby 2 33 kV | Loading (MVA) | 64.4% | 377.3% | 376.6% | 375.7% | 375%
SW | F008D_Central Dalby 2 33 kV | Loading (MW) | 63.38% | 376.2% | 375.5% | 374.6% | 374%
SW | F008D_Central Dalby 2 33 kV | Power Factor | 98.12% | 99.72% | 99.71% | 99.71% | 99.71%
SW | F008D_Central Dalby 2 33 kV | Rating (A) | 50000% | 16500% | 16500% | 16500% | 16500%
SW | F008D_Central Dalby 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F008D_Central Dalby 2 33 kV | Min Voltage at Constrained Conductor (pu) | 102.1% | 101.7% | 101.8% | 101.8% | 101.9%
SW | F019D_West Dalby No 1 33 kV | % of Rated A | 0.7408% | 8.039% | 8.251% | 8.465% | 8.636%
SW | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW | F019D_West Dalby No 1 33 kV | Loading (A) | 277.8% | 5105% | 5239% | 5375% | 5484%
SW | F019D_West Dalby No 1 33 kV | Loading (MVA) | 16.21% | 324% | 333% | 342.2% | 349.6%
SW | F019D_West Dalby No 1 33 kV | Loading (MW) | 7.76% | 200.5% | 214.8% | 228.7% | 239.6%
SW | F019D_West Dalby No 1 33 kV | Power Factor | 47.86% | 61.87% | 64.49% | 66.83% | 68.54%
SW | F019D_West Dalby No 1 33 kV | Rating (A) | 37500% | 63500% | 63500% | 63500% | 63500%
SW | F019D_West Dalby No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F019D_West Dalby No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 102.1% | 111% | 111.2% | 111.4% | 111.5%
SW | F039D_West Dalby No 2 33 kV | % of Rated A | 16.04% | 2.638% | 3.586% | 4.534% | 5.278%
SW | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_CABLE 139_1 | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 60091_1
SW | F039D_West Dalby No 2 33 kV | Loading (A) | 4555% | 881.2% | 1198% | 1514% | 1763%
SW | F039D_West Dalby No 2 33 kV | Loading (MVA) | 265.8% | 53.06% | 72.14% | 91.29% | 106.3%
SW | F039D_West Dalby No 2 33 kV | Loading (MW) | 265.6% | 52.7% | 71.93% | 91.19% | 106.3%
SW | F039D_West Dalby No 2 33 kV | Power Factor | 99.91% | 99.25% | 99.62% | 99.79% | 99.86%
SW | F039D_West Dalby No 2 33 kV | Rating (A) | 28400% | 33400% | 33400% | 33400% | 33400%
SW | F039D_West Dalby No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F039D_West Dalby No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 102.1% | 105.3% | 105.4% | 105.5% | 105.5%
SW | F095D_Kaimkillenbun 33 kV | % of Rated A | 6.073% | 7.968% | 8.491% | 8.984% | 9.342%
SW | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_LINE 23047_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW | F095D_Kaimkillenbun 33 kV | Loading (A) | 564.8% | 2685% | 2861% | 3028% | 3148%
SW | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 33.12% | 157.8% | 168.1% | 178% | 185.1%
SW | F095D_Kaimkillenbun 33 kV | Loading (MW) | 33.12% | 157.8% | 168.1% | 178% | 185.1%
SW | F095D_Kaimkillenbun 33 kV | Power Factor | 99.98% | 99.99% | 99.98% | 99.98% | 99.98%
SW | F095D_Kaimkillenbun 33 kV | Rating (A) | 9300% | 33700% | 33700% | 33700% | 33700%
SW | F095D_Kaimkillenbun 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F095D_Kaimkillenbun 33 kV | Min Voltage at Constrained Conductor (pu) | 102.6% | 102.8% | 102.8% | 102.9% | 102.9%
SW | F097D_Jandowae 33 kV | % of Rated A | 9.189% | 31.1% | 31.29% | 31.49% | 31.67%
SW | F097D_Jandowae 33 kV | Limiting Line Name | TR_CABLE 8481_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW | F097D_Jandowae 33 kV | Loading (A) | 918.9% | 4447% | 4474% | 4504% | 4529%
SW | F097D_Jandowae 33 kV | Loading (MVA) | 53.98% | 282.4% | 284.1% | 286.2% | 287.9%
SW | F097D_Jandowae 33 kV | Loading (MW) | 53.37% | 142.9% | 146.3% | 149.9% | 153%
SW | F097D_Jandowae 33 kV | Power Factor | 98.77% | 49.98% | 50.84% | 51.72% | 52.49%
SW | F097D_Jandowae 33 kV | Rating (A) | 10000% | 14300% | 14300% | 14300% | 14300%
SW | F097D_Jandowae 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F097D_Jandowae 33 kV | Min Voltage at Constrained Conductor (pu) | 102.8% | 111.1% | 111.1% | 111.2% | 111.2%
SW | F099D_Warra 33 kV | % of Rated A | 53.66% | 28.35% | 29.23% | 30.13% | 30.86%
SW | F099D_Warra 33 kV | Limiting Line Name | TR_CABLE 132_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1 | TR_LINE 193128_1
SW | F099D_Warra 33 kV | Loading (A) | 5366% | 3459% | 3566% | 3676% | 3765%
SW | F099D_Warra 33 kV | Loading (MVA) | 310.3% | 220.9% | 228.1% | 235.5% | 240.5%
SW | F099D_Warra 33 kV | Loading (MW) | 310.1% | 132.8% | 144% | 155.1% | 164%
SW | F099D_Warra 33 kV | Power Factor | 99.91% | 60.13% | 63.15% | 65.84% | 68.16%
SW | F099D_Warra 33 kV | Rating (A) | 10000% | 12200% | 12200% | 12200% | 12200%
SW | F099D_Warra 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F099D_Warra 33 kV | Min Voltage at Constrained Conductor (pu) | 101.2% | 111.7% | 111.9% | 112.1% | 111.7%
SW | F2060_Sladevale 1 33kV | % of Rated A | 7.728% | 1.625% | 1.628% | 1.631% | 1.632%
SW | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW | F2060_Sladevale 1 33kV | Loading (A) | 4907% | 250.3% | 250.7% | 251.1% | 251.4%
SW | F2060_Sladevale 1 33kV | Loading (MVA) | 301.2% | 15.88% | 15.93% | 15.99% | 16.03%
SW | F2060_Sladevale 1 33kV | Loading (MW) | 184.3% | 0.006663% | 0.006683% | 0.006707% | 0.006723%
SW | F2060_Sladevale 1 33kV | Power Factor | 61.19% | 0.04176% | 0.04176% | 0.04176% | 0.04176%
SW | F2060_Sladevale 1 33kV | Rating (A) | 63500% | 15400% | 15400% | 15400% | 15400%
SW | F2060_Sladevale 1 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2060_Sladevale 1 33kV | Min Voltage at Constrained Conductor (pu) | 107.4% | 111% | 111.2% | 111.4% | 111.5%
SW | F2325_Broxburn 33 kV | % of Rated A | 1.519% | 74.26% | 77.41% | 80.56% | 83.13%
SW | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 60091_1 | TR_LINE 195683_1 | TR_LINE 195683_1 | TR_LINE 195683_1 | TR_LINE 195683_1
SW | F2325_Broxburn 33 kV | Loading (A) | 507.4% | 11436% | 11920% | 12406% | 12802%
SW | F2325_Broxburn 33 kV | Loading (MVA) | 31.21% | 700.5% | 732.5% | 764.9% | 791.2%
SW | F2325_Broxburn 33 kV | Loading (MW) | 30.43% | 507.5% | 550.3% | 592.1% | 625.6%
SW | F2325_Broxburn 33 kV | Power Factor | 97.45% | 72.45% | 75.12% | 77.41% | 79.07%
SW | F2325_Broxburn 33 kV | Rating (A) | 33400% | 15400% | 15400% | 15400% | 15400%
SW | F2325_Broxburn 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2325_Broxburn 33 kV | Min Voltage at Constrained Conductor (pu) | 107.6% | 106.6% | 106.9% | 107.2% | 107.4%
SW | F2450_Carrington Road 33 kV | % of Rated A | 7.315% | 18.86% | 19.58% | 20.36% | 21.01%
SW | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW | F2450_Carrington Road 33 kV | Loading (A) | 2465% | 9995% | 10377% | 10790% | 11137%
SW | F2450_Carrington Road 33 kV | Loading (MVA) | 145.4% | 611.9% | 635.4% | 661% | 682.4%
SW | F2450_Carrington Road 33 kV | Loading (MW) | 145.4% | 362.5% | 403.6% | 445.3% | 478.8%
SW | F2450_Carrington Road 33 kV | Power Factor | 99.99% | 59.24% | 63.52% | 67.37% | 70.17%
SW | F2450_Carrington Road 33 kV | Rating (A) | 33700% | 53000% | 53000% | 53000% | 53000%
SW | F2450_Carrington Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2450_Carrington Road 33 kV | Min Voltage at Constrained Conductor (pu) | 103.2% | 107.1% | 107.1% | 107.2% | 107.2%
SW | F2460_Cecil Plains 33 kV | % of Rated A | 30.91% | 18.76% | 19.48% | 20.26% | 20.91%
SW | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW | F2460_Cecil Plains 33 kV | Loading (A) | 4420% | 9945% | 10326% | 10737% | 11082%
SW | F2460_Cecil Plains 33 kV | Loading (MVA) | 280.4% | 608.9% | 632.3% | 657.8% | 679%
SW | F2460_Cecil Plains 33 kV | Loading (MW) | 139.4% | 360.5% | 401.4% | 442.9% | 476.3%
SW | F2460_Cecil Plains 33 kV | Power Factor | 49.08% | 59.21% | 63.49% | 67.34% | 70.14%
SW | F2460_Cecil Plains 33 kV | Rating (A) | 14300% | 53000% | 53000% | 53000% | 53000%
SW | F2460_Cecil Plains 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2460_Cecil Plains 33 kV | Min Voltage at Constrained Conductor (pu) | 111% | 107.1% | 107.1% | 107.2% | 107.2%
SW | F2520_Clifton 33 kV | % of Rated A | 27.42% | 0.3092% | 0.3091% | 0.3091% | 0.3091%
SW | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 193128_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW | F2520_Clifton 33 kV | Loading (A) | 3346% | 154.6% | 154.6% | 154.6% | 154.6%
SW | F2520_Clifton 33 kV | Loading (MVA) | 213.3% | 9.362% | 9.358% | 9.36% | 9.357%
SW | F2520_Clifton 33 kV | Loading (MW) | 120.5% | 0.1319% | 0.1319% | 0.1319% | 0.1319%
SW | F2520_Clifton 33 kV | Power Factor | 56.48% | 1.153% | 1.153% | 1.153% | 1.153%
SW | F2520_Clifton 33 kV | Rating (A) | 12200% | 50000% | 50000% | 50000% | 50000%
SW | F2520_Clifton 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2520_Clifton 33 kV | Min Voltage at Constrained Conductor (pu) | 111.5% | 105.9% | 105.9% | 105.9% | 105.9%
SW | F2777_East Stanthorpe 33 kV | % of Rated A | 1.575% | 1.992% | 2.222% | 2.431% | 2.569%
SW | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 24111_1 | TR_LINE 24111_1 | TR_LINE 24111_1 | TR_LINE 24111_1
SW | F2777_East Stanthorpe 33 kV | Loading (A) | 242.5% | 493.9% | 551% | 602.9% | 637%
SW | F2777_East Stanthorpe 33 kV | Loading (MVA) | 14.88% | 29.17% | 32.54% | 35.61% | 37.62%
SW | F2777_East Stanthorpe 33 kV | Loading (MW) | 0.006267% | 29% | 32.4% | 35.49% | 37.51%
SW | F2777_East Stanthorpe 33 kV | Power Factor | 0.04193% | 99.35% | 99.51% | 99.61% | 99.67%
SW | F2777_East Stanthorpe 33 kV | Rating (A) | 15400% | 24800% | 24800% | 24800% | 24800%
SW | F2777_East Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2777_East Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 107.4% | 103.3% | 103.3% | 103.3% | 103.3%
SW | F2780_East Warwick No 1 33 kV | % of Rated A | 9.12% | 75.54% | 79.5% | 28.54% | 29.73%
SW | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 216737_1 | TR_LINE 216737_1 | TR_LINE 216402_1 | TR_LINE 216402_1
SW | F2780_East Warwick No 1 33 kV | Loading (A) | 4834% | 18734% | 19716% | 4823% | 5025%
SW | F2780_East Warwick No 1 33 kV | Loading (MVA) | 295.9% | 1121% | 1180% | 288.9% | 301.1%
SW | F2780_East Warwick No 1 33 kV | Loading (MW) | 103.6% | 1121% | 1179% | 288.7% | 300.9%
SW | F2780_East Warwick No 1 33 kV | Power Factor | 35.02% | 99.93% | 99.91% | 99.95% | 99.95%
SW | F2780_East Warwick No 1 33 kV | Rating (A) | 53000% | 24800% | 24800% | 16900% | 16900%
SW | F2780_East Warwick No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2780_East Warwick No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 107.1% | 104.7% | 104.7% | 104.7% | 104.8%
SW | F2785_East Warwick No 2 33 kV | % of Rated A | 9.075% | 13.65% | 15.57% | 17.42% | 18.88%
SW | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 120572_1 | TR_LINE 120572_1 | TR_LINE 120572_1 | TR_LINE 120572_1
SW | F2785_East Warwick No 2 33 kV | Loading (A) | 4810% | 8424% | 9604% | 10749% | 11649%
SW | F2785_East Warwick No 2 33 kV | Loading (MVA) | 294.5% | 510.9% | 582.4% | 652% | 706.5%
SW | F2785_East Warwick No 2 33 kV | Loading (MW) | 103% | 510.5% | 581.8% | 651.1% | 705.3%
SW | F2785_East Warwick No 2 33 kV | Power Factor | 34.98% | 99.92% | 99.89% | 99.86% | 99.83%
SW | F2785_East Warwick No 2 33 kV | Rating (A) | 53000% | 61700% | 61700% | 61700% | 61700%
SW | F2785_East Warwick No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F2785_East Warwick No 2 33 kV | Min Voltage at Constrained Conductor (pu) | 107.1% | 106.1% | 106.1% | 106.1% | 106.1%
SW | F3040 Hampton Street | % of Rated A | 0.3092% | 7.464% | 7.503% | 7.546% | 7.583%
SW | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW | F3040 Hampton Street | Loading (A) | 154.6% | 4740% | 4764% | 4792% | 4815%
SW | F3040 Hampton Street | Loading (MVA) | 9.362% | 300.8% | 302.8% | 305.1% | 307%
SW | F3040 Hampton Street | Loading (MW) | 0.1319% | 50.17% | 57.52% | 64.83% | 70.93%
SW | F3040 Hampton Street | Power Factor | 1.153% | 16.55% | 18.87% | 21.13% | 22.99%
SW | F3040 Hampton Street | Rating (A) | 50000% | 63500% | 63500% | 63500% | 63500%
SW | F3040 Hampton Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3040 Hampton Street | Min Voltage at Constrained Conductor (pu) | 105.9% | 111% | 111.2% | 111.4% | 111.5%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | % of Rated A | 24.03% | 1.608% | 2.542% | 3.677% | 4.615%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 216402_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (A) | 4061% | 204.2% | 322.8% | 467% | 586.2%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 240.1% | 11.99% | 18.78% | 26.87% | 33.75%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Loading (MW) | 240% | 7.386% | 16.35% | 25.33% | 32.55%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Power Factor | 99.97% | 61.62% | 87.06% | 94.27% | 96.47%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Rating (A) | 16900% | 12700% | 12700% | 12700% | 12700%
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3095_Highfields 33 kV ¦ F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor (pu) | 103.4% | 102.7% | 101.8% | 100.7% | 100.7%
SW | F3255_Jennings Street 33 kV | % of Rated A | 5.891% | 21.51% | 17.8% | 14.02% | 11%
SW | F3255_Jennings Street 33 kV | Limiting Line Name | TR_CABLE 7923_1 | TR_LINE 48564_1 | TR_LINE 48564_1 | TR_LINE 48564_1 | TR_LINE 48564_1
SW | F3255_Jennings Street 33 kV | Loading (A) | 3635% | 4753% | 3934% | 3099% | 2430%
SW | F3255_Jennings Street 33 kV | Loading (MVA) | 220.3% | 279.4% | 231.4% | 182.5% | 143.2%
SW | F3255_Jennings Street 33 kV | Loading (MW) | 220.3% | 279.3% | 231.3% | 182.3% | 143%
SW | F3255_Jennings Street 33 kV | Power Factor | 99.99% | 99.98% | 99.96% | 99.92% | 99.85%
SW | F3255_Jennings Street 33 kV | Rating (A) | 61700% | 22100% | 22100% | 22100% | 22100%
SW | F3255_Jennings Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3255_Jennings Street 33 kV | Min Voltage at Constrained Conductor (pu) | 106% | 102.8% | 102.9% | 103% | 103.1%
SW | F3315_Sladevale 2 33kV | % of Rated A | 7.202% | 7.121% | 5.981% | 4.835% | 3.943%
SW | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW | F3315_Sladevale 2 33kV | Loading (A) | 4573% | 4913% | 4127% | 3336% | 2721%
SW | F3315_Sladevale 2 33kV | Loading (MVA) | 280.7% | 288.1% | 241.9% | 195.7% | 159.6%
SW | F3315_Sladevale 2 33kV | Loading (MW) | 42.37% | 280.6% | 232.6% | 183.6% | 144.3%
SW | F3315_Sladevale 2 33kV | Power Factor | 14.97% | 97.38% | 96.12% | 93.83% | 90.41%
SW | F3315_Sladevale 2 33kV | Rating (A) | 63500% | 69000% | 69000% | 69000% | 69000%
SW | F3315_Sladevale 2 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3315_Sladevale 2 33kV | Min Voltage at Constrained Conductor (pu) | 107.4% | 102.6% | 102.6% | 102.6% | 102.6%
SW | F3530_Millmerran 33 kV | % of Rated A | 1.322% | 9.95% | 10.36% | 10.81% | 11.21%
SW | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 24237_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1
SW | F3530_Millmerran 33 kV | Loading (A) | 167.9% | 1154% | 1202% | 1254% | 1300%
SW | F3530_Millmerran 33 kV | Loading (MVA) | 9.849% | 69.5% | 72.39% | 75.59% | 78.37%
SW | F3530_Millmerran 33 kV | Loading (MW) | 2.846% | 66.42% | 69.46% | 72.82% | 75.73%
SW | F3530_Millmerran 33 kV | Power Factor | 28.89% | 95.45% | 95.84% | 96.22% | 96.51%
SW | F3530_Millmerran 33 kV | Rating (A) | 12700% | 11600% | 11600% | 11600% | 11600%
SW | F3530_Millmerran 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3530_Millmerran 33 kV | Min Voltage at Constrained Conductor (pu) | 102.6% | 105.3% | 105.4% | 105.5% | 105.5%
SW | F3815 North Street No 1 33 kV | % of Rated A | 0.6684% | 24.02% | 24.1% | 24.21% | 24.3%
SW | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 181524_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | F3815 North Street No 1 33 kV | Loading (A) | 230.6% | 5068% | 5084% | 5109% | 5128%
SW | F3815 North Street No 1 33 kV | Loading (MVA) | 13.46% | 298.3% | 299.1% | 300.7% | 301.8%
SW | F3815 North Street No 1 33 kV | Loading (MW) | 0.04298% | 24.03% | 32.91% | 42.07% | 49.33%
SW | F3815 North Street No 1 33 kV | Power Factor | 0.3193% | 8.037% | 10.98% | 13.97% | 16.32%
SW | F3815 North Street No 1 33 kV | Rating (A) | 34500% | 21100% | 21100% | 21100% | 21100%
SW | F3815 North Street No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3815 North Street No 1 33 kV | Min Voltage at Constrained Conductor (pu) | 102.1% | 103% | 102.9% | 103% | 103%
SW | F3820_Boundary Road 33 kV | % of Rated A | 2.108% | 17.63% | 17.63% | 17.62% | 17.62%
SW | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW | F3820_Boundary Road 33 kV | Loading (A) | 1455% | 4107% | 4108% | 4105% | 4106%
SW | F3820_Boundary Road 33 kV | Loading (MVA) | 85.63% | 240% | 240% | 240% | 240%
SW | F3820_Boundary Road 33 kV | Loading (MW) | 50.07% | 240% | 240% | 240% | 240%
SW | F3820_Boundary Road 33 kV | Power Factor | 58.48% | 100% | 100% | 100% | 100%
SW | F3820_Boundary Road 33 kV | Rating (A) | 69000% | 23300% | 23300% | 23300% | 23300%
SW | F3820_Boundary Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3820_Boundary Road 33 kV | Min Voltage at Constrained Conductor (pu) | 103% | 102.3% | 102.2% | 102.3% | 102.3%
SW | F3830_Norwin 33 kV | % of Rated A | 9.372% | 0.9686% | 1.719% | 2.568% | 3.251%
SW | F3830_Norwin 33 kV | Limiting Line Name | TR_LINE 23942_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_CABLE 106_1
SW | F3830_Norwin 33 kV | Loading (A) | 1087% | 290.6% | 515.8% | 770.4% | 975.3%
SW | F3830_Norwin 33 kV | Loading (MVA) | 66.88% | 17.52% | 31.13% | 46.54% | 58.95%
SW | F3830_Norwin 33 kV | Loading (MW) | 63.3% | 14.48% | 29.54% | 45.56% | 58.2%
SW | F3830_Norwin 33 kV | Power Factor | 94.55% | 82.57% | 94.86% | 97.88% | 98.71%
SW | F3830_Norwin 33 kV | Rating (A) | 11600% | 30000% | 30000% | 30000% | 30000%
SW | F3830_Norwin 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3830_Norwin 33 kV | Min Voltage at Constrained Conductor (pu) | 107.6% | 105.5% | 105.6% | 105.7% | 105.7%
SW | F3855 Omaras Road 33 kV | % of Rated A | 17.56% | 25.22% | 26.78% | 28.22% | 29.39%
SW | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | TR_LINE 216402_1 | TR_LINE 216402_1 | TR_LINE 216402_1 | TR_LINE 216402_1
SW | F3855 Omaras Road 33 kV | Loading (A) | 4091% | 4263% | 4525% | 4770% | 4967%
SW | F3855 Omaras Road 33 kV | Loading (MVA) | 240% | 257.6% | 273.7% | 288.9% | 301.1%
SW | F3855 Omaras Road 33 kV | Loading (MW) | 240% | 257.5% | 273.6% | 288.7% | 300.9%
SW | F3855 Omaras Road 33 kV | Power Factor | 100% | 99.96% | 99.96% | 99.95% | 99.95%
SW | F3855 Omaras Road 33 kV | Rating (A) | 23300% | 16900% | 16900% | 16900% | 16900%
SW | F3855 Omaras Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3855 Omaras Road 33 kV | Min Voltage at Constrained Conductor (pu) | 102.7% | 105.7% | 105.8% | 105.9% | 106%
SW | F3867_Pampas 33 kV | % of Rated A | 0.6721% | 2.922% | 3.64% | 4.412% | 5.014%
SW | F3867_Pampas 33 kV | Limiting Line Name | TR_LINE 177041_1 | TR_LINE 221370_1 | TR_LINE 221370_1 | TR_LINE 221370_1 | TR_LINE 221370_1
SW | F3867_Pampas 33 kV | Loading (A) | 356.2% | 417.9% | 520.5% | 630.9% | 717%
SW | F3867_Pampas 33 kV | Loading (MVA) | 21.91% | 26.8% | 33.4% | 40.51% | 46.06%
SW | F3867_Pampas 33 kV | Loading (MW) | 2.946% | 26.59% | 33.23% | 40.38% | 45.95%
SW | F3867_Pampas 33 kV | Power Factor | 13.44% | 99.21% | 99.5% | 99.67% | 99.75%
SW | F3867_Pampas 33 kV | Rating (A) | 53000% | 14300% | 14300% | 14300% | 14300%
SW | F3867_Pampas 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3867_Pampas 33 kV | Min Voltage at Constrained Conductor (pu) | 107.6% | 112.2% | 112.3% | 112.4% | 112.4%
SW | F3970_Pozieres 33 kV | % of Rated A | 2.08% | 23.07% | 23.01% | 23.01% | 22.98%
SW | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 23974_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | F3970_Pozieres 33 kV | Loading (A) | 320.3% | 4868% | 4856% | 4855% | 4849%
SW | F3970_Pozieres 33 kV | Loading (MVA) | 21.22% | 287.4% | 286.6% | 286.9% | 286.5%
SW | F3970_Pozieres 33 kV | Loading (MW) | 18.99% | 42.1% | 36.21% | 30.36% | 25.97%
SW | F3970_Pozieres 33 kV | Power Factor | 89.47% | 14.65% | 12.63% | 10.58% | 9.065%
SW | F3970_Pozieres 33 kV | Rating (A) | 15400% | 21100% | 21100% | 21100% | 21100%
SW | F3970_Pozieres 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor (pu) | 115.9% | 103.3% | 103.3% | 103.4% | 103.4%
SW | F3980_Purrawunda 33 kV | % of Rated A | 23.07% | 6.859% | 8.047% | 9.274% | 10.33%
SW | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1
SW | F3980_Purrawunda 33 kV | Loading (A) | 4867% | 4842% | 5681% | 6547% | 7293%
SW | F3980_Purrawunda 33 kV | Loading (MVA) | 286.5% | 285.2% | 334.5% | 385.8% | 429.8%
SW | F3980_Purrawunda 33 kV | Loading (MW) | 49.03% | 285.2% | 334.5% | 385.8% | 429.7%
SW | F3980_Purrawunda 33 kV | Power Factor | 17.11% | 100% | 99.99% | 99.99% | 99.99%
SW | F3980_Purrawunda 33 kV | Rating (A) | 21100% | 70600% | 70600% | 70600% | 70600%
SW | F3980_Purrawunda 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor (pu) | 103% | 103% | 103% | 103.1% | 103.1%
SW | F4005_Racecourse 33 kV | % of Rated A | 2.995% | 14.04% | 16% | 17.91% | 19.41%
SW | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 67_1 | TR_LINE 170027_1 | TR_LINE 170027_1 | TR_LINE 170027_1 | TR_LINE 170027_1
SW | F4005_Racecourse 33 kV | Loading (A) | 2114% | 8423% | 9602% | 10746% | 11646%
SW | F4005_Racecourse 33 kV | Loading (MVA) | 124.5% | 510.9% | 582.4% | 652% | 706.6%
SW | F4005_Racecourse 33 kV | Loading (MW) | 124.3% | 510.5% | 581.8% | 651.1% | 705.3%
SW | F4005_Racecourse 33 kV | Power Factor | 99.79% | 99.92% | 99.89% | 99.86% | 99.82%
SW | F4005_Racecourse 33 kV | Rating (A) | 70600% | 60000% | 60000% | 60000% | 60000%
SW | F4005_Racecourse 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4005_Racecourse 33 kV | Min Voltage at Constrained Conductor (pu) | 103% | 106.1% | 106.1% | 106.1% | 106.1%
SW | F4015_Ramsay Street 33 kV | % of Rated A | 5.97% | 56.26% | 59.09% | 39.27% | 40.39%
SW | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_CABLE 7922_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1
SW | F4015_Ramsay Street 33 kV | Loading (A) | 3582% | 23628% | 24818% | 16492% | 16962%
SW | F4015_Ramsay Street 33 kV | Loading (MVA) | 217.1% | 1398% | 1469% | 974.2% | 1002%
SW | F4015_Ramsay Street 33 kV | Loading (MW) | 217.1% | 1397% | 1467% | 974% | 1002%
SW | F4015_Ramsay Street 33 kV | Power Factor | 99.98% | 99.92% | 99.91% | 99.98% | 99.97%
SW | F4015_Ramsay Street 33 kV | Rating (A) | 60000% | 42000% | 42000% | 42000% | 42000%
SW | F4015_Ramsay Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4015_Ramsay Street 33 kV | Min Voltage at Constrained Conductor (pu) | 106.1% | 103.5% | 103.5% | 103.4% | 103.3%
SW | F4132_Shirley Road 33 kV | % of Rated A | 52.92% | 37.95% | 39.14% | 40.33% | 41.42%
SW | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1
SW | F4132_Shirley Road 33 kV | Loading (A) | 22227% | 11080% | 11428% | 11776% | 12096%
SW | F4132_Shirley Road 33 kV | Loading (MVA) | 1320% | 764.4% | 790.2% | 761.4% | 784.5%
SW | F4132_Shirley Road 33 kV | Loading (MW) | 1319% | 498.8% | 536.3% | 572.2% | 601.2%
SW | F4132_Shirley Road 33 kV | Power Factor | 99.95% | 65.25% | 67.86% | 75.14% | 76.62%
SW | F4132_Shirley Road 33 kV | Rating (A) | 42000% | 29200% | 29200% | 29200% | 29200%
SW | F4132_Shirley Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4132_Shirley Road 33 kV | Min Voltage at Constrained Conductor (pu) | 103.9% | 120.7% | 121% | 113.1% | 113.5%
SW | F4245_Stanthorpe 33 kV | % of Rated A | 36.37% | 0.4542% | 0.4541% | 0.4542% | 0.4541%
SW | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW | F4245_Stanthorpe 33 kV | Loading (A) | 10621% | 227.1% | 227.1% | 227.1% | 227%
SW | F4245_Stanthorpe 33 kV | Loading (MVA) | 708.4% | 13.75% | 13.75% | 13.75% | 13.75%
SW | F4245_Stanthorpe 33 kV | Loading (MW) | 456.4% | 0.2391% | 0.239% | 0.239% | 0.239%
SW | F4245_Stanthorpe 33 kV | Power Factor | 64.42% | 0.7761% | 0.7761% | 0.7761% | 0.7761%
SW | F4245_Stanthorpe 33 kV | Rating (A) | 29200% | 50000% | 50000% | 50000% | 50000%
SW | F4245_Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4245_Stanthorpe 33 kV | Min Voltage at Constrained Conductor (pu) | 116.7% | 105.9% | 105.9% | 105.9% | 105.9%
SW | F4470 Vacy Street | % of Rated A | 0.4542% | 11.66% | 12.67% | 13.63% | 14.42%
SW | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW | F4470 Vacy Street | Loading (A) | 227.1% | 4535% | 4927% | 5301% | 5607%
SW | F4470 Vacy Street | Loading (MVA) | 13.75% | 275.2% | 299% | 321.9% | 340.5%
SW | F4470 Vacy Street | Loading (MW) | 0.2391% | 275.1% | 299% | 321.9% | 340.5%
SW | F4470 Vacy Street | Power Factor | 0.7761% | 99.98% | 99.99% | 100% | 100%
SW | F4470 Vacy Street | Rating (A) | 50000% | 38900% | 38900% | 38900% | 38900%
SW | F4470 Vacy Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4470 Vacy Street | Min Voltage at Constrained Conductor (pu) | 105.9% | 106.2% | 106.2% | 106.2% | 106.2%
SW | F4605_West Warwick 33 kV | % of Rated A | 10.46% | 7.017% | 8.232% | 9.487% | 10.57%
SW | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1
SW | F4605_West Warwick 33 kV | Loading (A) | 4068% | 4842% | 5680% | 6546% | 7292%
SW | F4605_West Warwick 33 kV | Loading (MVA) | 249.1% | 285.2% | 334.5% | 385.8% | 429.8%
SW | F4605_West Warwick 33 kV | Loading (MW) | 249% | 285.2% | 334.5% | 385.8% | 429.7%
SW | F4605_West Warwick 33 kV | Power Factor | 99.97% | 100% | 99.99% | 99.99% | 99.99%
SW | F4605_West Warwick 33 kV | Rating (A) | 38900% | 69000% | 69000% | 69000% | 69000%
SW | F4605_West Warwick 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4605_West Warwick 33 kV | Min Voltage at Constrained Conductor (pu) | 107.1% | 103% | 103% | 103.1% | 103.1%
SW | F4685_Wyalla Street 33 kV | % of Rated A | 2.702% | 8.954% | 8.555% | 8.344% | 8.31%
SW | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1
SW | F4685_Wyalla Street 33 kV | Loading (A) | 1864% | 2364% | 2259% | 2203% | 2194%
SW | F4685_Wyalla Street 33 kV | Loading (MVA) | 109.8% | 472.7% | 451.6% | 440.4% | 438.6%
SW | F4685_Wyalla Street 33 kV | Loading (MW) | 109.8% | 164.2% | 94.14% | 25.14% | 30.7%
SW | F4685_Wyalla Street 33 kV | Power Factor | 99.99% | 34.74% | 20.85% | 5.707% | 6.854%
SW | F4685_Wyalla Street 33 kV | Rating (A) | 69000% | 26400% | 26400% | 26400% | 26400%
SW | F4685_Wyalla Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F4685_Wyalla Street 33 kV | Min Voltage at Constrained Conductor (pu) | 103% | 105% | 104.9% | 104.9% | 104.9%
SW | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 6.342% | 18.48% | 17.64% | 17.2% | 17.13%
SW | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 24297_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 1674% | 2347% | 2241% | 2184% | 2175%
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 334.8% | 469.3% | 448% | 436.8% | 434.9%
SW | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 116.1% | 164.1% | 94.03% | 25.04% | 30.57%
SW | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 34.66% | 34.96% | 20.99% | 5.732% | 6.936%
SW | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 26400% | 12700% | 12700% | 12700% | 12700%
SW | F5540_7244 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5540_7244 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 105% | 105% | 104.9% | 104.9% | 104.9%
SW | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 13.44% | 22.93% | 23.08% | 23.27% | 23.44%
SW | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140801_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 1707% | 6581% | 6624% | 6680% | 6728%
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 341.3% | 1295% | 1304% | 1315% | 1325%
SW | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 124.2% | 194.2% | 236.8% | 280.9% | 316%
SW | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 36.39% | 15% | 18.16% | 21.35% | 23.85%
SW | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 12700% | 28700% | 28700% | 28700% | 28700%
SW | F5545_7245 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5545_7245 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor (pu) | 105% | 103.3% | 103.3% | 103.4% | 103.4%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 11.61% | 22.95% | 23.1% | 23.29% | 23.46%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224268_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 3331% | 6587% | 6630% | 6685% | 6733%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 661.5% | 1296% | 1305% | 1317% | 1326%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 72.28% | 194.1% | 236.6% | 280.7% | 315.9%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 10.93% | 14.97% | 18.14% | 21.32% | 23.82%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 28700% | 28700% | 28700% | 28700% | 28700%
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5550_733(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 104.2% | 103.3% | 103.3% | 103.4% | 103.4%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 11.62% | 47.42% | 48.59% | 49.83% | 50.87%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 25640_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 3335% | 12188% | 12487% | 12805% | 13073%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 662.3% | 2442% | 2501% | 2565% | 2619%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 70.55% | 1211% | 1338% | 1464% | 1566%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 10.65% | 49.42% | 53.31% | 56.9% | 59.62%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 28700% | 25700% | 25700% | 25700% | 25700%
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5555_734(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor (pu) | 104.2% | 105.2% | 105.1% | 105.1% | 105.1%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 23.14% | 15.98% | 16.38% | 16.8% | 17.15%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 5946% | 12196% | 12495% | 12816% | 13087%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 1191% | 2456% | 2515% | 2580% | 2634%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 681.8% | 1264% | 1394% | 1523% | 1628%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 57.16% | 51.44% | 55.38% | 59.01% | 61.75%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 25700% | 76300% | 76300% | 76300% | 76300%
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5560_735(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 105.7% | 105.7% | 105.7% | 105.7%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 9.442% | 7.077% | 7.733% | 8.39% | 8.943%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141746_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 7412% | 2010% | 2196% | 2383% | 2540%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 1484% | 231.3% | 252.9% | 274.4% | 292.5%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 434.7% | 204.7% | 228.4% | 251.7% | 271%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 29.28% | 88.5% | 90.33% | 91.73% | 92.67%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 78500% | 28400% | 28400% | 28400% | 28400%
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW | F5565_736(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor (pu) | 105.1% | 100.7% | 100.7% | 100.7% | 100.7%
WB | 6112_Agnes Water 66 kV | % of Rated A | 6.066% | 4.098% | 4.093% | 4.088% | 4.083%
WB | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB | 6112_Agnes Water 66 kV | Loading (A) | 1723% | 1549% | 1547% | 1545% | 1543%
WB | 6112_Agnes Water 66 kV | Loading (MVA) | 199% | 371.7% | 371.3% | 370.8% | 370.4%
WB | 6112_Agnes Water 66 kV | Loading (MW) | 182% | 184.6% | 183.6% | 182.6% | 181.8%
WB | 6112_Agnes Water 66 kV | Power Factor | 91.46% | 49.67% | 49.45% | 49.25% | 49.08%
WB | 6112_Agnes Water 66 kV | Rating (A) | 28400% | 37800% | 37800% | 37800% | 37800%
WB | 6112_Agnes Water 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6112_Agnes Water 66 kV | Min Voltage at Constrained Conductor (pu) | 101.1% | 105% | 105% | 105% | 105%
WB | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 2.728% | 56.59% | 59.54% | 62.27% | 64.33%
WB | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 1031% | 22468% | 23637% | 24721% | 25539%
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 247.4% | 2611% | 2749% | 2876% | 2972%
WB | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 3.39% | 2429% | 2581% | 2721% | 2825%
WB | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 1.37% | 93.05% | 93.9% | 94.58% | 95.04%
WB | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 37800% | 39700% | 39700% | 39700% | 39700%
WB | 7188_Gin Gin - Korenan QR 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7188_Gin Gin - Korenan QR 132 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 101.6% | 101.7% | 101.7% | 101.8%
WB | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 23.28% | 67.34% | 70.33% | 73.25% | 75.54%
WB | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 9243% | 26734% | 27923% | 29079% | 29988%
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 1066% | 3102% | 3243% | 3379% | 3485%
WB | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 1023% | 2428% | 2613% | 2787% | 2921%
WB | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 95.98% | 78.29% | 80.57% | 82.49% | 83.82%
WB | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 39700% | 39700% | 39700% | 39700% | 39700%
WB | 6205_East Bundaberg-BUCE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6205_East Bundaberg-BUCE 66 kV | Min Voltage at Constrained Conductor (pu) | 100.9% | 100.6% | 100.7% | 100.7% | 100.7%
WB | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 35.06% | 17.47% | 18.88% | 20.19% | 21.24%
WB | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 50338_1 | TR_LINE 50338_1 | TR_LINE 50338_1 | TR_LINE 50338_1
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 13921% | 2307% | 2492% | 2665% | 2803%
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 1602% | 344.1% | 371.8% | 397.8% | 418.6%
WB | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 988.9% | 325.3% | 354.8% | 382.2% | 404%
WB | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 61.64% | 94.54% | 95.42% | 96.08% | 96.52%
WB | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 39700% | 13200% | 13200% | 13200% | 13200%
WB | 6302_Bundaberg Central - WEBU 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6302_Bundaberg Central - WEBU 66 kV | Min Voltage at Constrained Conductor (pu) | 100.3% | 130.5% | 130.5% | 130.6% | 130.6%
WB | 6366_Gootchie 66 kV | % of Rated A | 2.579% | 29.23% | 28.38% | 27.36% | 26.61%
WB | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 7245_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1
WB | 6366_Gootchie 66 kV | Loading (A) | 340.5% | 19844% | 19271% | 18575% | 18065%
WB | 6366_Gootchie 66 kV | Loading (MVA) | 40.17% | 4749% | 4612% | 4445% | 4323%
WB | 6366_Gootchie 66 kV | Loading (MW) | 0.01353% | 2699% | 2441% | 2183% | 1983%
WB | 6366_Gootchie 66 kV | Power Factor | 0.03369% | 56.83% | 52.93% | 49.1% | 45.87%
WB | 6366_Gootchie 66 kV | Rating (A) | 13200% | 67900% | 67900% | 67900% | 67900%
WB | 6366_Gootchie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 6366_Gootchie 66 kV | Min Voltage at Constrained Conductor (pu) | 103.2% | 104.7% | 104.7% | 104.7% | 104.7%
WB | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 19.1% | 2.711% | 2.711% | 2.711% | 2.711%
WB | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 12972% | 1529% | 1529% | 1529% | 1529%
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 3112% | 369.4% | 369.4% | 369.4% | 369.4%
WB | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 1813% | 130.2% | 130.2% | 130.2% | 130.2%
WB | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 58.27% | 35.25% | 35.25% | 35.25% | 35.26%
WB | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 67900% | 56400% | 56400% | 56400% | 56400%
WB | 7187_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7187_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 105.7% | 105.7% | 105.7% | 105.7%
WB | 7190_Woolooga-Mungar 132 kV | % of Rated A | 2.711% | 1.223% | 1.222% | 1.222% | 1.222%
WB | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 6802_2 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB | 7190_Woolooga-Mungar 132 kV | Loading (A) | 1529% | 1083% | 1083% | 1083% | 1083%
WB | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 369.4% | 265.1% | 265.1% | 265.1% | 265.1%
WB | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 130.2% | 260% | 260% | 260% | 260%
WB | 7190_Woolooga-Mungar 132 kV | Power Factor | 35.26% | 98.09% | 98.09% | 98.09% | 98.09%
WB | 7190_Woolooga-Mungar 132 kV | Rating (A) | 56400% | 88600% | 88600% | 88600% | 88600%
WB | 7190_Woolooga-Mungar 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7190_Woolooga-Mungar 132 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 107% | 107.1% | 107.1% | 107.1%
WB | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 1.221% | 93.08% | 93.22% | 93.02% | 92.86%
WB | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 1082% | 23084% | 23119% | 23068% | 23030%
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 265.1% | 5655% | 5667% | 5655% | 5646%
WB | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 260% | 5479% | 5485% | 5478% | 5472%
WB | 7204_Bundaberg - Clayton 132 kV | Power Factor | 98.08% | 96.64% | 96.55% | 96.63% | 96.69%
WB | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 88600% | 24800% | 24800% | 24800% | 24800%
WB | 7204_Bundaberg - Clayton 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7204_Bundaberg - Clayton 132 kV | Min Voltage at Constrained Conductor (pu) | 107.2% | 106.8% | 106.9% | 106.9% | 106.9%
WB | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 56.19% | 34.59% | 36.03% | 37.41% | 38.49%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 13934% | 37777% | 39343% | 40856% | 42030%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 3415% | 9114% | 9495% | 9858% | 10140%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 3304% | 8993% | 9369% | 9746% | 10038%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 96.75% | 98.68% | 98.67% | 98.86% | 98.99%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 24800% | 109200% | 109200% | 109200% | 109200%
WB | 7215_Bundaberg - ISIS No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7215_Bundaberg - ISIS No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 106.9% | 105.5% | 105.5% | 105.5% | 105.5%
WB | 7315_Aramara 132 kV | % of Rated A | 18.36% | 34.59% | 36.03% | 37.41% | 38.49%
WB | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 88000_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1
WB | 7315_Aramara 132 kV | Loading (A) | 20047% | 37776% | 39342% | 40855% | 42029%
WB | 7315_Aramara 132 kV | Loading (MVA) | 4840% | 9114% | 9495% | 9858% | 10140%
WB | 7315_Aramara 132 kV | Loading (MW) | 4754% | 8993% | 9368% | 9746% | 10037%
WB | 7315_Aramara 132 kV | Power Factor | 98.22% | 98.68% | 98.67% | 98.86% | 98.99%
WB | 7315_Aramara 132 kV | Rating (A) | 109200% | 109200% | 109200% | 109200% | 109200%
WB | 7315_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7315_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 105.5% | 105.5% | 105.5% | 105.5%
WB | 7316_Aramara 132 kV | % of Rated A | 18.36% | 93.02% | 93.16% | 92.95% | 92.8%
WB | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88004_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB | 7316_Aramara 132 kV | Loading (A) | 20045% | 23068% | 23103% | 23053% | 23015%
WB | 7316_Aramara 132 kV | Loading (MVA) | 4839% | 5651% | 5663% | 5651% | 5642%
WB | 7316_Aramara 132 kV | Loading (MW) | 4754% | 5475% | 5481% | 5475% | 5469%
WB | 7316_Aramara 132 kV | Power Factor | 98.22% | 96.87% | 96.78% | 96.86% | 96.91%
WB | 7316_Aramara 132 kV | Rating (A) | 109200% | 24800% | 24800% | 24800% | 24800%
WB | 7316_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7316_Aramara 132 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 107.1% | 107.2% | 107.2% | 107.2%
WB | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 56.07% | 30.01% | 32.65% | 34.63% | 36.19%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 13905% | 16924% | 18412% | 19533% | 20412%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 3408% | 4115% | 4483% | 4757% | 4971%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 3297% | 3711% | 4057% | 4383% | 4634%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 96.75% | 90.06% | 90.4% | 92.08% | 93.17%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 24800% | 56400% | 56400% | 56400% | 56400%
WB | 7328_Bundaberg - ISIS No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7328_Bundaberg - ISIS No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 107.2% | 106.3% | 106.4% | 106.4% | 106.4%
WB | 7329_Maryborough 132 kV | % of Rated A | 14.28% | 30.01% | 32.65% | 34.63% | 36.19%
WB | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 120325_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1
WB | 7329_Maryborough 132 kV | Loading (A) | 8054% | 16924% | 18412% | 19533% | 20412%
WB | 7329_Maryborough 132 kV | Loading (MVA) | 1959% | 4115% | 4483% | 4757% | 4971%
WB | 7329_Maryborough 132 kV | Loading (MW) | 1672% | 3711% | 4057% | 4383% | 4634%
WB | 7329_Maryborough 132 kV | Power Factor | 85.28% | 90.06% | 90.4% | 92.08% | 93.17%
WB | 7329_Maryborough 132 kV | Rating (A) | 56400% | 56400% | 56400% | 56400% | 56400%
WB | 7329_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7329_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 106.4% | 106.3% | 106.4% | 106.4% | 106.4%
WB | 7330_Maryborough 132 kV | % of Rated A | 14.27% | 8.856% | 9.404% | 9.958% | 10.43%
WB | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 7684_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB | 7330_Maryborough 132 kV | Loading (A) | 8050% | 2196% | 2332% | 2470% | 2587%
WB | 7330_Maryborough 132 kV | Loading (MVA) | 1959% | 530.6% | 563.4% | 596.6% | 624.9%
WB | 7330_Maryborough 132 kV | Loading (MW) | 1672% | 411.2% | 455.1% | 497.9% | 533.3%
WB | 7330_Maryborough 132 kV | Power Factor | 85.28% | 77.43% | 80.7% | 83.37% | 85.26%
WB | 7330_Maryborough 132 kV | Rating (A) | 56400% | 24800% | 24800% | 24800% | 24800%
WB | 7330_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 7330_Maryborough 132 kV | Min Voltage at Constrained Conductor (pu) | 106.4% | 105.7% | 105.7% | 105.7% | 105.7%
WB | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 7.598% | 8.856% | 9.404% | 9.958% | 10.43%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 1884% | 2196% | 2332% | 2470% | 2587%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 455.2% | 530.6% | 563.4% | 596.6% | 624.9%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 335.7% | 411.2% | 455.1% | 497.9% | 533.3%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 73.7% | 77.43% | 80.7% | 83.37% | 85.26%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 24800% | 24800% | 24800% | 24800% | 24800%
WB | 764_Woolooga-Kilkivan No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 764_Woolooga-Kilkivan No 1 132 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 105.7% | 105.7% | 105.7% | 105.7%
WB | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 7.598% | 91.02% | 92.01% | 93.32% | 94.35%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 1884% | 22573% | 22819% | 23144% | 23400%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 455.2% | 5529% | 5593% | 5674% | 5737%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 335.7% | 5510% | 5572% | 5654% | 5718%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 73.7% | 99.64% | 99.61% | 99.64% | 99.67%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 24800% | 24800% | 24800% | 24800% | 24800%
WB | 765_Woolooga-Kilkivan No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 765_Woolooga-Kilkivan No 2 132 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 107% | 107.1% | 107.1% | 107.1%
WB | 784_ISIS 132 kV | % of Rated A | 51.28% | 91.35% | 92.34% | 93.66% | 94.69%
WB | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 6779_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB | 784_ISIS 132 kV | Loading (A) | 12717% | 22654% | 22901% | 23227% | 23484%
WB | 784_ISIS 132 kV | Loading (MVA) | 3108% | 5549% | 5613% | 5694% | 5757%
WB | 784_ISIS 132 kV | Loading (MW) | 3096% | 5530% | 5592% | 5674% | 5739%
WB | 784_ISIS 132 kV | Power Factor | 99.59% | 99.65% | 99.62% | 99.66% | 99.69%
WB | 784_ISIS 132 kV | Rating (A) | 24800% | 24800% | 24800% | 24800% | 24800%
WB | 784_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 784_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 106.8% | 107.1% | 107.2% | 107.2% | 107.2%
WB | 785_ISIS 132 kV | % of Rated A | 52.02% | 70.02% | 68% | 65.54% | 63.75%
WB | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1
WB | 785_ISIS 132 kV | Loading (A) | 12902% | 19817% | 19244% | 18549% | 18041%
WB | 785_ISIS 132 kV | Loading (MVA) | 3154% | 4742% | 4606% | 4439% | 4318%
WB | 785_ISIS 132 kV | Loading (MW) | 3141% | 2687% | 2429% | 2171% | 1971%
WB | 785_ISIS 132 kV | Power Factor | 99.6% | 56.61% | 52.71% | 48.88% | 45.65%
WB | 785_ISIS 132 kV | Rating (A) | 24800% | 28300% | 28300% | 28300% | 28300%
WB | 785_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 785_ISIS 132 kV | Min Voltage at Constrained Conductor (pu) | 106.9% | 104.7% | 104.7% | 104.7% | 104.7%
WB | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 45.8% | 12.9% | 14.33% | 15.77% | 16.95%
WB | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 12960% | 7068% | 7855% | 8641% | 9290%
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 3109% | 853.8% | 949.3% | 1045% | 1124%
WB | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 1804% | 834% | 932.9% | 1031% | 1112%
WB | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 58.03% | 97.57% | 98.2% | 98.66% | 98.94%
WB | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 28300% | 54800% | 54800% | 54800% | 54800%
WB | 786_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | 786_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 105.7% | 105.7% | 105.7% | 105.7%
WB | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 5.798% | 12.9% | 14.33% | 15.77% | 16.95%
WB | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7977_1 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2
WB | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 3178% | 7067% | 7854% | 8640% | 9290%
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 383.9% | 854.3% | 952.5% | 1050% | 1131%
WB | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 363.9% | 839.7% | 939.9% | 1040% | 1122%
WB | M001_Tarong-Kingaroy East 66 kV | Power Factor | 94.73% | 97.59% | 98.21% | 98.67% | 98.95%
WB | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 54800% | 54800% | 54800% | 54800% | 54800%
WB | M001_Tarong-Kingaroy East 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M001_Tarong-Kingaroy East 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 105.7% | 105.7% | 105.7% | 105.7%
WB | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 5.8% | 34.26% | 36.53% | 38.67% | 40.41%
WB | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_2 | TR_LINE 7254(2) | TR_LINE 7254(2) | TR_LINE 7254(2) | TR_LINE 7254(2)
WB | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 3178% | 4523% | 4822% | 5105% | 5335%
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 384% | 551.5% | 588.6% | 623.8% | 652.4%
WB | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 365.2% | 550.5% | 587.8% | 623.1% | 651.9%
WB | M002_Tarong-Kingaroy West 66 kV | Power Factor | 94.77% | 99.68% | 99.75% | 99.81% | 99.84%
WB | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 54800% | 13200% | 13200% | 13200% | 13200%
WB | M002_Tarong-Kingaroy West 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M002_Tarong-Kingaroy West 66 kV | Min Voltage at Constrained Conductor (pu) | 105.7% | 106.2% | 106.2% | 106.3% | 106.3%
WB | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 31.74% | 6.47% | 6.545% | 6.628% | 6.708%
WB | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7254(2) | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 4190% | 1093% | 1106% | 1120% | 1134%
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 511.2% | 163% | 165% | 167.2% | 169.3%
WB | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 510% | 48.99% | 55.03% | 61.19% | 66.63%
WB | M003_Kingaroy- Yarraman 66 kV | Power Factor | 99.57% | 30.06% | 33.35% | 36.6% | 39.36%
WB | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 13200% | 16900% | 16900% | 16900% | 16900%
WB | M003_Kingaroy- Yarraman 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M003_Kingaroy- Yarraman 66 kV | Min Voltage at Constrained Conductor (pu) | 106.3% | 130.4% | 130.5% | 130.6% | 130.6%
WB | M004_Murgon-Kingaroy 66 kV | % of Rated A | 6.382% | 1.66% | 1.67% | 1.682% | 1.695%
WB | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7239_1 (FDR-M005)
WB | M004_Murgon-Kingaroy 66 kV | Loading (A) | 1079% | 909.5% | 915.1% | 922% | 928.7%
WB | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 160.2% | 111.2% | 111.9% | 112.9% | 113.8%
WB | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 42.71% | 15.58% | 19.48% | 23.5% | 26.94%
WB | M004_Murgon-Kingaroy 66 kV | Power Factor | 26.66% | 14.01% | 17.41% | 20.83% | 23.68%
WB | M004_Murgon-Kingaroy 66 kV | Rating (A) | 16900% | 54800% | 54800% | 54800% | 54800%
WB | M004_Murgon-Kingaroy 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M004_Murgon-Kingaroy 66 kV | Min Voltage at Constrained Conductor (pu) | 129.9% | 106.9% | 107% | 107.1% | 107.1%
WB | M005 KINGAROY-BOONDOOMA | % of Rated A | 1.643% | 5.938% | 6.171% | 6.426% | 6.662%
WB | M005 KINGAROY-BOONDOOMA | Limiting Line Name | TR_LINE 7239_1 (FDR-M005) | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1
WB | M005 KINGAROY-BOONDOOMA | Loading (A) | 900.3% | 587.9% | 610.9% | 636.1% | 659.6%
WB | M005 KINGAROY-BOONDOOMA | Loading (MVA) | 109.4% | 87.66% | 91.15% | 94.97% | 98.52%
WB | M005 KINGAROY-BOONDOOMA | Loading (MW) | 11.51% | 49.03% | 55.07% | 61.24% | 66.67%
WB | M005 KINGAROY-BOONDOOMA | Power Factor | 10.52% | 55.94% | 60.42% | 64.48% | 67.67%
WB | M005 KINGAROY-BOONDOOMA | Rating (A) | 54800% | 9900% | 9900% | 9900% | 9900%
WB | M005 KINGAROY-BOONDOOMA | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M005 KINGAROY-BOONDOOMA | Min Voltage at Constrained Conductor (pu) | 106.3% | 130.4% | 130.5% | 130.6% | 130.7%
WB | M007_Proston 66 kV | % of Rated A | 5.707% | 12.24% | 13.49% | 14.87% | 16.11%
WB | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7264_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB | M007_Proston 66 kV | Loading (A) | 565% | 2216% | 2442% | 2691% | 2916%
WB | M007_Proston 66 kV | Loading (MVA) | 83.92% | 327.7% | 361.1% | 398% | 431.2%
WB | M007_Proston 66 kV | Loading (MW) | 42.75% | 229.3% | 275.5% | 323.1% | 363.9%
WB | M007_Proston 66 kV | Power Factor | 50.94% | 69.95% | 76.29% | 81.16% | 84.37%
WB | M007_Proston 66 kV | Rating (A) | 9900% | 18100% | 18100% | 18100% | 18100%
WB | M007_Proston 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M007_Proston 66 kV | Min Voltage at Constrained Conductor (pu) | 129.9% | 129.4% | 129.4% | 129.3% | 129.3%
WB | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 7.022% | 12.49% | 13.57% | 14.81% | 15.93%
WB | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 7214_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 1271% | 2110% | 2294% | 2502% | 2693%
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 188% | 311.4% | 338.5% | 369.2% | 397.3%
WB | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 103.3% | 196.1% | 238% | 281.2% | 318.5%
WB | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 54.97% | 62.57% | 69.84% | 75.66% | 79.59%
WB | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 18100% | 16900% | 16900% | 16900% | 16900%
WB | M008_Kilkivan-Murgon No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M008_Kilkivan-Murgon No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 129.4% | 129.1% | 129.1% | 129.1% | 129.1%
WB | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 7.386% | 3.286% | 3.646% | 4.003% | 4.297%
WB | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 1248% | 818.1% | 908% | 996.8% | 1070%
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 184.6% | 95.79% | 106.5% | 117% | 125.6%
WB | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 77.57% | 73.9% | 87.38% | 100% | 110.1%
WB | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 41.84% | 77.15% | 82.01% | 85.49% | 87.65%
WB | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 16900% | 24900% | 24900% | 24900% | 24900%
WB | M009_Kilkivan-Murgon No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M009_Kilkivan-Murgon No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 129.4% | 102.4% | 102.7% | 102.7% | 102.7%
WB | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 2.931% | 31.07% | 33.12% | 35% | 36.49%
WB | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199623_1 | TR_LINE 42253_1 | TR_LINE 42253_1 | TR_LINE 42253_1 | TR_LINE 42253_1
WB | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 729.9% | 4102% | 4372% | 4621% | 4817%
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 86.03% | 607.5% | 647.6% | 684.6% | 714.3%
WB | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 59.64% | 596.4% | 638.3% | 676.7% | 707%
WB | M010_Maryborough - Owanyilla 66 kV | Power Factor | 69.33% | 97.57% | 97.92% | 98.2% | 98.38%
WB | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 24900% | 13200% | 13200% | 13200% | 13200%
WB | M010_Maryborough - Owanyilla 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M010_Maryborough - Owanyilla 66 kV | Min Voltage at Constrained Conductor (pu) | 103.1% | 129.6% | 129.6% | 129.6% | 129.6%
WB | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 25.41% | 14.7% | 15.08% | 16% | 16.76%
WB | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 42253_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 3354% | 8056% | 8263% | 8765% | 9185%
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 496% | 948.9% | 975.7% | 1035% | 1085%
WB | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 493.4% | 114.2% | 838.2% | 909.6% | 968.1%
WB | M011_Kilkivan-Maryborough 66 kV | Power Factor | 98.97% | 11.89% | 85.75% | 87.73% | 89.11%
WB | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 13200% | 54800% | 54800% | 54800% | 54800%
WB | M011_Kilkivan-Maryborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M011_Kilkivan-Maryborough 66 kV | Min Voltage at Constrained Conductor (pu) | 129.4% | 103% | 103.3% | 103.3% | 103.3%
WB | M012_Maryborough-Rocky St 66 kV | % of Rated A | 9.322% | 30.75% | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7168_1 | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Loading (A) | 5109% | 18693% | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 602% | 2271% | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 151.3% | 2160% | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Power Factor | 25.04% | 95.11% | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Rating (A) | 54800% | 60800% | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Time | 12:00:00 | 12:00:00 | 0% | 0% | 0%
WB | M012_Maryborough-Rocky St 66 kV | Min Voltage at Constrained Conductor (pu) | 103.1% | 106.3% | 0% | 0% | 0%
WB | M014_Torquay-Pialba 66 kV | % of Rated A | 7.647% | 7.647%
WB | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1
WB | M014_Torquay-Pialba 66 kV | Loading (A) | 4650% | 4650%
WB | M014_Torquay-Pialba 66 kV | Loading (MVA) | 557.8% | 557.8%
WB | M014_Torquay-Pialba 66 kV | Loading (MW) | 438.3% | 438.3%
WB | M014_Torquay-Pialba 66 kV | Power Factor | 78.57% | 78.57%
WB | M014_Torquay-Pialba 66 kV | Rating (A) | 60800% | 60800%
WB | M014_Torquay-Pialba 66 kV | Time | 12:00:00 | 12:00:00
WB | M014_Torquay-Pialba 66 kV | Min Voltage at Constrained Conductor (pu) | 104.9% | 104.9%
0%
WB | M014_Torquay-SOPI 66 kV | % of Rated A |  |  | 33.16% | 34.53% | 35.52%
WB | M014_Torquay-SOPI 66 kV | Limiting Line Name |  |  | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB | M014_Torquay-SOPI 66 kV | Loading (A) |  |  | 20162% | 20993% | 21596%
WB | M014_Torquay-SOPI 66 kV | Loading (MVA) |  |  | 2468% | 2571% | 2646%
WB | M014_Torquay-SOPI 66 kV | Loading (MW) |  |  | 2282% | 2395% | 2476%
WB | M014_Torquay-SOPI 66 kV | Power Factor |  |  | 92.45% | 93.15% | 93.6%
WB | M014_Torquay-SOPI 66 kV | Rating (A) |  |  | 60800% | 60800% | 60800%
WB | M014_Torquay-SOPI 66 kV | Time |  |  | 12:00:00 | 12:00:00 | 12:00:00
WB | M014_Torquay-SOPI 66 kV | Min Voltage at Constrained Conductor (pu) |  |  | 107.1% | 107.1% | 107.2%
WB | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.888% | 3.809% | 3.817% | 3.817% | 3.817%
WB | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2 | TR_LINE 7139_2
WB | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 249.2% | 502.8% | 503.9% | 503.8% | 503.8%
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 29.36% | 59.25% | 59.51% | 59.5% | 59.49%
WB | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 0.1122% | 0.01146% | 0.01151% | 0.01151% | 0.01151%
WB | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.3822% | 0.01842% | 0.01842% | 0.01842% | 0.01842%
WB | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
WB | M015_Maryborough-Howard No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M015_Maryborough-Howard No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 103.1% | 103.1% | 103.3% | 103.3% | 103.3%
WB | M016_Maryborough-Howard No 2 66 kV | % of Rated A | 1.93% | 14.11% | 15.02% | 15.93% | 16.69%
WB | M016_Maryborough-Howard No 2 66 kV | Limiting Line Name | TR_LINE 7139_2 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1
WB | M016_Maryborough-Howard No 2 66 kV | Loading (A) | 254.8% | 7733% | 8232% | 8730% | 9146%
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MVA) | 30.03% | 917.4% | 979% | 1038% | 1088%
WB | M016_Maryborough-Howard No 2 66 kV | Loading (MW) | 0.1014% | 763% | 837.2% | 908.6% | 967%
WB | M016_Maryborough-Howard No 2 66 kV | Power Factor | 0.3373% | 83.17% | 85.52% | 87.5% | 88.88%
WB | M016_Maryborough-Howard No 2 66 kV | Rating (A) | 13200% | 54800% | 54800% | 54800% | 54800%
WB | M016_Maryborough-Howard No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M016_Maryborough-Howard No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 103.1% | 103.8% | 104% | 104% | 104.1%
WB | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 8.332% | 15.33% | 15.64% | 16.07% | 16.52%
WB | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 7924_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1
WB | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 4566% | 8403% | 8572% | 8804% | 9053%
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 539.5% | 990.2% | 1012% | 1040% | 1069%
WB | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 534.6% | 146.3% | 257.9% | 366.1% | 454%
WB | M017_Rocky St - Maryborough City 66 kV | Power Factor | 99.09% | 14.63% | 25.34% | 35.07% | 42.32%
WB | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 54800% | 54800% | 54800% | 54800% | 54800%
WB | M017_Rocky St - Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M017_Rocky St - Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 103.3% | 103.1% | 103.3% | 103.3% | 103.3%
WB | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 6.506% | 14.08% | 14.04% | 14.04% | 14.04%
WB | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 122162_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1
WB | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 3565% | 7714% | 7695% | 7694% | 7693%
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 420.2% | 905.1% | 905.1% | 905.1% | 905.1%
WB | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 121.6% | 903.9% | 903.9% | 903.9% | 903.9%
WB | M018_Maryborough-Maryborough City 66 kV | Power Factor | 28.93% | 99.87% | 99.87% | 99.87% | 99.87%
WB | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 54800% | 54800% | 54800% | 54800% | 54800%
WB | M018_Maryborough-Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M018_Maryborough-Maryborough City 66 kV | Min Voltage at Constrained Conductor (pu) | 103.1% | 102.6% | 102.9% | 102.9% | 102.9%
WB | M020_Maryborough-Torquay 66 kV | % of Rated A | 29.1% | 31.11% | 33.31% | 34.72% | 35.73%
WB | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 112154_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1
WB | M020_Maryborough-Torquay 66 kV | Loading (A) | 17690% | 18821% | 20153% | 21003% | 21618%
WB | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 2105% | 2274% | 2452% | 2556% | 2632%
WB | M020_Maryborough-Torquay 66 kV | Loading (MW) | 2087% | 2163% | 2285% | 2399% | 2481%
WB | M020_Maryborough-Torquay 66 kV | Power Factor | 99.13% | 95.1% | 93.22% | 93.86% | 94.27%
WB | M020_Maryborough-Torquay 66 kV | Rating (A) | 60800% | 60500% | 60500% | 60500% | 60500%
WB | M020_Maryborough-Torquay 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M020_Maryborough-Torquay 66 kV | Min Voltage at Constrained Conductor (pu) | 104.1% | 105.5% | 106.2% | 106.3% | 106.3%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | % of Rated A | 22.41% | 8.384% | 8.846% | 9.247% | 9.537%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Limiting Line Name | TR_LINE 224569_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (A) | 13559% | 4595% | 4848% | 5067% | 5226%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MVA) | 1626% | 538.1% | 568.2% | 594% | 612.7%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Loading (MW) | 1586% | 537.3% | 567.3% | 593% | 611.5%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Power Factor | 97.58% | 99.85% | 99.83% | 99.82% | 99.81%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Rating (A) | 60500% | 54800% | 54800% | 54800% | 54800%
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M021_Maryborough-Howard-Pialba Tee 66 kV | Min Voltage at Constrained Conductor (pu) | 104.8% | 102.2% | 102.3% | 102.3% | 102.3%
WB | M022_Howard - ISIS 66 kV | % of Rated A | 7.811% | 20.33% | 21.08% | 21.79% | 22.29%
WB | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB | M022_Howard - ISIS 66 kV | Loading (A) | 4280% | 12301% | 12752% | 13185% | 13487%
WB | M022_Howard - ISIS 66 kV | Loading (MVA) | 503.2% | 1478% | 1539% | 1592% | 1629%
WB | M022_Howard - ISIS 66 kV | Loading (MW) | 502.6% | 1398% | 1462% | 1519% | 1558%
WB | M022_Howard - ISIS 66 kV | Power Factor | 99.86% | 94.59% | 94.99% | 95.38% | 95.63%
WB | M022_Howard - ISIS 66 kV | Rating (A) | 54800% | 60500% | 60500% | 60500% | 60500%
WB | M022_Howard - ISIS 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M022_Howard - ISIS 66 kV | Min Voltage at Constrained Conductor (pu) | 102.6% | 105.1% | 105.6% | 105.6% | 105.7%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 19.4% | 21.45% | 21.4% | 21.75% | 22.1%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 11735% | 2831% | 2825% | 2871% | 2917%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 1411% | 328.2% | 329% | 334.6% | 340.2%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 1325% | 58.68% | 77.5% | 97.4% | 114.5%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 93.93% | 17.09% | 22.77% | 28.31% | 32.84%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 60500% | 13200% | 13200% | 13200% | 13200%
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M023_6242 (Pialba-Point Vernon) 66 kV | Min Voltage at Constrained Conductor (pu) | 105.2% | 101.4% | 101.9% | 101.9% | 102%
WB | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 20.6% | 3.179% | 3.456% | 3.771% | 4.061%
WB | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1
WB | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 2719% | 340.1% | 369.8% | 403.5% | 434.6%
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 311.2% | 40.02% | 42.73% | 46.7% | 50.35%
WB | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 38.23% | 26.06% | 31.21% | 36.47% | 41.07%
WB | M024_Gayndah - Mundubbera 66 kV | Power Factor | 11.52% | 65.12% | 73.03% | 78.1% | 81.58%
WB | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 13200% | 10700% | 10700% | 10700% | 10700%
WB | M024_Gayndah - Mundubbera 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M024_Gayndah - Mundubbera 66 kV | Min Voltage at Constrained Conductor (pu) | 100.1% | 102.9% | 101.1% | 101.2% | 101.3%
WB | M025_Eidsvold 66 kV | % of Rated A | 2.903% | 17.58% | 18.37% | 19.07% | 19.61%
WB | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 77926_1 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2 | TR_LINE 118887_2
WB | M025_Eidsvold 66 kV | Loading (A) | 310.6% | 2321% | 2425% | 2517% | 2588%
WB | M025_Eidsvold 66 kV | Loading (MVA) | 35.93% | 271.3% | 283.7% | 294.4% | 302.8%
WB | M025_Eidsvold 66 kV | Loading (MW) | 20.62% | 270.5% | 283.1% | 293.9% | 302.3%
WB | M025_Eidsvold 66 kV | Power Factor | 57.38% | 99.69% | 99.76% | 99.8% | 99.83%
WB | M025_Eidsvold 66 kV | Rating (A) | 10700% | 13200% | 13200% | 13200% | 13200%
WB | M025_Eidsvold 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M025_Eidsvold 66 kV | Min Voltage at Constrained Conductor (pu) | 101.2% | 102.3% | 102.3% | 102.3% | 102.3%
WB | M026_ISIS - Bundaberg 66 kV | % of Rated A | 21.9% | 0.2428% | 0.243% | 0.243% | 0.243%
WB | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_CABLE 3770_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1
WB | M026_ISIS - Bundaberg 66 kV | Loading (A) | 2190% | 106.6% | 106.7% | 106.7% | 106.7%
WB | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 257.9% | 12.26% | 12.28% | 12.28% | 12.28%
WB | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 257.7% | 0.0001924% | 0.0001927% | 0.0001927% | 0.0001927%
WB | M026_ISIS - Bundaberg 66 kV | Power Factor | 99.92% | 0.001569% | 0.001569% | 0.001569% | 0.001569%
WB | M026_ISIS - Bundaberg 66 kV | Rating (A) | 10000% | 43900% | 43900% | 43900% | 43900%
WB | M026_ISIS - Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M026_ISIS - Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 103% | 100.6% | 100.7% | 100.7% | 100.7%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | % of Rated A | 0.2403% | 13.72% | 14.3% | 14.87% | 15.34%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Limiting Line Name | TR_LINE 12084300_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (A) | 105.5% | 3540% | 3688% | 3837% | 3957%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MVA) | 12.01% | 415.7% | 433.5% | 451% | 465.1%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MW) | 0.0001884% | 294.8% | 319.5% | 343.4% | 362.1%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Power Factor | 0.001569% | 70.79% | 73.58% | 76.02% | 77.73%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Rating (A) | 43900% | 25800% | 25800% | 25800% | 25800%
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M026b_FORMER_ISIS - Bundaberg 66kV | Min Voltage at Constrained Conductor (pu) | 99.6% | 102.7% | 102.8% | 102.8% | 102.8%
WB | M027_ISIS - Childers 66 kV | % of Rated A | 10.5% | 7.369% | 7.348% | 7.564% | 7.778%
WB | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 183684_1 | TR_LINE 12103276_2(New M028) | TR_LINE 12103276_2(New M028) | TR_LINE 12103276_2(New M028) | TR_LINE 12103276_2(New M028)
WB | M027_ISIS - Childers 66 kV | Loading (A) | 2709% | 4038% | 4027% | 4145% | 4262%
WB | M027_ISIS - Childers 66 kV | Loading (MVA) | 317.7% | 472.9% | 471.9% | 485.8% | 499.5%
WB | M027_ISIS - Childers 66 kV | Loading (MW) | 134.2% | 155.8% | 151.7% | 191.9% | 225.8%
WB | M027_ISIS - Childers 66 kV | Power Factor | 42.26% | 32.44% | 31.66% | 39% | 44.68%
WB | M027_ISIS - Childers 66 kV | Rating (A) | 25800% | 54800% | 54800% | 54800% | 54800%
WB | M027_ISIS - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M027_ISIS - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 102.6% | 102.5% | 102.5% | 102.5% | 102.5%
WB | M028_GAYN TEE DEGI FDR 66kV | % of Rated A | 6.325% | 0.8556% | 0.9043% | 0.9546% | 0.9936%
WB | M028_GAYN TEE DEGI FDR 66kV | Limiting Line Name | TR_LINE 12103276_2(New M028) | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (A) | 3466% | 165.1% | 174.5% | 184.2% | 191.8%
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MVA) | 405.9% | 18.74% | 19.82% | 20.92% | 21.77%
WB | M028_GAYN TEE DEGI FDR 66kV | Loading (MW) | 302.6% | 18.52% | 19.61% | 20.72% | 21.59%
WB | M028_GAYN TEE DEGI FDR 66kV | Power Factor | 74.55% | 98.82% | 98.95% | 99.06% | 99.13%
WB | M028_GAYN TEE DEGI FDR 66kV | Rating (A) | 54800% | 19300% | 19300% | 19300% | 19300%
WB | M028_GAYN TEE DEGI FDR 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M028_GAYN TEE DEGI FDR 66kV | Min Voltage at Constrained Conductor (pu) | 102.5% | 99.28% | 99.33% | 99.33% | 99.33%
WB | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 0.8106% | 17.46% | 17.57% | 17.69% | 17.78%
WB | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 205843_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 415% | 2304% | 2320% | 2335% | 2348%
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 47.25% | 273.1% | 275.2% | 277.1% | 278.6%
WB | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 17.24% | 70.21% | 76.27% | 82.47% | 87.4%
WB | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 36.46% | 25.62% | 27.63% | 29.68% | 31.29%
WB | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 51200% | 13200% | 13200% | 13200% | 13200%
WB | M029_Bundaberg - Farnsfield 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M029_Bundaberg - Farnsfield 66 kV | Min Voltage at Constrained Conductor (pu) | 99.6% | 103.7% | 103.8% | 103.8% | 103.8%
WB | M030_Farnsfield - Childers 66 kV | % of Rated A | 17.23% | 26.59% | 27.68% | 28.48% | 29.4%
WB | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1
WB | M030_Farnsfield - Childers 66 kV | Loading (A) | 2274% | 3510% | 3654% | 3760% | 3881%
WB | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 267.4% | 401.1% | 417.7% | 429.8% | 443.7%
WB | M030_Farnsfield - Childers 66 kV | Loading (MW) | 63.49% | 268.5% | 293.1% | 316.9% | 336.1%
WB | M030_Farnsfield - Childers 66 kV | Power Factor | 23.66% | 66.94% | 70.15% | 73.73% | 75.74%
WB | M030_Farnsfield - Childers 66 kV | Rating (A) | 13200% | 13200% | 13200% | 13200% | 13200%
WB | M030_Farnsfield - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M030_Farnsfield - Childers 66 kV | Min Voltage at Constrained Conductor (pu) | 102.9% | 99.95% | 100% | 100% | 100%
WB | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 23.25% | 11.46% | 11.82% | 12.03% | 12.35%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 3069% | 2955% | 3050% | 3103% | 3187%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 350.6% | 340% | 351.2% | 357.3% | 367.1%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 143.7% | 184.8% | 204.7% | 224.1% | 239.9%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 40.98% | 54.34% | 58.29% | 62.71% | 65.33%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 13200% | 25800% | 25800% | 25800% | 25800%
WB | M032_Bundaberg-South Kolan No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M032_Bundaberg-South Kolan No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 99.94% | 100.6% | 100.7% | 100.7% | 100.8%
WB | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 4.154% | 61.46% | 64.11% | 66.69% | 68.71%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 2277% | 26979% | 28145% | 29277% | 30163%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 259.6% | 3182% | 3325% | 3463% | 3571%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 206.1% | 2441% | 2627% | 2804% | 2939%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 79.32% | 76.71% | 79.01% | 80.95% | 82.29%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 54800% | 43900% | 43900% | 43900% | 43900%
WB | M035_Bundaberg-South Kolan No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M035_Bundaberg-South Kolan No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 99.75% | 99.66% | 99.71% | 99.71% | 99.71%
WB | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 28.01% | 64.39% | 67.23% | 70.09% | 72.24%
WB | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 12296% | 14553% | 15195% | 15840% | 16327%
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 1415% | 1736% | 1791% | 1869% | 1928%
WB | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 1250% | 820.8% | 1718% | 1800% | 1862%
WB | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 88.31% | 47.1% | 95.89% | 96.32% | 96.62%
WB | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 43900% | 22600% | 22600% | 22600% | 22600%
WB | M036_Bundaberg-South Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M036_Bundaberg-South Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 99.6% | 103.9% | 102.6% | 102.7% | 102.7%
WB | M037_South - East Bundaberg 66 kV | % of Rated A | 12.17% | 27.01% | 28.39% | 29.76% | 30.87%
WB | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1
WB | M037_South - East Bundaberg 66 kV | Loading (A) | 2749% | 21773% | 22880% | 23990% | 24879%
WB | M037_South - East Bundaberg 66 kV | Loading (MVA) | 318.1% | 2479% | 2607% | 2733% | 2834%
WB | M037_South - East Bundaberg 66 kV | Loading (MW) | 274% | 1681% | 1863% | 2037% | 2172%
WB | M037_South - East Bundaberg 66 kV | Power Factor | 86.13% | 67.81% | 71.45% | 74.51% | 76.63%
WB | M037_South - East Bundaberg 66 kV | Rating (A) | 22600% | 80600% | 80600% | 80600% | 80600%
WB | M037_South - East Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M037_South - East Bundaberg 66 kV | Min Voltage at Constrained Conductor (pu) | 101.2% | 99.6% | 99.64% | 99.65% | 99.64%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 14.68% | 26.83% | 28.19% | 29.56% | 30.65%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 200241_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 11830% | 21625% | 22723% | 23825% | 24707%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 1347% | 2473% | 2601% | 2727% | 2829%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 907.4% | 1670% | 1850% | 2023% | 2158%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 67.37% | 67.5% | 71.13% | 74.18% | 76.28%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 80600% | 80600% | 80600% | 80600% | 80600%
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M039_Bundaberg-West Bundaberg No 1 66 kV | Min Voltage at Constrained Conductor (pu) | 99.6% | 99.6% | 99.65% | 99.65% | 99.64%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 14.13% | 18.48% | 19.55% | 20.53% | 21.27%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 169764_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 11392% | 4177% | 4418% | 4640% | 4807%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 1298% | 477.3% | 505.3% | 530.9% | 550.1%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 874.8% | 404.6% | 436.3% | 465% | 486.3%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 67.36% | 84.76% | 86.35% | 87.59% | 88.4%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 80600% | 22600% | 22600% | 22600% | 22600%
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M040_Bundaberg-West Bundaberg No 2 66 kV | Min Voltage at Constrained Conductor (pu) | 99.6% | 99.97% | 100% | 100.1% | 100.1%
WB | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 21.18% | 13.54% | 14.31% | 15.03% | 15.59%
WB | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 4786% | 1503% | 1588% | 1668% | 1730%
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 549.6% | 171.8% | 181.7% | 190.9% | 198.1%
WB | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 484.5% | 171.6% | 181.5% | 190.7% | 198%
WB | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 88.16% | 99.8% | 99.83% | 99.85% | 99.87%
WB | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 22600% | 11100% | 11100% | 11100% | 11100%
WB | M041_West Bundaberg-Meadowvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M041_West Bundaberg-Meadowvale 66 kV | Min Voltage at Constrained Conductor (pu) | 100.4% | 99.98% | 100.1% | 100.1% | 100.1%
WB | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 12.61% | 7.295% | 7.295% | 7.295% | 7.295%
WB | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7779_2 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 1400% | 1817% | 1816% | 1816% | 1816%
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 160.7% | 219.2% | 219.2% | 219.2% | 219.2%
WB | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 160.5% | 208.2% | 208.2% | 208.2% | 208.2%
WB | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 99.75% | 94.99% | 94.99% | 94.98% | 94.98%
WB | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 11100% | 24900% | 24900% | 24900% | 24900%
WB | M042_Meadowvale-Gooburrum 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M042_Meadowvale-Gooburrum 66 kV | Min Voltage at Constrained Conductor (pu) | 100.4% | 105.5% | 105.5% | 105.5% | 105.5%
WB | M046_Tarong-Caboonbah 66 kV | % of Rated A | 7.292% | 21.68% | 20.9% | 20.26% | 19.73%
WB | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB | M046_Tarong-Caboonbah 66 kV | Loading (A) | 1816% | 8652% | 8341% | 8085% | 7871%
WB | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 219.2% | 1012% | 976.5% | 946.6% | 921.5%
WB | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 208.2% | 930.3% | 895.9% | 861.3% | 832.1%
WB | M046_Tarong-Caboonbah 66 kV | Power Factor | 94.97% | 91.9% | 91.75% | 90.99% | 90.29%
WB | M046_Tarong-Caboonbah 66 kV | Rating (A) | 24900% | 39900% | 39900% | 39900% | 39900%
WB | M046_Tarong-Caboonbah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M046_Tarong-Caboonbah 66 kV | Min Voltage at Constrained Conductor (pu) | 105.6% | 101.8% | 101.9% | 102% | 102%
WB | M049_ISIS - Gayndah 66 kV | % of Rated A | 14.5% | 18.18% | 19.34% | 20.44% | 21.31%
WB | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1
WB | M049_ISIS - Gayndah 66 kV | Loading (A) | 5785% | 1945% | 2070% | 2187% | 2281%
WB | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 677.6% | 238.9% | 254.5% | 269.2% | 281.2%
WB | M049_ISIS - Gayndah 66 kV | Loading (MW) | 617.9% | 238.1% | 253.9% | 268.9% | 280.9%
WB | M049_ISIS - Gayndah 66 kV | Power Factor | 91.18% | 99.3% | 99.43% | 99.53% | 99.6%
WB | M049_ISIS - Gayndah 66 kV | Rating (A) | 39900% | 10700% | 10700% | 10700% | 10700%
WB | M049_ISIS - Gayndah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M049_ISIS - Gayndah 66 kV | Min Voltage at Constrained Conductor (pu) | 102.1% | 107.4% | 107.6% | 107.7% | 107.8%
WB | M051_Tarong Tie 66 kV | % of Rated A | 16.89% | 24.48% | 25.74% | 26.9% | 27.79%
WB | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 37804_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB | M051_Tarong Tie 66 kV | Loading (A) | 1808% | 10035% | 10555% | 11029% | 11393%
WB | M051_Tarong Tie 66 kV | Loading (MVA) | 222.2% | 1160% | 1221% | 1276% | 1319%
WB | M051_Tarong Tie 66 kV | Loading (MW) | 220.9% | 1159% | 1220% | 1275% | 1318%
WB | M051_Tarong Tie 66 kV | Power Factor | 99.12% | 99.92% | 99.91% | 99.9% | 99.9%
WB | M051_Tarong Tie 66 kV | Rating (A) | 10700% | 41000% | 41000% | 41000% | 41000%
WB | M051_Tarong Tie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB | M051_Tarong Tie 66 kV | Min Voltage at Constrained Conductor (pu) | 107.5% | 101.1% | 101.2% | 101.2% | 101.2%
Note on A672: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed NCC - 11kV